## Precast
INSPECTION & TEST PLAN
|  | Contract Name: | [6 empty] | Rev: | Originator | Date | Approved | Date
|  | Tauhara Field facilities |  |  | Hold Point (H) | Verify (V) |  |  | 0 | Cameron Hinge | 2022-03-19
[5 empty] | Submit (S) | Review (R) |  |  | 1 | JD | 2022-03-26
[5 empty] | Approve(A) | Surveillance (SU)
TASK | SPECIFICATION REFERENCE | TEST REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL Signature | Client Signature | UCCL | Client | DATE | COMMENTS
Pre Construction
IFC Drawing and IFC Project Specifications Review | Confirmation all inspection and test requirements from the IFC drawings and IFC project specifications are captured | General review of the IFC drawing and IFC project specifications | UCCL/ CEL | Commencement / Completion | IFC Drawing and IFC project specifications; Work Pack Checklist (if applicable) |  |  | R
Shop Drawings | Reviewed and approved prior to commencement | Designer general review of the shop drawings | UCCL/ CEL | 10 days prior to fabrication | Shop drawing approval |  |  | H | R/A
Lifting Design | Approved Code of Practice for the Safe Handling, Transportation and Erection of Pre-Cast Concrete. | Lift design produced for demoulding, storage, transportation and installation of precast items | UCCL | Prior to Casting | Lift Designs for each precast element |  |  | R
MATERIAL
Concrete Mix Design | NZS 3101, NZS 3109, NZS 3104, Project Specification Tauhara Steamfields – Structural Specifications | Mix designs shall be supplied to Designer's for review and acceptance. | UCCL/ CEL | Submission 4 weeks prior to pouring any concrete (intended for new concrete mix design) | Approved Mix Design |  |  | H | R/A
Supply of Reinforcement Steel reinforcement compliance records | In accordance with AS/NZS4671. Steel shall be grade 300 or 500 Compliance with Project Specification Tauhara Steamfields – Structural Specifications | Schedules shall be prepared by the supplier and to be reviewed and accepted prior to fabrication. | UCCL | Per Delivery | Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet |  |  | H
Embedded / inserts product data | Compliance with Project Specification Tauhara Steamfields – Structural Specifications, and are in accordance with the Approved Code of Practice for the Safe Handling, Transportation and Erection of Pre-Cast Concrete. | Product data review | UCCL | prior to casting | Product testing conformance |  |  | H
PRECAST FABRICATION (Pre-pour inspections & concrete testing)
Mould bed preparation | Compliance with Project Specification Tauhara Steamfields – Structural Specifications | Conduct inspection on precast mould bed for level and cleanliness. | UCCL | Prior to casting | Concrete placement card |  |  | W
Steel reinforcement installation | IFC drawings, Approved shop drawings | Check bar size, spacing, lap, location and cover. | UCCL | Prior to casting | Concrete placement card |  |  | W
Embedded items including anchor bolts and couplers | IFC drawings, Approved shop drawings | Check size, type, number, location, alignment, elevation and that firmly supported / protected from damage or movement during the pour. | UCCL | Prior to casting | Concrete placement card |  |  | W
Formwork moulds /Reinforcing | IFC drawings | Dimensional checks against shop drawings, propping, chamfers and form release agent. | UCCL | Prior to casting | Concrete placement card |  |  | W
Designer's Inspection | Specification / Project Requirements | No concrete shall be placed until the Designer's review / inspection. | UCCL | Per individual structural element | Approved Drawings / Hold Point Release signed on Concrete Pour Inspection Sheet (ConQA) |  |  | H | Su
Slump test | Compliance with Project Specification Tauhara Steamfields – Structural Specifications | On site pre-pour | UCCL | Each truck prior to placing | Concrete pour record sheet |  |  | W
Compression tests | Compliance with Project Specification Tauhara Steamfields – Structural Specifications | 1no. for 7 day & 2no. for 28 day | UCCL/ CEL | 3no. specimens taken from each 100m3 of concrete placed (or part thereof), each day, of each different mix | Concrete pour record sheet, IANZ Accredited Independent test report |  |  | W
Precast concrete curing | Compliance with Project Specification Tauhara Steamfields – Structural Specifications | Heat accelerated curing for panels instead of water curing proposed. Curing method to submitted and approved prior to casting. | UCCL/ CEL | After casting | Concrete pour record sheet |  |  | H | R/A
PRECAST FABRICATION (Post Pour Inspection)
Precast pre-delivery check | Compliance with Project Specification Tauhara Steamfields – Structural Specifications | Check completed precast unit for compliance with the specifications, tolerances and drawings | UCCL | Prior to delivery | Supplier Fabrication ITP, Post Pour Inspection Record |  |  | W
Defective precast concrete or reinforcing | CEL approval | Method statement to be prepared and agreed before repair is undertaken | UCCL | 2 wks prior to repair work | Method statement approval by RFI |  |  | S | R/A
Precast unit handling, transport and delivery | Compliance with Project Specification Tauhara Steamfields – Structural Specifications | Ensure precast units have been designed for all temporary load cases | UCCL | Prior to delivery / post installation | Supplier Fabrication ITP, Post Pour Inspection Record |  |  | W
POST-CONSTRUCTION
As Built Survey | Compliance to IFC Drawings / Shop Drawings. | Red Line Markup for any change | UCCL | Completion | As built drawing/ report |  |  | S | R
Precast panel warranty | Compliance with Project Specification Tauhara Steamfields – Structural Specifications | Product warranty | UCCL | Completion of supply | Warranty |  |  | S | R
Producer Statement | Compliance with Project Specification Tauhara Steamfields – Structural Specifications | Precast subcontractor producer statement | UCCL | Completion of supply | Signed PS3 Certificate |  |  | S | R