## QA Folder Structure WBS
QA Folder Structure |  |  | Checklists
OVERALL - Schedule of Inspections and Tests |  |  | IMF-35 - Schedule of Inspections and Tests
United Lift Services QA
Goods Lift 1
|  | Pre-Start | IMF Site Pre-start Checklist
|  | Lift Shaft | IMF08 -ITP9 - Lift Shaft
|  | Lift Pit | IMF08 -ITP10 - Lift Pit
|  | Hall Equipment | IMF08 -ITP12 - Hall Equipment
|  | Lift Controller | IMF08 -ITP5 - Lift Controller
|  | Main Circuit Breaker Panel | IMF08 -ITP1 - Main Circuit Breaker Panel
|  | Hoisting Machine | IMF08 -ITP3 - Hoisting Machine
|  | Machine Brake | IMF08 -ITP4 - Machine Brake
|  | Overspeed Governor | IMF08 -ITP2 - Overspeed Governor
|  | Counterweight | IMF08 -ITP8 - Counterweight
|  | Car Top | IMF08 -ITP7 - Lift Car - Car Top
|  | Lift Car Interior | IMF08 -ITP11 - Lift Car Interior
|  | Protection of Conductors | IMF08 -ITP6 - Protection of Conductors
|  | Ride Comfort, Noise & Vibration | IMF08 -ITP13 - Ride Comfort, Noise and Vibration
Goods Lift 2
|  | Pre-Start | IMF Site Pre-start Checklist
|  | Lift Shaft | IMF08 -ITP9 - Lift Shaft
|  | Lift Pit | IMF08 -ITP10 - Lift Pit
|  | Hall Equipment | IMF08 -ITP12 - Hall Equipment
|  | Lift Controller | IMF08 -ITP5 - Lift Controller
|  | Main Circuit Breaker Panel | IMF08 -ITP1 - Main Circuit Breaker Panel
|  | Hoisting Machine | IMF08 -ITP3 - Hoisting Machine
|  | Machine Brake | IMF08 -ITP4 - Machine Brake
|  | Overspeed Governor | IMF08 -ITP2 - Overspeed Governor
|  | Counterweight | IMF08 -ITP8 - Counterweight
|  | Car Top | IMF08 -ITP7 - Lift Car - Car Top
|  | Lift Car Interior | IMF08 -ITP11 - Lift Car Interior
|  | Protection of Conductors | IMF08 -ITP6 - Protection of Conductors
|  | Ride Comfort, Noise & Vibration | IMF08 -ITP13 - Ride Comfort, Noise and Vibration
Lift 3
|  | Pre-Start | IMF Site Pre-start Checklist
|  | Lift Shaft | IMF08 -ITP9 - Lift Shaft
|  | Lift Pit | IMF08 -ITP10 - Lift Pit
|  | Hall Equipment | IMF08 -ITP12 - Hall Equipment
|  | Lift Controller | IMF08 -ITP5 - Lift Controller
|  | Main Circuit Breaker Panel | IMF08 -ITP1 - Main Circuit Breaker Panel
|  | Hoisting Machine | IMF08 -ITP3 - Hoisting Machine
|  | Machine Brake | IMF08 -ITP4 - Machine Brake
|  | Overspeed Governor | IMF08 -ITP2 - Overspeed Governor
|  | Counterweight | IMF08 -ITP8 - Counterweight
|  | Car Top | IMF08 -ITP7 - Lift Car - Car Top
|  | Lift Car Interior | IMF08 -ITP11 - Lift Car Interior
|  | Protection of Conductors | IMF08 -ITP6 - Protection of Conductors
|  | Ride Comfort, Noise & Vibration | IMF08 -ITP13 - Ride Comfort, Noise and Vibration
Lift 4
|  | Pre-Start | IMF Site Pre-start Checklist
|  | Lift Shaft | IMF08 -ITP9 - Lift Shaft
|  | Lift Pit | IMF08 -ITP10 - Lift Pit
|  | Hall Equipment | IMF08 -ITP12 - Hall Equipment
|  | Lift Controller | IMF08 -ITP5 - Lift Controller
|  | Main Circuit Breaker Panel | IMF08 -ITP1 - Main Circuit Breaker Panel
|  | Hoisting Machine | IMF08 -ITP3 - Hoisting Machine
|  | Machine Brake | IMF08 -ITP4 - Machine Brake
|  | Overspeed Governor | IMF08 -ITP2 - Overspeed Governor
|  | Counterweight | IMF08 -ITP8 - Counterweight
|  | Car Top | IMF08 -ITP7 - Lift Car - Car Top
|  | Lift Car Interior | IMF08 -ITP11 - Lift Car Interior
|  | Protection of Conductors | IMF08 -ITP6 - Protection of Conductors
|  | Ride Comfort, Noise & Vibration | IMF08 -ITP13 - Ride Comfort, Noise and Vibration

## QA Checklists ITCs
type | name | values
checklist-flat | IMF08 -ITP1 - Main Circuit Breaker Panel
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is the lift main circuit breaker panel installed in accordance with current layout drawings
checkpoint | Is the lift main switch clearly identified with its unit number
checkpoint | Is the type and rating of main switch correct for the load and duty
checkpoint | Is circuit breaker earthing terminated by not less than 1/4" bolt and continuous
checkpoint | Is the builders main switch correctly identified as to source and designation of supply
checkpoint | Is the type and rating of builders main switch correct for load and duty
checkpoint | Are lift car light and power circuit breakers correctly rated and marked
checkpoint | Are circuit breaker lockouts fitted and operational with an appropriate label fitted
checkpoint | Is an emergency power source available to the lift main circuit breaker panel
checkpoint | Are "emergency power source" signs fitted clearly identifying location of supply
checkpoint | Has an emergency power simulation test been satisfactorily performed
checkpoint | Has earth continuity and insulation resistance been checked on all mains cables.
checkpoint | If checked please verify type of equipment used and Serial numbers.
checkpoint | Type of Equipment - Insulation KYORITSU Serial No. 5024602
checkpoint | Earth Continuity KYORITSU Serial No. 5024602
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist-flat | IMF08 -ITP2 - Overspeed Governor
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is the governor correctly marked with its unit identification number
checkpoint | Is the governor secured and properly mounted
checkpoint | Is the governor cleaned and lubricated (free of packing tape etc.)
checkpoint | Is the nominal diameter of the governor rope appropriate to the governor
checkpoint | Does the governor rope run free from the governor jaws and floor penetrations
checkpoint | Does the governor operate correctly under slow speed trip in conditions
checkpoint | Are the governor safety switches aligned and connected in accordance with site charts
checkpoint | Is data plate fitted stating rated speed, elec./mech. tripping speed, rope size & pull through force
checkpoint | Does the governor operate at correct settings
label | Mechanical 1.38
label | Electrical 1.27
checkpoint | Are adjustments sealed
checkpoint | Do safety switches operate correctly
checkpoint | Trip speed on Final Inspection Report (IF45)
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist | IMF08 -ITP3 - Hoisting Machine
section | Hoist Machine Checks 1
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is the machine correctly marked with its unit identification number visible from main C/B
checkpoint | Are the machine beams free from distortion and/or deflection
checkpoint | Is the sound isolation between the machine and surrounding building structure satisfactory
checkpoint | Is the machine's rotation "up" and "down" clearly and correctly marked
checkpoint | Is the machine alignment correct, clearance on main shaft checked with feeler gauge
checkpoint | Is the traction sheave free from any apparent wear
checkpoint | Are all machine and motor bolts tightened according to manufacturers specification
checkpoint | Are rope keepers fitted to prevent ropes jumping groves
section | Hoist Machine Checks 2
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Are all motor and machine guards fitted and easily removable for maintenance purposes
checkpoint | Is the machine and motor running quietly without signs of overheating
checkpoint | Is the bedplate and motor clean.
checkpoint | Is the motor cooling fan correctly fitted and wired in accordance with site charts
checkpoint | Are motor cables arranged so as to prevent undue tension being placed on terminations
checkpoint | Are all terminations tight with no signs of over-heating
checkpoint | Are all tachos and tacho drives correctly mounted
checkpoint | Is the tacho wiring correct, i.e. cable segregation and screening connected
checkpoint | Is the machine and motor free of apparent oil leaks
checkpoint | Is the belt data plate fitted clear and legible
checkpoint | Is rope traction sufficient to stop car at 125% load, full speed, bottom of shaft with negligible rope slip
checkpoint | Do the Belt slip when the counterweight is bottomed and the machine driven
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist-flat | IMF08 -ITP4 - Machine Brake
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is the brake drum and coupling clean and free from signs of scouring
checkpoint | Are the brake and brake shoes clean and pivot points lubricated
checkpoint | Is the solenoid locking ring securely pinned in accordance with SAFE information
checkpoint | Are the correct asbestos free brake shoes fitted
checkpoint | Is the brake correctly set to manufacturers specifications, i.e. tension and minimum lift
checkpoint | Does the brake sustain the car in the lower part of its travel with 125% rated load
checkpoint | Does each brake shoe hold 105% full load at rated speed
checkpoint | Are all adjusting nuts correctly tightened and pinned where necessary
checkpoint | If a hydraulic brake is fitted, is the oil and oil level correct in tank
checkpoint | Is the system free from apparent oil leaks
checkpoint | Are hoses so arranged to prevent crimping or other mechanical damage
checkpoint | Are all hose clamps securely attached
checkpoint | Is the "safety solenoid" correctly fitted in the hydraulic line
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist-flat | IMF08 -ITP5 - Lift Controller
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is the controller correctly marked with it's unit identification number visible from main C/B
checkpoint | Are the controller cabinet and doors undamaged, painted and moving freely and earthed
checkpoint | Is the controller secured and vertically mounted
checkpoint | Is there a minimum of 300mm clearance behind controller panel in accordance with layout drawings
checkpoint | Is there a minimum of 700mm clearance in front of controller panel
checkpoint | Are all controller components securely mounted
checkpoint | Are all controller components correctly labelled
checkpoint | Are all cables so arranged as to prevent undue tension or stress being placed on terminals
checkpoint | Are all controller terminals marked in a clear permanent manner
checkpoint | Are all controller terminals tight, ensuring cable insulation is not being pinched in screw terminals
checkpoint | Are all contacts cleared and making proper contact
checkpoint | Are all fuses new and correctly rated and so marked
checkpoint | Are all spare cables terminated in separate terminals with their origin marked
checkpoint | Does the phase reversal and phase failure protection operate correctly
checkpoint | Are all circuit bridges removed
checkpoint | Is safety board correctly adjusted
checkpoint | If Miconic V is handheld keyboard cable fitted
checkpoint | Is monitor securely mounted on stand
checkpoint | Has all wiring been checked prior to switching on power to each circuit
checkpoint | Has earth continuity been checked
checkpoint | Has insulation resistance been checked
checkpoint | If 9.20 and 9.21 where checked please verify type of equipment used and Serial numbers
label | Type of Equipment - Insulation KYORITSU Serial No. 5024602
label | Earth Continuity KYORITSU Serial No. 5024602
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist-flat | IMF08 -ITP6 - Protection of Conductors
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is the fixed wiring in conduit or duct work or fittings which ensure mechanical protection
checkpoint | Are all wires protected from sharp edges in ducting
checkpoint | Are conductors carrying different voltages correctly segregated in accordance with site charts
checkpoint | Is telephone cabling run in accordance with AUSTEL specifications
checkpoint | Earthing - Is the car connected to the controller earthing terminal by 4 parallel flexes (min. 0.75mm or 2 x 2mm)
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist | IMF08 -ITP7 - Lift Car - Car Top
section | Car Top 1
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is car sling assembled without any obvious signs of a twist or misalignment
checkpoint | Are all bolts on car sling correct tensile (i.e. tensile strength) and of full length (full nut)
checkpoint | Are all bolts on car sling and frame tight including side stay rods
checkpoint | Are car steady brackets and buffers correctly fitted and adjusted
checkpoint | Is the car body correctly isolated from the car frame (sound isolation maintained)
checkpoint | Is the limit cam secure and properly aligned to limit rollers and of adequate length
checkpoint | Are the car guides correctly fitted, pinned and adjusted to allow minimum movement of the car
checkpoint | Are keeper plates provided with the adjustment of guide pinned to prevent accidental movement
checkpoint | Are the required nip point guards and lubrication warning labels fitted
checkpoint | If guide oilers fitted are they filled with the correct type and quantity of oil with lubrication label fitted
checkpoint | Is a suitable standing platform provided on the lift car top
checkpoint | Is the working platform and top of car clean and painted
checkpoint | Is the car top lighting adequate for maintenance purposes with its switch labelled
checkpoint | Lighting level measured at top of car (min 100lux):
checkpoint | Is a suitable hand lamp provided with a suitable storage bracket
checkpoint | Is there a GPO provided on the car top suitable for maintenance purposes (2X10A GPO's provided)
checkpoint | Is the layout of the lift car top designed to prevent unnecessary trip hazards including of celicated lanyard cleat
checkpoint | Is the inspection control box suitably located with switch positions correctly marked
checkpoint | Are all car top safety switches correctly mounted and aligned - test every safety switch
checkpoint | Are safeties cleaned, correctly set and operating properly
section | Car Top 2
checkpoint | Will the trap door support a persons weight when closed
checkpoint | Is there clearance through the trap door when open and the total area not less than 0.25m2 and
checkpoint | is the area on either side not less than 400mm or more than 625mm
checkpoint | Will the trap door stay open (is a latch necessary)
checkpoint | Is the OKRL wired neatly with wiring connections tight and properly marked
checkpoint | Is the overrun clearance above the car roof as per layout drawing
checkpoint | Does the Mechanical & Man clearance comply with AS1735.
checkpoint | Is the door drive operation smooth and silent and as per set up notes
checkpoint | Is the car door wiring neat and run in a manner to prevent undue stress or snagging of conductors
checkpoint | Are the torque limiting switches primarily set up. If side opening is door resistor board fitted
checkpoint | Is the car door and door drive earthed properly
checkpoint | Are all car door wiring connections tight and properly marked on door operator
checkpoint | Are all necessary guards and covers fitted to door operator
checkpoint | State the clearance above the highest projection of the car top with the cwt fully compressing buffers
checkpoint | Is the 2:1 idler sheave or 1:1 rope hitch correctly fitted in car bow with lock plates in place
checkpoint | Are grease nipples fitted and idler sheave bearings properly lubricated
checkpoint | Are idler sheave rope keepers and sheave guards correctly fitted
checkpoint | Is air cord fitted through secon fittings
checkpoint | Are the main rope anchorage bolts correctly fitted, lock nutted and pinned
checkpoint | Are bulldog clamps fitted to rope tails if not SECON
section | Car Top 3
checkpoint | Are the guides correctly fitted and adjusted with appropriate keeper plates and pinning of adjustment
checkpoint | Are the required nip-point guards and warning labels fitted
checkpoint | If guide oilers are fitted are they fitted with the correct oil type and quantity
checkpoint | Are the guide rails clean and lubricated if required (visual)
checkpoint | Are guide rails and joints filed (visual)
checkpoint | Is the governor rope hitch correctly positioned and lock nutted and pinned
checkpoint | Are the safety gear activating arms and rods preliminarily adjusted and lock nutted
checkpoint | Are all duct lids and covers fitted and screwed down if necessary
checkpoint | Is the bow/car frame correctly earthed
checkpoint | Are the anchorages correct size and belt ends made off
checkpoint | Are the anchorages fitted with the main anti twist rope
checkpoint | Are all the main belts of the same tension
checkpoint | Are the belts the correct lay
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist | IMF08 -ITP8 - Counterweight
section | Counterweight Checks 1
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is the counterweight frame free from twist or distortion
checkpoint | Are all bolts on counterweight frame correct tensile and of full length and tightened
checkpoint | Is the 2:1 idler sheave or 1:1 rope hitch correctly fitted with locking plates in place
checkpoint | Are grease nipples fitted and accessible for idler sheave bearings correctly lubricated
checkpoint | Are idler sheave rope keepers and sheave guards fitted
checkpoint | Are the main rope anchorage bolts correctly fitted, lock nutted and pinned
checkpoint | Are the anchorages the correct size and rope ends made off
checkpoint | Are the anchorages fitted with the main anti-twist rope secon
checkpoint | Are bulldog clamps fitted to tails on wedge clamp fittings
checkpoint | Are the counterweight guides correctly fitted and adjusted with appropriate keeper plates
checkpoint | Are keeper plates provided with the adjustment of guides pinned to prevent accidental movement
checkpoint | Are the required nip point guards and lubrication warning labels fitted
checkpoint | If guide oilers are fitted are they fitted with the correct type and quantity of oil
checkpoint | Is the counterweight preliminarily balanced to specified balance
checkpoint | Are counterweight blocks properly fitted and rattle free
checkpoint | Are the block securing rods fitted with double nuts and split pins
checkpoint | Is the counterweight tank filler hole securely fitted
checkpoint | Is the counterweight clean and painted safety yellow
checkpoint | Are the compensating rope anchorage bolts correctly fitted, lock nutted and pinned
checkpoint | Are the anchorages correct size and rope ends made off
section | Counterweight Checks 2
checkpoint | Are the anchorages fitted with the main anti-twist rope secon
checkpoint | Is the compensating chain fixing correctly fitted with swivel locknut and split pin
checkpoint | Is the counterweight overtravel as per layout diagram
checkpoint | If safety gear is fitted is the governor rope correctly positioned and lock nutted
checkpoint | Are the safety gear activating arms and rods preliminarily adjusted and lock nutted
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist | IMF08 -ITP9 - Lift Shaft
section | Lift Shaft Checks 1
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Are diverter sheaves at top of shaft fitted correctly with locking plates and lock nuts on sheave brackets
checkpoint | Are diverter sheave guard and rope keepers correctly fitted
checkpoint | Are diverter sheave bearings lubricated with grease nipple accessible from on car top
checkpoint | Are all guide rails free of shaft ceiling by min. of 100mm
checkpoint | Are shaft walls smooth and free of loose building material or projections
checkpoint | Are all holes filled and ledges splayed where necessary
checkpoint | Is the shaft smoke vent waterproof with mesh guarding of suitable material fixed from inside shaft
checkpoint | Are shaft over travel limits correctly mounted and aligned with car actuating ramp and pinned
checkpoint | Is slow down correctly mounted and aligned with slow down magnets
checkpoint | Are all trimmer beams fitted horizontally and brackets properly fitted to shaft wall
checkpoint | Are all guide rail fixings secure and of approved type fixing anchors
checkpoint | Are all bolts of full length with washers and spring washers fitted
checkpoint | Are all fishplate bolts fitted of correct size and full length
checkpoint | Are guide rails clean and plumb with joints aligned and smooth
checkpoint | Is shaft ducting installed so as to prevent distortion from building shrinkage
checkpoint | Is ducting secured and properly earth bonded with sharp edges removed
checkpoint | Are wires in the ducting properly supported
checkpoint | Are all ducting covers securely fitted with blunt tip screws
checkpoint | Are all conduits correctly lock nutted and saddled with inspection covers fitted
checkpoint | Are all door sills supported properly and suitable for operational conditions
section | Lift Shaft Checks 2
checkpoint | Are all landing doors hung plumb and adjusted centrally in the door opening
checkpoint | Are all hanger rollers parallel to door track and pinned to prevent dropping or twisting, twin washers fitted
checkpoint | Are all top door tracks properly secure
checkpoint | Do all landing doors have a clearance of 5mm or less between door and jamb
checkpoint | Do all landing doors have an up thrust opening clearance to reject a 5mm tube
checkpoint | Are all floor access devices operating freely and effectively
checkpoint | Are all doors and frames properly finished
checkpoint | Are tracks and hangers cleared and lightly oiled
checkpoint | Are all door locks cleaned, oiled and adjusted to ensure positive mechanical latching
checkpoint | Are door lock rollers and spindles preliminarily adjusted to ensure running clearance and greased
checkpoint | Are all landing doors self closing (and locking) when released from 200mm apart
checkpoint | Are all door stops fitted and correctly set
checkpoint | Are all door locks/frames correctly earthed
checkpoint | Is the horizontal distance between the sill of the car and the sill of the landing 13mm to 40mm.
checkpoint | Are all flushing panels adequately supported and painted, with sharp edges removed
checkpoint | Are top trailing cable brackets secure and in correct position
checkpoint | Are the cables correctly suspended (i.e. nylon or steel cores)
checkpoint | Is the halfway cable bracket secure in connect position with cable guided freely
checkpoint | Are cables free throughout and clear of obstacles
checkpoint | Are walls smooth behind cables from halfway to pit
section | Lift Shaft Checks 3
checkpoint | If a flex screen is fitted is it smooth and hung correctly
checkpoint | Is bistable shaft information installed in accordance with layout drawings
checkpoint | In case of halfway junction box is it securely mounted, earthed and neatly wired
checkpoint | Are inductor planes installed
checkpoint | Are well lights fitted, guarded and operating, including 2 way switching
checkpoint | Are door panels linked together for centre opening doors
checkpoint | Is well flushing adequate
checkpoint | Is minimum clearnace between car and structure greater than 20mm, car and cwt 25mm, 2 cars 100mm
checkpoint | Is equipment requiring service on car closer than 230mm adjacent lift car and if so is adequate screening
checkpoint | in place
checkpoint | Is screening in place between car and cwt of adjacent lift cars
checkpoint | Are air cord ends on doors tied off correctly and with no projection
checkpoint | Lift well ventilation installed in Lift well in accordance with drawings
checkpoint | Lift well ventilation tested and operational
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist | IMF08 -ITP10 - Lift Pit
section | Lift Pit Checks 1
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is the pit ladder installed in accordance with layout drawing (1200 mm above sill as per AS1735)
checkpoint | Is the pit shaft light correctly fitted with switch, labelled and accessible from the landing
checkpoint | Are the pit switches correctly fitted, earthed and accessible from landing and beneath landed car
checkpoint | Is the pit lighting adequate with a landed car
checkpoint | Is the position and height of car and counterweight in accordance with layout drawing
checkpoint | Are the buffers filled with the correct oil to correct level with buffer labels attached
checkpoint | Is the compensating pit sheave secure and installed in accordance with layout drawing
checkpoint | Is the compensating chain guide installed in accordance with layout drawing
checkpoint | Is the compensation sheave safety switch correctly aligned and earthed
checkpoint | Is the compensating chain running free and clear of obstacles and pit floor
checkpoint | Are lock down stops on compensating sheave bracket correct and operational
checkpoint | Are all compensating ropes of equal tension
checkpoint | Are compensating rope anchorage bolts corrected fitted, lock nutted and pinned
checkpoint | Are the anchorages of correct size, with rope ends made off and twist rope fitted
checkpoint | Is the governor rope jenny wheel tension device installed in accordance with layout drawing
checkpoint | Is the tension weight safety switch correctly aligned and earthed
checkpoint | Are all rope nip point guards fitted and effective
checkpoint | Is a counterweight screen fitted to a min height of 2000mm and clear of cwt and car by minimum of 25mm
checkpoint | Is the lift pit and sump clean and dry with floor flush, smooth, level and free of debris
checkpoint | Is a suitable lift pit sump cover provided flush with floor
section | Lift Pit Checks 2
checkpoint | Is the pit frame channel secure and free of rust
checkpoint | In case of adjustable guide rail base is a 3mm clearance provided
checkpoint | In the case of lubricated guide rails are suitable drip trays provided
checkpoint | Is the overtravel by-pass station suitably located with switch positions correctly marked
checkpoint | Is clearance under cwt with car at top landing less than R +460mm and greater than R+ 230mm for oil buffer
label | R+ 300mm for solid or spring buffer
label | (R= rope stretch allowance = 6.5 x rope length x 1 for 1:1 roping or 0.5 for 2:1 roping)
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist | IMF08 -ITP11 - Lift Car Interior
section | Lift Car Interior Checks 1
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Is superstructure installed in accordance with layout drawing and properly finished
label | Car dimensions (Clear of finishes): W 1100 mm; D 1400 mm
label | Minimum clear internal height: 2300 mm
checkpoint | Is floor covering provided with floor/sill free from trip hazards
label | Measured slip resistance rating: P2
checkpoint | Is lift car fixed ventilation adequate to floor area
checkpoint | Is lift car lighting adequate.
checkpoint | Are notices of load and telephone operation fitted and accurate including building address
checkpoint | Is the lift number clearly identified
checkpoint | Are all push button/switches and indicators operative
checkpoint | Are emergency stop and alarm buttons less than 1500mm from F.F.L.
checkpoint | Is car to motor room communication operative
checkpoint | Are emergency telephone, alarms operative
label | Out of hours emergency call redirects to United Lifts Services 24hrs answering service
checkpoint | If fire brigade intercom is provided does it function correctly
checkpoint | Is the emergency light/alarm power supply functioning correctly
label | Emergency lighting levels measured at car door way min 100 Lux
checkpoint | If car button isolation (security) is fitted is the switch operating correctly
section | Lift Car Interior Checks 2
checkpoint | Is the false ceiling secured and not impeding trap door access
checkpoint | Is the trap door size and position in accordance with layout drawings
checkpoint | Is the trap door fitted with an electro mechanic lock with standard TD key
checkpoint | Are all power door, passenger protective devices operating correctly
checkpoint | Does the trap door remain in the open position
checkpoint | Is the car ventilation fan operating quietly and efficiently and meets the required flow rate (8.5m3/s)
checkpoint | Do all car operating panels and doors close and lock easily and neatly
checkpoint | Car display indicator displays for the following conditions:
label | Not in service, Alarm activated, Emergency call, Fire mode, Independent mode
checkpoint | Is the car position indicator fitted and operational and higher than 1800mm from car floor
checkpoint | If a stretcher pocket is fitted does not door close and latch correctly
checkpoint | Has the anti srcratch and an graffiti film been installed
checkpoint | Car fan turns off automatically when there is no demand on the lift
checkpoint | Pressing any call or emergency button perates the car fan
checkpoint | UPS provices 2hrs backup in event of power loss
checkpoint | Minimum clear opening at door: W 900 mm; H 2100 mm
checkpoint | Car air conditioning fitted and working correctly with temperature control set at 24 deg
section | Lift Car Interior Checks 3
checkpoint | Battery Backup Drive ARD - Drive to Ground/ Level 1 and display "Not in Service" on all indication panels
checkpoint | Switches fitted for below
bool | Landing Operating Panel: Security, Fire service On-Off
bool | Car Operating Panel: Light On/Off/Test, Fire Service, Exclusive Service, Fan On/Off/Auto
checkpoint | Trip Meter - Provided in controller with minimim of 6 Dgigits and cannot be rest
checkpoint | Car overload warning - Signal provided with the car nor able to close doors or move from the floor
checkpoint | UP Runaway Protection - Provice and tested
checkpoint | Water sensors - Provided at 30 mm and 700mm in lift pit and tested
checkpoint | Temperature sensor - Provided at top of lift well and tested
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist | IMF08 -ITP12 - Hall Equipment
section | Doors and Frames
checkpoint | Latest IFC drawings checked & referenced
text | Drawing & Revision # (or Attach photo below)
checkpoint | Minimum clear opening at landing door (Ground level)
text | Width (mm)
text | Height (mm)
checkpoint | Minimum clear opening at landing door (Level 1)
text | Width (mm)
text | Height (mm)
checkpoint | Frame and door panel type as per layout drawing (construction as specified)
checkpoint | Frames fitted square and plumb (same height as adjacent frames)
checkpoint | Frames properly finished without scratches or dents
checkpoint | Car and landing sills parallel, clearance correct as per specification
checkpoint | Tracks and sills cleaned
checkpoint | Door panels hanging plumb, operating smoothly and quietly
checkpoint | Sight guards fitted
checkpoint | Door closer adjusted and operates freely through entire travel
checkpoint | Gap between door panels and jamb even (less than 5mm)
checkpoint | Well access devices fitted and operating correctly
section | Push Buttons and Indicators
checkpoint | Type of indicator fitted in accordance with appointment drawings
checkpoint | Type of hall push buttons fitted in accordance with appointment drawings
checkpoint | Indicator plates and button plates fitted square, plumb and flush to wall
checkpoint | Faceplates suitably finished and without damage
checkpoint | Faceplates have correct engraving "Do not use lifts if there is a fire"
checkpoint | Indicators working correctly
checkpoint | Gongs working correctly, pre-direction, reverse direction
checkpoint | Hall push buttons working correctly
checkpoint | Button and indicator plates correctly earthed
checkpoint | Out of Service" Indicators working correctly
checkpoint | Landing position indicator display "Not in Service" message when lifts are not operational:
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist-flat | IMF08 -ITP13 - Ride Comfort, Noise and Vibration
checkpoint | Device used to record car vibration, acceleration, decelartion and velocity: STEP
checkpoint | Device used to record sound meadurements: Db metre
checkpoint | Calibration date: 27/06/2018
checkpoint | Lift speed measured at: 1.0 m/s
checkpoint | Maximum acceleration 0.6 m/s (Device positioned at the centre of the lift car)
checkpoint | Maximum jerk: 1.3 m/s2 (On the floor and measurements commenced with doors)
checkpoint | Maximum latetal quaking: 1.5 mg (Held in the open position and call logged, to when the lift opens at the destination floor//0
checkpoint | Results provided in graphical format showing the different measured parametrs against time
checkpoint | Maximum noise in lift car: < 60 dBa
label | Measured at 1500mm flor and 1000mm from face of landing entrance and including the lift door face and includes opening and closing of doors
checkpoint | Maximum noise in lobby: < 60 dBa
label | Measured at 1500mm from the floor and 1000mm from face of landing entrance and including the doors opening and closing, lift traveling and fan operational
checkpoint | Door dwell time (Concourse level): 6 sec
checkpoint | Door open dwell time (Platform/ground level): 6 sec
checkpoint | Work(s) completed to specification/drawings
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checkpoint | HOLD POINT- Sign-Offs completed - Click to Attach Signature(s) below
button | Signature by Builders Site Coordinator - Attached below as applicable | Yes, No
button | United Lift Services Signature Sign-Off added below | Yes, No
checklist | IMF-35 - Schedule of Inspections and Tests
section | Shaft
checkpoint | Check shaft as follows
label | Shaft - Positions and dimensions are within tolerances
label | Shaft - Surface finishes smooth and Free from irregularities
label | Shaft - Guide rail bond blocks for type, material, size, position and fixings if applicable
label | Shaft - Width of landing nosing projection
label | Shaft - Smoke vent penetration for size and position
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS work instruction
label | ULS procedure
label | Frequency: Prior to starting lift installation onsite
label | Acceptance Criteria: Approved layout Drawings
label | Acceptance Criteria: Front Walls +12 to -0mm
label | Acceptance Criteria: Side and rear walls +25 to -0mm
label | .. ..
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Pit
checkpoint | Check pit as follows
label | Pit - Dimensions are within tolerances
label | Pit - Surface finishes
label | Pit - Light fittings and power outlets type, position
label | Pit - Plinths and kerbs for Penetrations and castins
label | Pit - Sumps for size & Position
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS work instruction
label | ULS procedure
label | Frequency: Prior to starting lift installation onsite
label | Acceptance Criteria: Approved layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
bool | Layout Drawing
section | Builders Work
checkpoint | Check Builders Work - Structural door openings
label | Dimensions are within tolerances
label | Surface finishes square
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | Frequency: Upon to Installation
label | Acceptance Criteria: BCA
label | Acceptance Criteria: Fire regulations
label | Acceptance Criteria: AS:1735 & EN81.20
label | Acceptance Criteria: Approved layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check Builders Work - Pockets for hall lanterns and buttons
label | Type and material
label | Colour and finish
label | Size and thickness
label | Alignment, square
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | Frequency: Upon to Installation
label | Acceptance Criteria: AS:1735 & EN81.20
label | Acceptance Criteria: Approved layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Ladders & Metalwork
checkpoint | Check ladders and metalwork in lift pit
label | Type and material
label | Size
label | Positions
label | Fixings and Supports
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon to Installation
label | Acceptance Criteria: Approved Drawings
label | Acceptance Criteria: Vendor QA Plan
label | Acceptance Criteria: AS:1735 & EN81.20
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
bool | Records/Remarks: Compliance Certificate
section | Lift Car
checkpoint | Check lift car - Platform and Framing
label | Materials
label | Dimensions
label | Joints and Connections
label | Vibration Dampers
label | Threshold Plate
label | Reinforcement of Roof
label | Maintenance Platform
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon to Installation
label | Acceptance Criteria: Approved Drawings
label | Acceptance Criteria: Vendor QA Plan
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
bool | Records/Remarks: Threshold Concrete by Builder
checkpoint | Check lift car - Superstructure
label | Materials
label | Dimensions
label | Services light, power outlets and access panel on roof
label | Type and Material
label | Fixings and Supports
label | Position
label | Markings
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Work Instruction
label | Frequency: Upon to Installation
label | Acceptance Criteria: Approved Drawings
label | Acceptance Criteria: AS:1735
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Buffers and Supports
checkpoint | Check buffers and supports
label | Type and Material
label | Fixings and Supports
label | Position
label | Markings
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon to Installation
label | Acceptance Criteria: Approved Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Guides
checkpoint | Check Guide Rails
label | Type and Material
label | Size
label | Joints and Base Connections
label | Fixings and Supports
label | Position
label | Verticality and Alignment
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon to Installation
label | Acceptance Criteria: Approved Layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check Guide Shoes
label | Type and Material
label | Fixings and Supports
label | Position
label | Provision for Adjustment
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon to Installation
label | Acceptance Criteria: Technical Specification
label | Acceptance Criteria: Approved Layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Mechanical Safety Devices
checkpoint | Check Installed Mechanical Safety Devices
label | Type
label | Position and Supports
label | Access for Lubrication, Inspection and Repairs
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon to Installation
label | Acceptance Criteria: AS:1735 & AS:3000
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Counterweights
checkpoint | Check Counterweights
label | Type
label | Weight
label | Frame
label | Screen
label | Fixings
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon to Installation
label | Acceptance Criteria: Approved Layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Hoisting Machines
checkpoint | Check Hoisting Machines - Drive Unit and Gearbox
label | Type
label | Capacity
label | Lubrication and Inspection
label | Instruments and Data Plates
label | Isolating Filters
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Prior to Delivery Upon Completion
label | Acceptance Criteria: Approved Layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check Hosting Machines - Drive Sheaves
label | Grooves for type, number and diameter
label | Alignment and Position
label | .. ..
label | Frequency: Prior to Delivery Upon Completion
label | Acceptance Criteria: Technical Specification
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check Hosting Machines - Brakes
label | Type
label | Position
label | Facility for adjusting shoes
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Work Instruction
label | Frequency: Prior to Delivery Upon Completion
label | Acceptance Criteria: Technical Specification
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check structural works lift motor room (MRL N/A)
label | Dimensions within tolerances
label | Surface Finishes
label | Light fittings and power outlets for approved types, position, fixing and wiring
label | Ventilation
label | Plinths and kerbs checked for levels, size and position
label | Penetrations, cast-in anchors and fixings in floors and walls checked for size and position
label | Machine and trimming beams checked for type, material, size, levels, clearance from floor, position and fixings
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Prior to Start of lift installation in lift motor room
label | Acceptance Criteria: Mechanical Layout drawings
label | BCA
label | AS:1735
button | Verification Inspection by United Lift Services | Yes, No, N/A
button | Verification by Client Representative | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check Installed Hosting Machines
label | Type & Size
label | Make & Model No.
label | Capacity/Output
label | Fixings and supports
label | Mountings and vibration pads
label | Position
label | Access for Lubrication
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: Technical Specification
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Governors
checkpoint | Check Speed Governors
label | Type
label | Capacity
label | Control Switch
label | Facility for Adjustment
label | Data plate
label | Position and Supports
label | Access for lubrication, inspection and repairs
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: AS:1735
label | Lift Layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Sheaves
checkpoint | Check Installed Sheaves
label | Grooves for type, number and diameter
label | Alignment and Position
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: ULS Procedure
label | Frequency: Upon Installation
label | Acceptance Criteria: Lift Layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Ropes
checkpoint | Check Installed Ropes
label | Size and Capacity
label | Connections and Anchorage's
label | Separators and anti-twist
label | Lubricating and rust inhibiting compound
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: ULS Procedure
label | Project Specification
label | Clause: N/A
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: AS:1735
label | Lift Layout Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Guards and Screens
checkpoint | Check Guards and Screens
label | Type and Material
label | Dimensions within tolerances
label | Fixings and Supports
label | Position
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: ULS Procedure
label | Project Specification
label | Clause: N/A
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: AS:1735
label | Lift Layout Drawings
button | Verification Inspection by Subcontractor/Supplier | Yes, No, N/A
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Lift Car Finishes
checkpoint | Check lift car fit - Finishes to car and doors
label | Type and Material
label | Colour and FInish
label | Size and Thickness
label | Joints and Connections
label | Alignment and Position
label | Square and flatness
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: Architects Specifications
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: AS:1735
label | Approved Appointment Drawings
button | Verification Inspection by Subcontractor/Supplier | Yes, No, N/A
button | Witness Inspection by United Lift Services | Yes, No, N/A
button | Witness Inspection by Client Representative | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check lift car fit - Car Operating Panels
label | Material
label | Colour and FInish
label | Size
label | Position
label | Switches and Indicators
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: Architects Specifications
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: AS:1735
label | Approved Appointment Drawings
button | Verification Inspection by Subcontractor/Supplier | Yes, No, N/A
button | Witness Inspection by United Lift Services | Yes, No, N/A
button | Witness Inspection by Client Representative | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check lift car fit - Services and Safety Facilities
label | Lighting and Ventilation checked for type and position
label | Recess in door for Telecom approved handset, position and notice
label | Fire Brigade intercom in fire lifts (Where specified), checked for type, position and notice
label | Alarm bells checked for type and position
label | Emergency lighting checked for type and position
label | Door protective devices checked for type and position
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | Frequency: Upon Installation
label | Acceptance Criteria: AS:1735
label | Approved Appointment Drawings
button | Verification Inspection by Subcontractor/Supplier | Yes, No, N/A
button | Witness Inspection by United Lift Services | Yes, No, N/A
button | Witness Inspection by Client Representative | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check door frames, bottom tracks, sill plates and locks
label | Materials and finishes
label | Clear opening sizes
label | Size and profile of members
label | Fixings and supports
label | Grouting and grout guard
label | Straightness and alignment
label | Free form wrapping, bulging etc
label | Door locks checked for type, material, position, fixings and supports
label | Provision of maintenance unlocking device in top and bottom landing door frames for means of operation and location of key in box room *
label | *MRL NA re KEY
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: Approved Design Drawings
label | Fire Assessment Report
button | Verification Inspection by Subcontractor/Supplier | Yes, No, N/A
button | Witness Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
bool | Lift Landing Door and Frame Acceptance Compliance Certificate
checkpoint | Check flushing panel and sills
label | Material and FInish
label | Size
label | Position
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: Approved Design Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check landing door panels
label | Materials
label | Colour and finish
label | Size and thickness
label | Joints and connections
label | Position
label | Alignment
label | Square and flatness
label | Free from visible joints, wanes, bulges, dents and dishing
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | ULS Work Instruction
label | Frequency: Upon Installation
label | Acceptance Criteria: Approved Design Drawings
label | Fire Assessment Report
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
bool | Lift Landing Door and Frame Acceptance Compliance Certificate
checkpoint | Check closing devices
label | Check door closing devices for correct type
label | Check door protective devices for type and position
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Acceptance Criteria: Approved Design Drawings
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
bool | Compliance Certificate
section | Electrical Services
checkpoint | Check electrical services - Conduits and/or trunking
label | Type and material
label | Grade
label | Size, gauge and capacity
label | Section/profile
label | Joints and connections
label | Fixings and supports
label | Free from crimping at bends
label | Cleaned out prior to drawing cables
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Upon Installation
label | Acceptance Criteria: AS:1735
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check electrical services - Cabling
label | Type and material
label | Grade
label | Size and capacity
label | Joints, connections and terminations
label | Bends not less than specified Radii
label | Separation of cables
label | Fixings and supports
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | Acceptance Criteria: Approved Design Drawings
label | AS:1735
label | AS:3000
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Check electrical services - Equipment, Switching and Controls
label | Type and material
label | Make and model No.
label | Size
label | Capacity / Output
label | Fixings and supports
label | Position
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | Frequency: Upon Installation
label | Acceptance Criteria: AS:1735
label | AS:3000
button | Verification Inspection by United Lift Services | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Test Electrical circuits
label | Insulation resistance
label | Earthing Continuity
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | Frequency: Upon Installation
label | Acceptance Criteria: Mark up prints
label | AS:3000
label | AS:1735
button | Verification Inspection by United Lift Services | Yes, No, N/A
button | Witness Inspection by Regulatory Authority | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
section | Functionality
checkpoint | Check landing buttons, hall lanterns and face plates
label | Size
label | Position
label | Statutory warning notices
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Upon Installation
label | Acceptance Criteria: Approved Design Drawings
button | Verification Inspection by Subcontractor/Supplier | Yes, No, N/A
button | Witness Inspection by Regulatory Authority | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
checkpoint | Lift design registration Registered design
label | Worksafe Victoria Plant/ Design registration
label | .. ..
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Prior to Practical Completion
label | Acceptance Criteria: AS:1735
label | EN81.20
label | AS:3000
button | Verification Inspection by United Lift Services | Yes, No, N/A
button | Verification Inspection by Client Representative | Yes, No, N/A
bool | Records/Remarks: WSV Registration
section | Handover & Documentation
checkpoint | Obtain As-Built Documents
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Prior to Practical Completion
label | Acceptance Criteria: AS:1735
label | EN81.20
button | Verification Inspection by United Lift Services | Yes, No, N/A
button | Verification Inspection by Client Representative | Yes, No, N/A
button | Verification Inspection by Head Contractor | Yes, No, N/A
bool | Records/Remarks: Mechanical Drawing Transmittal & Register Transmittal
checkpoint | Procedure operating and maintenance manuals
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Prior to Practical Completion
label | Acceptance Criteria: ULS Quality Plan
label | EN81.20
button | Verification Inspection by United Lift Services | Yes, No, N/A
button | Verification Inspection by Client Representative | Yes, No, N/A
button | Verification Inspection by Head Contractor | Yes, No, N/A
bool | Records/Remarks: Transmittal Draft O&M Manual
checkpoint | HOLD POINT - Obtain Guarantees (If Applicable)
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Prior to Practical Completion
button | HOLD POINT - Inspection by Head Contractor | Yes, No, N/A
bool | Records/Remarks: Bank Guarantees
checkpoint | Final Commissioning
label | Operation of:
label | Lift Controls
label | Doors
label | Safety Devices
label | Hall lanterns and buttons
label | Lift car facilities
label | Automatic levelling
label | Inspection and Tests Plan details
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Prior to Practical Completion
label | Acceptance Criteria: Mark up prints
label | AS:1735
label | EN81.20
label | AS:3000
button | Verification Inspection by United Lift Services | Yes, No, N/A
button | Witness Inspection by Regulatory Authority | Yes, No, N/A
button | Witness Inspection by Client Representative | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
bool | ULS Test and Commissioning Checklist
checkpoint | FINAL INSPECTION - Including review of records all above items
label | Methods/References: Project Specification
label | Clause: N/A
label | ULS Procedure
label | Frequency: Prior to Practical Completion
label | Acceptance Criteria: Project Handover Documentation
label | AS:1735
label | EN81.20
label | AS:3000
button | Verification Inspection by United Lift Services | Yes, No, N/A
button | Witness Inspection by Regulatory Authority | Yes, No, N/A
button | Witness Inspection by Client Representative | Yes, No, N/A
button | Witness Inspection by Head Contractor | Yes, No, N/A
bool | Records/Remarks: IMF-08- Completion Checklist - Elevator completed
bool | ULS Test and Commissioning Checklist
bool | Final O&M Manual
checklist | IMF Site Pre-start Checklist
checkpoint | Undercover site storage ready for lift components near lift shaft.
checkpoint | All builders’ shaft works completed – e.g. joints are caulked, structural brackets welded, bond blocks and penetrations cleaned.
checkpoint | Lift shaft and pit clean and dry.
checkpoint | Lifting hooks are installed in correct location.
checkpoint | Structural openings according to shop drawings.
checkpoint | Clear access in front of all door openings.
checkpoint | Finished floor levels marked 1 meter above FFL.
checkpoint | Building grid lines marked in front of lift shaft (to enable shaft set outs to be completed).
checkpoint | Controller location is protected from wind driven rain and can be accessed at all times.
checkpoint | 2x32amp socket outlets (three phase earth and neutral) per lift available within 5 mts of control panel(s) location.
checkpoint | Single phase temporary power available within 5 meters of lift shaft(s).
checkpoint | Appropriate site amenities available for ULS staff.
checkpoint | Person Responsible for ensuring these works are complete: