## Project Structure
Bankstown Airport ITP Layout
Building | Equipment Name | ITP Name
Warehouse 1 A
| ACU-1A.1 GF | Split Ducted AC Unit
| ACU-1A.2 FF | Split Ducted AC Unit
| TEF-1A Roof | Roof Mounted Toilet Exhaust Fan
| MCP-1A GF | Mechanical Control Panel
Warehouse 1 B
| ACU-1B.1 GF | Split Ducted AC Unit
| ACU-1B.2 FF | Split Ducted AC Unit
| TEF-1B Roof | Roof Mounted Toilet Exhaust Fan
| MCP-1B GF | Mechanical Control Panel
Warehouse 2 A
| ACU-2A.1 GF | Split Ducted AC Unit
| ACU-2A.2 FF | Split Ducted AC Unit
| TEF-2A Rof | Roof Mounted Toilet Exhaust Fan
| MCP-2A GF | Mechanical Control Panel
Warehouse 2 B
| ACU-2B.1 GF | Split Ducted AC Unit
| ACU-2B.2 FF | Split Ducted AC Unit
| TEF-2B Roof | Roof Mounted Toilet Exhaust Fan
| MCP-2B GF | Mechanical Control Panel
Warehouse 3 A
| ACU-3A.1 GF | Split Ducted AC Unit
| ACU-3A.2 FF | Split Ducted AC Unit
| TEF-3A Roof | Roof Mounted Toilet Exhaust Fan
| MCP-3A GF | Mechanical Control Panel
Warehouse 3 B
| ACU-3B.1 GF | Split Ducted AC Unit
| ACU-3B.2 FF | Split Ducted AC Unit
| TEF-3B Roof | Roof Mounted Toilet Exhaust Fan
| MCP-3B GF | Mechanical Control Panel
Warehouse 3 C
| ACU-3C.1 GF | Split Ducted AC Unit
| ACU-3C.2 FF | Split Ducted AC Unit
| TEF-3C Roof | Roof Mounted Toilet Exhaust Fan
| MCP-3C GF | Mechanical Control Panel
Warehouse 4 A
| ACU-4A.1 | Split Ducted AC Unit
| TEF-4A Roof | Roof Mounted Toilet Exhaust Fan
| MCP-4A | Mechanical Control Panel
Warehouse 4 B
| ACU-4B.1 | Split Ducted AC Unit
| TEF-4B Roof | Roof Mounted Toilet Exhaust Fan
| MCP-4B | Mechanical Control Panel
Warehouse 4 C
| ACU-4C.1 | Split Ducted AC Unit
| TEF-4C Roof | Roof Mounted Toilet Exhaust Fan
| MCP-4C | Mechanical Control Panel

## ITP's
ITP Checklists
Type | Name | Values
checklist | Split Ducted AC Unit
section | General
checkpoint | Area ready and accessible for work - take picture of all
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing - Record Drawing Number
checkpoint | Coordination with other services
section | Pipework
checkpoint | Pipework roughin complete
checkpoint | All insulation joints glued - test and photograph
checkpoint | Drain roughin - Pressure Pipe - Green Glue
checkpoint | All horizontal drain runs insulated
checkpoint | Traps on FCU and Safety Tray installed (if required)
checkpoint | Drain Test - min 1L
section | Fan Coil Unit
checkpoint | Correct Fan Coil Installed - Record Serial Number
checkpoint | Seismic mounts installed as per drawing (M12 Rod with Hilti HSC-I Anchors into concrete)
checkpoint | R/A Plenum with filters installed (Check filter access both sides)
checkpoint | Anti Vibration mounts fitted to FCU and R/A plenum
checkpoint | R/A and S/A hard connections (not canvas)
checkpoint | R/A and S/A connections lagged
checkpoint | Drain roughin from FCU to tundish point - horizontal runs insulated
text | Number and Size of filters
section | Duct Work
checkpoint | Duct work installed with clearance from other services
checkpoint | Duct work adequately supported with anti vibration mounts (where required)
checkpoint | Duct work sealed through walls
checkpoint | Dampers 100% open
checkpoint | Flex installed and adequately supported (with Gutterguard)
checkpoint | Outside Air connected
checkpoint | Access panel installed (by others) - [If required]
checkpoint | Grilles installed
section | Electrical
checkpoint | Electrical interconnect roughed in
checkpoint | Fan coil and condenser terminations complete
checkpoint | Control Pad cable roughed in
checkpoint | Control Pad fit off
checkpoint | Electrical supply roughed in (dektites for roof penetration)
checkpoint | Isolator installed adjacent to condenser and Sealed
checkpoint | Power available
section | Condenser
checkpoint | Roof Platform Installed (by others)
checkpoint | Penetration through roof sealed and turned down
checkpoint | Correct Condenser installed - Record Serial Number
checkpoint | Condenser mounts installed - Rubber Feet and loose bolted to suit seismic requirements
checkpoint | System pressure tested for 24 hours - 3500 KPA
checkpoint | System evacuated
checkpoint | Additional refrigerant charge - Record amount + Write on indide of condenser service panel
checkpoint | System test run on Cooling cycle and Heating cycle (minimum 2 hours each)
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
0
checklist | Roof Mounted Toilet Exhaust Fan
section | General
checkpoint | Area ready and accessible for work - take picture of all
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | Correct Fan Installed - Record Serial Number
checkpoint | Coordination with other services
section | Ductwork
checkpoint | Dropper installed in shaft and sealed to underflashing
checkpoint | VCD Installed
checkpoint | Fan sealed to duct with foam tape
checkpoint | Overflashing installed
checkpoint | Fan secured to duct with a minimum of 4 screws
checkpoint | Duct work installed with clearance from other services
checkpoint | Duct work adequately supported
checkpoint | Duct work sealed through walls
checkpoint | Dampers 100% open
checkpoint | Flex installed and adequately supported (with Gutterguard)
checkpoint | Grilles Installed
section | Electrical
checkpoint | Equipment Isolator - installed and correctly labelled
checkpoint | Electrical Isolator, Decktite and Conduit - all sealed with silicon
checkpoint | Electrical terminations - all terminations complete
section | Handover
checkpoint | Handover - Work completed as per specification, checked and accepted
Checklist | Mechanical Control Panel
section | General
checkpoint | Area ready and accessible for work - take picture of all
checkpoint | Inspect - Materials free from Damage
checkpoint | Location Correct As per Plan/Drawing
checkpoint | Electrical Mains supplied by others
checkpoint | Electrical Mains correct size
checkpoint | Coordination with other services
section | Mounting
checkpoint | Wall mounts adequate for control panel
checkpoint | Cabling concealed and supported in wall
section | Electrical
checkpoint | Electrical terminations - all terminations complete
section | Handover
checkpoint | FIP Interface Connected
checkpoint | Fire Trip Tested - Passed
checkpoint | Handover - Work completed as per specification, checked and accepted