## res_1630-P200-SYM-QAC-ITP-0013.
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 1630-P200-SYM-QAC-ITP-0021 Conduit and Pit Installation | [5 empty] | 1630-P200-SYM-QAC-ITP-0021 Conduit and Pit Installation
section | 1.0 Pre-start activities
checkpoint | 1.1 - Boring under Carriageways
label | Ref docs - VR Clause 733.05
label | Acceptance criteria - Boring by water jet not permitted.
label | • Detailed proposals for boring under carriageways shall be submitted to the superintendent for review two weeks prior to the programmed commencement of work.
button | Approval to proceed? | Yes,No,N/A
label | Freq - Prior to start of works
label | Key - H
label | Resp - SE
label | SI Key - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint-no-status | 1.1.1 - Lot Map
button | Lot map | Yes,No,N/A
checkpoint-no-status | 1.1.2 - Environmental Permit
button | Environmental permit | Yes,No,N/A
section | 2.0 Conduit Materials
checkpoint | 2.1 - Material Conformance – Conduits and bends
label | Ref docs - VR Clause 733.02 Table 733.041
label | Acceptance criteria - Conduits are correct type, class & diameter and comply with AS1477, AS2053, AS4130 (as relevant), unless noted otherwise.
label | • Electrical – Heavy Duty Grade, Rigid orange UPVC conduit to AS/NZS 2053.2.
label | • Communications – Heavy Duty Grade, Rigid White UPVC communication conduit to AS/NZS 2053.2.
button | Have all the above materials been approved? | Yes,No
label | Freq - Each Lot & Each possession
label | Key - R
label | Resp - SE
label | Remarks/record -
button | • Supplier Compliance Certificate | Yes,No
section | 3.0 Conduit Cover
checkpoint | 3.1 - Excavation and Cover Requirements
label | Ref docs - VR Clause 733.05 Table 733.051
label | Acceptance criteria - Cover requirements for both electrical and communications conduits shall be:
label | • Pavement surface to top of conduit minimum 1200 mm.
label | • Invert of open drain to top of conduit minimum 750 mm.
label | • Unpaved areas to top of conduit minimum 600 mm.
label | ○ Or else as specified on design drawings.
button | Has all the above been completed and approved? | Yes,No
label | Freq - Each Lot & Each possession
label | Key - S
label | Resp - SE
section | 4.0 Installation of Conduits
checkpoint | 4.1 - General
label | Ref docs - VR Clause 733.06 Table 733.061 AS/NZS 3000 AS/ACIF S009
label | Acceptance criteria - All conduits shall be installed as shown on the VicRoads Standard Drawings and Contract specific drawings, or as otherwise specified.
label | All conduits for electrical and communications cabling shall be installed to conform to the relevant requirements of controlling legislation, regulations, industry codes and standards, including:
label | • AS/NZS 3000 Electrical installations (Australian/New Zealand Wiring Rules)
label | • AS/ACIF S009 Installation requirements for customer cabling (Wiring Rules), and any other relevant requirements of the Australian Communications and Media Authority (ACMA) for connections to telecommunication carriers’ network.
label | ○ Installation of conduits shall be carried out in accordance with the following:
label | • HD UPVC Plain to be Thrust bore or Open Trench.
label | • HDPE continuous (must have ID not less than that of 100 mm HD UPVC for electrical and 90 mm HD UPVC for communications) to be Directional Bore.
label | Freq - Each Lot
label | Key - I
label | Resp - SE
checkpoint | 4.2 - Bedding Material/Placement
label | Ref docs - VR Clause 733.08
label | Acceptance criteria - Bedding material does comply with the requirements of Table 733.081.
label | • Minimum 80 mm bedding below conduits on earth foundation.
label | • Minimum 200 mm bedding below conduits on rock foundation.
label | • Bedding placed to full width of trench, and between conduits as shown on trench details on latest revision IFC drawings.
label | • Shaped sufficiently to maintain the conduit in line as the sections are placed.
button | Has all the above been completed? | Yes,No
label | Freq - Each Lot
label | Key - I
label | Resp - SE
label | Remarks/record -
button | • Material Compliance for Bedding/NATA Test Report | Yes,No
checkpoint | 4.3 - Bedding Material/Placement
label | Ref docs - VR Clause 733.08
label | Acceptance criteria - Once the bedding material has been laid and the conduits put in place, works shall not proceed prior to inspection by Superintendent.
button | Approval to proceed? | Yes,No
label | Freq - Each Lot
label | Key - H I
label | Resp - SE
label | SI Key - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Bedding Material/Placement
label | Ref docs - VR Clause 733.08
label | Acceptance criteria - When conduit sections are in position, additional layers of bedding material shall be placed and compacted to a height 150 mm above the bedding previously placed.
label | • Bedding material must not be the same material excavated for the trench, it shall be clearly identifiable as introduced material.
button | Has all the above been completed? | Yes,No
label | Freq - Each Lot
label | Key - I
label | Resp - SE
checkpoint | 4.5 - Conduits for Traffic Signals/ITS/Public Lighting
label | Ref docs - VR Clause 733.06
label | Acceptance criteria - a) All conduits shall terminate in a pit in accordance with VicRoads Standard Drawing TC 1207, TC-1230 and TC-2200 – TC223.
label | b) Only one size conduit shall be used for a complete run between pits; unequal size conduits shall not be joined in the ground.
label | c) All conduits shall be temporarily sealed prior to cabling to avoid blockage.
label | d) Changes in conduit direction or depth shall be made by natural set or in the case of bottom entry, by means of a swept bend; elbows or tees shall not be used.
label | e) All conduit joints shall be correctly prepared and sealed with approved solvent cement.
label | f) Conduits for detector cables shall be installed as shown in VicRoads Standard Drawings TC 1207 and TC 1320; and
label | • A 50 mm electrical (orange) conduit shall be used to convey the detector feeder cable from the detector pit to the cable pit, as shown in VicRoads Standard Drawing TC 1207.
button | Has all the above been completed correctly and to a high standard? | Yes,No
label | Freq - Each Lot
label | Key - S I
label | Resp - SE
label | Remarks/record -
button | • Installation Records from Subcontractor | Yes,No
checkpoint | 4.6 - Draw Cords
label | Ref docs - VR Clause 733.07
label | Acceptance criteria - Draw Cords to be 3 mm diameter and with a minimum breaking strain of 1.6 kN.
label | ○ Where the conduit terminates in a pit
label | • Have no less than 500 mm of the draw cord tied to a marker peg 25 mm x 25 mm, no less than 300 mm long, left coiled in the pit for future use.
label | ○ Where conduits do not terminate into a pit.
label | • Be tied to a marker peg 100 mm x 100 mm, not less than 400 mm long, driven firmly into the ground with the top 50 mm projecting above finished surface and painted yellow.
button | Has all the above been completed correctly and to VicRoads standard? | Yes,No,N/A
label | Freq - Each Lot
label | Key - I
label | Resp - SE
label | Remarks/record -
button | • Installation Records from Subcontractor | Yes,No
button | • Material Conformance Certificate | Yes,No
section | 5.0 Backfill
checkpoint | 5.1 - Bore access excavation
label | Ref docs - VR Clause 733.05
label | Acceptance criteria - Before backfilling the bore access excavation, the pressure grouting shall be inspected by the superintendent or representative.
button | Has all the above been completed? | Yes,No
label | Freq - Each Lot
label | Key - H
label | Resp - SE
label | SI Key - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Material Properties
label | Ref docs - VR Clause Table 733.081
label | Acceptance criteria - Backfill material properties to be as per Table 733.081.
button | Has all the above been completed? | Yes,No
label | Freq - Each Lot
label | Key - R
label | Resp - SE
label | Remarks/record -
button | • NATA Test Report (if applicable) | Yes,No
checkpoint | 5.3 - Filling
label | Ref docs - VR Clause 733.08
label | Acceptance criteria - Unless otherwise specified or shown on the drawings, selected and common backfill shall be placed and compacted as follows under, around, and above the conduit after the sections are bedded:
label | • Place and compact selected backfill 400 mm above bedding (in non-trafficable areas) remaining fill to be common backfill.
label | • Place and compact selected backfill to subgrade level (in area’s to be paved)
label | Freq - Each Lot
label | Key - R
label | Resp - SE
checkpoint | 5.4 - Compaction - Areas not to be paved and below pavement
label | Ref docs - VR Clause 733.08
label | Acceptance criteria - All pavement material shall have during compaction, uniform moisture content within the range 85% to 115% of the optimum moisture content as determined in the Modified Compaction test.
label | • Compacted to refusal using handheld mechanical equipment.
button | Has all the above been completed? | Yes,No
label | Freq - Each Lot
label | Key - R
label | Resp - SE
checkpoint | 5.5 - Compaction – Area’s pavement layer
label | Ref docs - VR Clause 733.08
label | Acceptance criteria - Where specified, pavement material shall be assessed for compaction in lots as defined in Section 173. The number of tests per lot shall be three.
label | • All pavement material shall have during compaction, uniform moisture content within the range 85% to 115% of the optimum moisture content as determined in the Modified Compaction test.
label | • All pavement layers shall be placed and compacted in layers to a density ratio of not less than 98%. The calculation of density ratio shall be based on Modified compactive effort.
label | • Compacted to refusal using handheld mechanical equipment.
button | Has all the above been completed? | Yes,No
label | Freq - Each Lot
label | Key - R
label | Resp - SE
label | Remarks/record -
button | • NATA Test Report (if applicable) | Yes,No
checkpoint | 5.6 - Warning Tape
label | Ref docs - AS/NZS2648.1
label | Acceptance criteria - Where marker tapes overlap electrical tape to overlay communications tape:
label | • Marker tape 100 mm wide complying with AS/NZS2648.1 coloured orange with black lettering “DANGER BURIED ELECTRIC CABLE BELOW” inscribed at regular intervals installed 300 mm above the conduits in all trenches where electrical conduits are provided.
label | • Marker tape 100 mm wide with two stainless steel tracer wires coloured white with black lettering “DANGER BURIED COMMUNICATION CABLE BELOW” inscribed at regular intervals installed 300 mm above the conduits. In all trenches where communication conduits are provided at least two meters of each tracer wire shall be anchored to and neatly coiled in each communication pit.
label | • Where both electrical and communication conduits are provided in a trench two marker tapes shall be provided one for electrical and the other for communication conduits.
button | Has all of the above been completed? | Yes,No
label | Freq - Each Lot
label | Key - S
label | Resp - SE
section | 6.0 Installation of Pits, Lids and Cables
checkpoint | 6.1 - Cable Pits & Pit Lids
label | Ref docs - VR Clause 733.09
label | Acceptance criteria - Before the pit lid surround or pre-formed collar is cemented into position an inspection by VicRoads Superintendent or representative must be carried out.
label | • Install cable pits in accordance with the design drawings and VicRoads Standard Drawings TC-1210, TC-1220 and TC-1230, TC2200-TC2232.
label | • Top of pit lid matches the surrounding finished surface level fits neatly without movement.
label | • Pits watertight and suitably drained.
label | • All conduit connections to cable pits shall be neatly made and the ends of the conduits trimmed off and fitted with a conduit bush. The area between the conduit bush and pit wall shall be stopped with a suitable sealant that bonds to the pit wall and the conduit.
label | • Heavy Duty Pit lids provided for pits in the road pavement.
button | Has all of the above been completed correctly and to a high standard? | Yes,No,N/A
label | Freq - Each Pit & Each possession
label | Key - S I
label | Resp - SE
label | SI Key - H I
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.2 - Detector Pits for Traffic Signals
label | Ref docs - VR Clause 733.10
label | Acceptance criteria - Install detector pits in accordance with the design drawings and VicRoads Standard Drawings TC-1310 and TC-1320.
label | • Fix pit cover securely using the fixing device supplied.
button | Has all the above been completed correctly and to a high standard? | Yes,No,N/A
label | Freq - Each Lot
label | Key - S
label | Resp - SE
section | 7.0 Completion
checkpoint | 7.1 - As-built Information
label | Ref docs - VR Clause 733.12
label | Acceptance criteria - Identification and recording as follows:
label | • All conduit locations not identified by pits immediately installed at the ends shall be marked with pegs 75 x 38 mm stakes projecting 0.4 m above the ground, with the top 150 mm painted yellow, or as otherwise agreed by the Superintendent.
label | • Conduits under road pavement shall be marked with stakes clear of the road pavement.
label | • Conduits not under road pavement shall be marked with stakes at the ends, at changes of direction, and at intervals of not more than 30 m.
label | • The actual installed location and depth of conduits on the as-built drawings.
button | Has all the above been completed correctly and to a high standard? | Yes,No,N/A
label | Freq - Each Lot
label | Key - R
label | Resp - SE
label | Remarks/record -
button | • Survey Conformance Report | Yes,No
section | 8.0 Work Lot Close Out
checkpoint | 8.1 - Test Reports
label | Ref docs - VIC Roads Specifications
label | Acceptance criteria - All Test reports received and reviewed.
button | Has all the above been proven to meet and/or exceed minimum tested requirements? | Yes,No
label | Freq - Each Lot
label | Key - R I
label | Resp - SE
label | Remarks/record -
button | • NATA Endorsed Test Reports | Yes,No
checkpoint | 8.2 - Product Non-Conformance
label | Ref docs - CQMP
label | Acceptance criteria - All Product Non-Conformance(s) recorded and closed (if applicable)
button | Has all the above been proven to meet and/or exceed minimum tested requirements? | Yes,No
label | Freq - Each Lot
label | Key - R
label | Resp - SE
label | Remarks/record -
button | • NCR reports | Yes,No
checkpoint | Works complete
text | Name:
text | Position:
text | Date Completed:
holdpoint | Sign ITP
checkpoint | Lot Conformance
dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | Lot opened date:
text | Lot opened by:
text | Date lot closed:
button | NCR raised? | Yes, No
text | NCR Raised Date:
button | NCR closed? | Yes, No
text | NCR Closed Date:
text | NCR Number:
text | Comments
holdpoint | Sign ITP