## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
2a137d84-cdf9-40ab-be63-48fb0850fd2c | checklist | Colphene Uni NG Riser Pit (ITC) |  | Colphene Uni NG Riser Pit (ITC) |  | 66483389-e8f8-4a8c-b149-130d03e504e6
226addae-abb4-43a4-a65a-4fa3f1875217 | section | Details
c3d55f82-0daa-4630-99b3-52e79f5ef482 | checkpoint | Substrate - To Pile Base
c2cc497a-8444-5fff-9631-ab9a10d5a42f | button | All surfaces dry, clean, smooth and free from sharp objects, laitance, oils, grease or any foreign materials which may inhibit or reduce adhesion. | Yes,No
3aa758d9-2654-5563-96c0-f2c4bb5deec0 | button | Commencement of installation shall be taken as acceptance of the substrate by the Applicator | Yes,No
c1bb9b38-063c-4d4b-b7ce-b887b115f832 | checkpoint | Colphene BSW UNI NG - To Raft Slab
5f17449b-4f0d-5725-ac86-ce0414158842 | button | Confirm rolls stored upright, with the selvedge side on top. If the product is stored outdoors confirm covered with an protective cover | Yes,No
59906662-7e5a-5ced-b989-3536b6bcec18 | button | Check COLPHENE BSW UNI NG thickness is 4mm | Yes,No
8617d554-d0b8-5f59-a820-4cfcdce80649 | button | Apply COLPHENE BSW UNI NG loose laid on blinding concrete | Yes,No
3385c9b4-c4e5-5f50-8b21-fc58fa5ddf52 | button | Confirm minimum 100 mm side overlap | Yes,No
d62fe843-27d0-5765-936d-61149f5cc37f | button | Confirm minimum 150 mm end lap between each strip | Yes,No
729c4898-a9de-5bde-8b13-68a12b9a3c8a | button | Confirm end laps are staggered by at least 300 mm | Yes,No
b11259a7-01d3-5c18-a221-87a2a3a590d3 | button | Confirm laps avoid excessive layering | Yes,No
95b4427a-4f9f-5fdc-8000-1e5b3ac6a19b | button | Visual inspection of joint welds at cross laps | Yes,No
e1d7c715-43e3-5a75-a23f-7de6e427b6c7 | button | Confirm no laps at capping beam construction joint | Yes,No
0a2ba39d-abf7-533d-ac12-8d101b988ba3 | button | Confirm all side laps are sealed and end laps by heat-welding the selvedge with a propane torch and minimum 2-10mm bleed | Yes,No
e06df59e-1687-5112-bde9-94e98c23ebf9 | button | Confirm all angle changes (inside and outside corners) are reinforced by heat-welding on additional 300 mm piece of COLPHENE BSW UNI NG centered on the angle | Yes,No
b27d5723-a7cc-48d9-9507-3e78376e9534 | checkpoint | Colphene BSW UNI NG Reiforcement Strip - Floor/Wall Junction and Existing Wall Upturn
fa3e56a1-e41f-5082-a0d0-894b1ce8faf6 | button | Confirm rolls stored upright, with the selvedge side on top. If the product is stored outdoors confirm covered with an protective cover | Yes,No
9d63b735-8565-551a-af3b-58af3ffbb405 | button | Check COLPHENE BSW UNI NG thickness is 4mm | Yes,No
149f94ce-ea63-56c8-ab62-163cfaff654f | button | Confirm minimum 100 mm side overlap | Yes,No
2b897576-6890-5038-ae39-45e8ec4fc86c | button | Confirm minimum 150 mm end lap between each strip | Yes,No
8755b459-5512-504d-8fc6-7e648357a72e | button | Confirm end laps are staggered by at least 300 mm | Yes,No
1b104f4d-2edf-53ac-91df-c769acbc84af | button | Confirm laps avoid excessive layering | Yes,No
b4661318-27ad-5524-8ea1-b8ec1625271d | button | Visual inspection of joint welds at cross laps | Yes,No
5adc1450-ff9f-513b-86d4-69760a587566 | button | Confirm no laps at capping beam construction joint | Yes,No
d3e5f15c-9194-5b8b-bb91-5fec6a2213f6 | button | Confirm all side laps are sealed and end laps by heat-welding the selvedge with a propane torch and minimum 2-10mm bleed | Yes,No
| checkpoint | Pressure Seal
| button | Pressure seal conecting new membrane with existing - By Delta | Yes,No
| button | Bolts sealed galvanised paint - By Delta | Yes,No
| checkpoint | SOPRAHOSE 13
| checkpoint | Substrate Requirements:
| button | Flat, dry, clean, and smooth surface. | Yes,No
| button | Free from sharp objects, laitance, oils, grease, or any materials that might hinder adhesion. | Yes,No
| button | Commencement of installation shall be taken as acceptance of the substrate by the Applicator | Yes,No
| checkpoint | Positioning SOPRAHOSE 13:
| button | SOPRAHOSE 13 should be centered on the substrate or positioned with a minimum of 100 mm concrete cover from any external edge. | Yes,No
| checkpoint | Installation of SOPRAHOSE 13:
| button | Must lay flat on the concrete with appropriate hose clamps mechanically fixed. | Yes,No
| button | Hose clips should be spaced at 200 mm intervals. | Yes,No
| checkpoint | SOPRAHOSE 13 End Box:
| button | To be installed on the formwork flask with the internal side of the wall or slab. | Yes,No
| checkpoint | Hose End Overlap:
| button | A minimum 150 mm parallel overlap required, with 30-50 mm gap between the hoses. | Yes,No
| checkpoint | Injection Boxes
| button | Installed at a maximum spacing of 10 meters. | Yes,No
| checkpoint | Hold Points
| button | Bravada Installer: Final review to ensure compliance with the shop drawing/specification. | Yes,No
| button | Bravada Supervisor: Final review for compliance. | Yes,No
| button | Delta Group Project Team: Review and acknowledgment of the Injection Hose Prototype, ITC completion, and handover of the works package. | Yes,No
| checkpoint | Colphene BSW UNI NG - To Insitu Walls
| button | ANTIROCK PRIMER can be applied with a brush or roller on clean, dry substrates free of any residue that may hinder adherence. Shake well before using. | Yes,No
| button | It must be thoroughly dry before applying the waterproofing membrane. Drying time will vary depending on air and surface temperature and humidity. | Yes,No
| button | Confirm rolls stored upright, with the selvedge side on top. If the product is stored outdoors confirm covered with an protective cover | Yes,No
| button | Check COLPHENE BSW UNI NG thickness is 4mm | Yes,No
| button | Confirm minimum 100 mm side overlap | Yes,No
| button | Confirm minimum 150 mm end lap between each strip | Yes,No
| button | Confirm end laps are staggered by at least 300 mm | Yes,No
| button | Confirm laps avoid excessive layering | Yes,No
| button | Visual inspection of joint welds at cross laps | Yes,No
| button | Confirm no laps at capping beam construction joint | Yes,No
| button | Confirm all side laps are sealed and end laps by heat-welding the selvedge with a propane torch and minimum 2-10mm bleed | Yes,No
| button | Confirm all angle changes (inside and outside corners) are reinforced by heat-welding on additional 300 mm piece of COLPHENE BSW UNI NG centered on the angle | Yes,No
| checkpoint | Sopradrain 20 - To Insitu Walls
| button | The substrate must be firm, even, clean and free from loose materials or any construction debris on the surface. | Yes,No
| button | Install SOPRADRAIN 20 with the geotextile facing the backfill. | Yes,No
| button | Join by simply butting edge to edge and overlapping the geotextile overhang and securing with reinforced canvastape | Yes,No
| button | Terminate SOPRADRAIN 20 by nailing pressure bar at required height | Yes,No
| checkpoint | WPA 100 - To Top of Raft Slab
| button | Mix well the product before use | Yes,No
| button | WPA100 is applied with a with a brush or a roller in two (2) layers. Application must be a minimum of 2 coats @ >= 1.2kg/m2 per coat to achieve a dry film thickness not less than 2mm as per the technical data sheet. | Yes,No
| button | Ready to recoat after 2 hours Dry: 24 hours (remains tacky to touch) | Yes,No
| button | Store WPA 100 in chemical bunds provided by Delta | Yes,No
| checkpoint | CHECKLIST COMPLETE AND SIGNED
| button | ITC completed | Yes,No
db16214c-1f6a-4174-bb4d-856eca1d6eb1 | checklist | Colphene Uni NG Riser Pit ITP |  | Colphene Uni NG Riser Pit ITP |  | 113bc979-5bd5-4d90-a78c-ff542630b875
8b313fe3-12db-4bdc-9071-3d925df9113c | section | Details
7b23096b-5a01-4b22-9202-d17cf007c4ab | checkpoint | RISER PIT WATERPROOFING ITP
b5b77e20-27be-5670-9098-420e8e7a2758 | button | Sample Submissions Approved | Yes,No
bf0b603e-2f3c-5449-98dd-af4de99f2a2f | button | Shop Drawings Approved | Yes,No
dd84061d-0a9b-5865-a652-398862fcff85 | button | Colphene BSW UNI NG Installed - To Raft Slab Blinding | Yes,No
337ed77f-b8f3-5887-b46e-19a4b5da10b4 | button | Colphene BSW UNI NG Upturn to Installed - Existing Wall | Yes,No
9adc7d3e-fa7e-5d62-8250-9a3d21503587 | button | Colphene BSW UNI NG Reiforcement Strip Installed - Floor/Wall Junction | Yes,No
| button | Pressure Seal installed - By Delta | Yes,No
7fb3e28c-8b84-5b1b-b148-ea3e7c2305a3 | button | Injection System Installed | Yes,No
7ddbbb32-c503-5b00-a4d6-6b7f1ad98efb | button | Primer Installed - To Insitu Walls | Yes,No
4097dbab-2d82-553c-ace4-e55b81530a93 | button | Colphene BSW UNI NG Installed - To Insitu Walls | Yes,No
c9ccffb5-fc7c-5ee7-8915-54c75441fa1a | button | Sopradrain Installed - To Insitu Walls | Yes,No
9841948e-416f-5dce-8ce9-e444ae6793b4 | button | WPA 100 Installed - To Top of Raft Slab | Yes,No