## ITP-xxx
|  |  | Inspection and Test Plan - Control and Supervision of the Works | [7 empty] | FHC-ITP-010
[11 empty] | Revision : 1 | Date : 12/03/2025
Client: |  | MRPA |  | Construction Process: |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: |  | Watergardens Station Carpark |  | Storm Trap Precast Units |  | Name: Jake Cardillo |  | Name: Patrick Fagan |  |  | Name: Shaun Kent
Job No: |  | 7432000 |  | Specifications: VicRoads Specification Section 701, 705, 626 and Drawings
|  |  |  | Structure / Component: Stormwater Detention |  | Signed : |  | Signed : |  |  | Signed :
|  |  |  | Location: Watergardens Station |  | Date : 12/03/2025 |  | Date : 12/03/2025 |  |  | Date : 12/03/2025
Lot No: |  |  | Lot Details: | [5 empty] | Lot Size/ Quantity:
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Client | Fulton Hogan | FH's Sub-contractor | Date
1 | Preliminary Works
1.1 | Check for correct documentation |  | Prior to commencing any activity | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings - all drawings are the latest revision | IFC Drawings Approved Shop Drawings | Visual inspection | This ITP signed off | HP* | Site Engineer / Site Foreman | N/A |  | N/A
1.2 | Implementation of all measures and controls |  | Prior to commencing any activity | All necessary measures and controls are being implemented, that is: OHSCP, PHSCP, PCMP, EMP, ECP, CEMP, ERA, QMP, CHMP, SWMS | OHSCP, PHSCP, PCMP, EMP, ECP, CEMP, ERA, QMP, CHMP, SWMS | Visual Inspection | This ITP signed off | HP* | Site Engineer / Site Foreman | N/A |  | N/A
1.3 | Material approvals |  | Prior to Placement | Material intended for use is to be submitted to the client prior to placement to verify it conforms to required specifications. | Material specification sheets | Verfiy | Teambinder Acceptance | HP* | Site Engineer | N/A |  | N/A
1.4 | Precast Materials Inspection |  | Each Delivery | Precast materials have been inspected and fit for purpose and free of defects | 619.08 | Visual Inspection | This ITP signed Receival and Inspection Checklist | IP | Site Engineer | N/A |  | N/A
1.5 | Precast Unit Compliance |  | Prior to Commencing | Precast Reinforced Concrete Box Culverts to comply with requirements of VicRoads Section 619. | VicRoads Spec. Cl.619 701.04 701.05 | Document review & Site inspection | Receival & Inspection Checklist Manufacturer cetificate or accreditation | IP | Site Engineer | N/A |  | N/A
1.6 | Slab Bedding Material |  | Prior to start | Stormtrap modules shall be placed on an insitu concrete base supported on a level, 150mm pad of compacted road sub-base material compacted to 95% relative MDD with a minimum allowable bearing capacity of 150kpa that extends 600mm past the outside of the system. | IFC Drawings Supplier Shop Drawings | Verify | Test Reports from supplier | TP | Site Engineer | N/A |  | N/A
1.7 | Backfill Material Classification |  | Prior to start | Nominated material shall be free from perishable matter and conform with the requirements of Vicroads section 204. The placement and compaction methodology adjacent to the detention system shall not compromise the stability of the system and be placed in even layers no more than 600mm higher than the fill on the opposite side in accordance with AS1289 | FHC-ITP-021 204.04 AS1289 | Verify | Test Reports from supplier / site | TP | Site Engineer | N/A |  | N/A
1.8 | Grouting Material Classification |  | Prior to start | Where required for general applications other than those specified elsewhere in this specification, cementitious mortars and grouts shall be shrinkage compensating proprietary products with a consistency appropriate for the required use, and able to be placed and compacted to achieve full encapsulation. Cementitious mortars and grouts shall have a minimum 28 day compressive strength of not less than 40 MPa. Cementitious grouts shall be as a minimum Type C Class dual shrinkage compensating. Only whole bags of material shall be used. Test certificates, material data sheets and health and safety data sheets shall be available for all materials. The mortar and grout applications shall be cured in accordance with the requirements of clause 610.23. | 610.33 | Verify | Test Reports from supplier | TP | Site Engineer | N/A |  | N/A
2 | Construction Works
2.1 | Excavation Permit |  | Each lot | An excavation permit must be issued prior to any excavation commencing. Plant and equipment shall be appropriate for the task. Excavation operations shall not disturb areas outside the limit of excavation. | Excavation Permit | Verify | ITP Signed | HP* | Site Engineer | N/A |  | N/A
2.2 | Review |  | Prior to construction | Stormtrap construction shall not commence until the Contractor’s construction quality procedure and inspection and test plan(s) addressing all requirements of this section have been reviewed by the Superintendent. Stormtrap modules shall be manufactured according to shop drawings and approved by the installing contractor and engineer. The shop drawings shall indicate size and location of all roof openings and inlet/outlet pipe openings. | Shop Drawings 626.02 | Visual Inspection | ITP Signed | HP | Site Engineer/ Superintendent |  |  | N/A
2.3 | Diversion of Water |  | Prior to construction | Stormtrap construction shall not commence until water flow has been diverted to the satisfaction of the Superintendent. | 626.04 | Visual Inspection | ITP Signed | IP | Site Engineer | N/A |  | N/A
2.4 | Conformity with Drawings |  | Prior to excavation | Prior to commencement of excavation for the stormtrap the Contractor shall confirm the position of all stormtrap units with the Superintendent. | 701.1 | Visual Inspection | ITP Signed | HP | Site Engineer/ Superintendent |  |  | N/A
2.5 | Tolerances For Placement |  | Prior to Backfilling | The stormtrap shall be constructed in the location, to the alignment, cross sectional shape, dimensions and levels shown on the drawings. | Shop Drawings | Visual Inspection | ITP Signed | IP | Site Foreman | N/A |  | N/A
2.6 | Foundation Inspection |  | Prior to Bedding | Bedding for the cast-in-place concrete base slab shall consist of a compacted layer of 20 mm Class 3 crushed rock, of not less than 150 mm compacted thickness or as specified by geotechnical engineer. No bedding material shall be placed until the foundation or foundation materials have been inspected and approved by the Superintendent. Per FHC-ITP-006 - Class 3 Crushed Rock | IFC Drawings 812 626.06 FHC-ITP-006 | Visual Inspection | ITP Signed | TP | Site Engineer/ Superintendent |  |  | N/A
2.7 | Cast in Place Blinding Concrete |  | Prior to construction of blinding slab | All cast‑in‑place concrete for stormtrap construction shall comply with the drawings and Section 610. Construction of the concrete blinding shall not commence until the bedding has been approved by the Superintendent. | IFC Drawings 610 611 626.07 | Visual Inspection | ITP Signed | HP | Site Engineer/ Superintendent |  |  | N/A
2.8 | Cast in Place Structural Concrete |  | Prior to construction of concrete base slab | All cast‑in‑place concrete for culvert construction shall comply with the drawings and Section 610. Steel reinforcement shall comply with the drawings and Section 611. Construction of the concrete base slab shall not commence until the pre-pour checklist and the reinforcement and form levels has been checked and approved by the Superintendent. | FHC-ITP-025 | Visual Inspection | ITP Signed, Completion of Pre-Pour Checklist & Load Batch Traceability Checklist | HP | Site Engineer/ Superintendent |  |  | N/A
2.9 | Placement of Precast Units |  | During Construction | The perimeter horizontal joint of the stormtrap modules, shall be sealed with preformed mastic joint sealer (stormmastic). The stormtrap modules shall be placed such that the maximum space between adjacent modules does not exceed 20mm. If the space exceeds 20mm, the modules shall be laid again with appropriate adjustment made to line and grade to bring the space into specification. | Shop Drawings | Visual Inspection | ITP Signed | IP | Site Engineer / Site Foreman | N/A |  | N/A
2.1 | Covering External Surface of Joints |  | During Construction | All exterior joints between adjacent stormtraps modules shall be sealed with 300mm preformed cold-applied, self-adhering elastometric resin bonded to woven highly punctured resistant polymer wrap and shall be 300mm integrated primer sealant as approved by humes (stormwrap). The adhesive exterior joint wraps shall be prepared/cleaned and installed according to the manufacturers installation instructions. | Shop Drawings | Visual Inspection | ITP Signed | HP | Site Engineer/ Superintendent |  |  | N/A
3 | Testing & Completion
3.1 | Concrete Sampling and Testing |  | Each Strucutral Concrete Pour | Concrete sampled and tessted for strength and slump as per requirements outlined FHC-ITP-025 - Structural Concrete Construction | FHC-ITP-025 | Verify | Test Reports | TP | Site Engineer | N/A |  | N/A
3.2 | Final Inspection |  | Post Construction | Units which do not comply with the requirements of clause 619.14 prior to laying and backfilling shall be rejected and removed from the site. Where inspections after backfilling identify defects which do not comply with the requirements of clause 619.14, such culverts shall be removed and replaced, unless the Superintendent approves repairs to be undertaken in accordance with the requirements of Section 610, and Section 687 for crack repairs and Section 689 for conventional patch repairs | 701.31 (d) | Visual Inspection | ITP Signed | IP | Site Engineer / Site Foreman | N/A |  | N/A
3.3 | Lot Mapping |  | Post Construction | Stormtrap to have suitable lot map based on days production for traceability purposes. | Shop Drawings | Visual Inspection | Lot Maps | TP | Site Engineer / Site Foreman | N/A |  | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
AP | Approval Point | Written or verbal approval given by the Superintendent