## ITP007 - Unbound Pavements
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP031 - AGL Luminaires Installation | [5 empty] | ITP031 - AGL Luminaires Installation
section | 1.0 Preliminary Works
checkpoint | 1.1 - Check for correct documentation
label | Frequency: Prior to commencing any activity
label | Acceptance Criteria:
label | • Ensure that all employees and subcontractors are using the latest and complete set of drawings
label | Reference Documents:
label | • IFC Drawings
label | • Appendix K- AGL Specification
label | Inspection/ Test Method: Verify
label | Record of conformity: Drawings
label | IP
label | Responsibility: Subcontractor Representative
text | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency: Prior to commencing any activities
label | Acceptance Criteria:
label | • All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents:
label | • PSP
label | • EMP
label | • TMP
label | • JSEA
label | • SWMS
label | • WP
label | Inspection/ Test Method: Verify
label | Record of conformity: Site and Office Inspection
label | HP*
label | Responsibility: Site Engineer / Site Supervisor
text | Date Completed:
checkpoint | 1.3 - Material/Equipment Approvals and Certification
label | Frequency: Prior to Start
label | Acceptance Criteria:
label | • All materials shall be proven to meet contractual requirements prior to acceptance.
label | Reference Documents:
label | • Appendix K- AGL Specification Section 2.3.3
label | Inspection/ Test Method: Verify
label | Record of conformity: Datasheet / Material Submission
label | HP*
label | Responsibility: Site Engineer
text | Date Completed:
section | 2.0 Installation of Light
checkpoint | 2.1 - Setting out of Airfield Luminaires
label | Frequency: Each Lot
label | Acceptance Criteria:
label | • Surveyor to confirm location with IFC drawings. Alignment of luminaire positions, shallow seating pots to be checked.
label | Reference Documents:
label | • IFC Drawings
label | • 12554937-E031 to 12554937-E037
label | Inspection/ Test Method: Verify
label | Record of conformity: SCP
label | IP
label | Responsibility: Site Engineer / Surveyor
text | Date Completed:
checkpoint | 2.2 - Isolation of lights
label | Frequency: Each Light
label | Acceptance Criteria:
label | • Prior to commencement of removal, the subcontractor shall ensure that the light has been isolated from power.
label | Reference Documents:
label | • APAM Electrical Isolation Standards
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer / Site Supervisor
text | Date Completed:
checkpoint | 2.1 - Coring
label | Frequency: Each Light
label | Acceptance Criteria:
label | • As required, Core asphalt to depth as per subcontractor ITC for relevant Method.
label | • Remove blanking plate and clean void.
label | Reference Documents:
label | • IFC Drawings
label | • 12554937-E031 to 12554937-E037
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer / Site Supervisor
text | Date Completed:
checkpoint | 2.1 - Saw Cutting
label | Frequency: Each Light
label | Acceptance Criteria:
label | • Saw cut pavement to accommodate new light base. Protect edges as required.
label | Reference Documents:
label | • IFC Drawings
label | • 12554937-E031 to 12554937-E037
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer / Site Supervisor
text | Date Completed:
checkpoint | 2.3 - Installation of Inset light
label | Frequency: Each light
label | Acceptance Criteria:
label | • Ensure correct light is installed in correct position as per the IFC drawings, this ITP and ITC
label | Reference Documents:
label | • IFC Drawings
label | • 12554937-E031 to 12554937-E037
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer / Site Supervisor
text | Date Completed:
checkpoint | 2.4 - Light spacing
label | Frequency: Each Light
label | Acceptance Criteria:
label | • Ensure gap between new light base and pavement not less than 7mm and not more than 15mm.
label | Reference Documents:
label | • IFC Drawings
label | • 12554937-E031 to 12554937-E037
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer / Site Supervisor
text | Date Completed:
checkpoint | 2.5 - Recess Sealing
label | Frequency: Each light
label | Acceptance Criteria:
label | • Seal top of recess around light base with Dowsil 888 in concrete
label | • Sealant in asphalt as detailed in IFC Drawing
label | Reference Documents:
label | • IFC Drawings
label | • 12554937-E033
label | Inspection/ Test Method: Verify
label | Record of conformity: This Signed ITP / ITC/As-Built Documentation
label | IP
label | Responsibility: Site Engineer / Site Supervisor
text | Date Completed:
checkpoint | 2.6 - Installation of secondary and Earthing Cable
label | Frequency: Each Light
label | Acceptance Criteria:
label | • Each fitting shall have earthing cable provided
label | – Earthing to be 6mm2 single core green/yellow PVC cable.
label | – Twin secondary cable to be 4mm2 each.
label | Reference Documents: -
label | Inspection/ Test Method: Verify
label | Record of conformity: This Signed ITP & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 2.7 - Series Isolation transformer
label | Frequency: Each Light
label | Acceptance Criteria:
label | • Each luminaire / fitting shall be connected to a series isolation transformer in closest SIT duct pit/ junction can.
label | Reference Documents:
label | • IFC Drawings
label | • 12554937-E031 to 12554937-E037
label | Inspection/ Test Method: Verify
label | Record of conformity: This Signed ITP & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 2.8 - Luminaire Circuit
label | Frequency: Each Light
label | Acceptance Criteria:
label | • Each luminaire fitting shall be installed on the appropriate circuit as specified in the construction drawings.
label | Reference Documents:
label | • IFC Drawings
label | • 12554937-E031 to 12554937-E037
label | Inspection/ Test Method: Verify
label | Record of conformity: This Signed ITP / As-Built Documentation
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
section | 3.0 Post Construction
checkpoint | 3.1 - Redundant equipment
label | Frequency: Each Light
label | Acceptance Criteria:
label | • All existing AGL bases shall be raised, abandoned, removed or replaced as per specification
label | Reference Documents:
label | • Appendix K- AGL Specification Section 3.5.2
label | Inspection/ Test Method: Verify
label | Record of conformity: This Signed ITP & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 3.2 - Equipment Survey
label | Frequency: Each Light
label | Acceptance Criteria:
label | • Accurately survey the location of airfield lighting equipment.
label | • The survey plan, endorsed by a registered surveyor, must identify the location of all installed equipment in relation to permanent site features and other underground services.
label | • The survey must also capture all installation details such as the orientation and rotation of visual aids, colour pattern, constructed foundations, etc.
label | Reference Documents:
label | • Appendix K- AGL Specification Section 3.4
label | Inspection/ Test Method: Verify
label | Record of conformity: This Signed ITP & Sub-contractor ITC
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 3.3 - As-Built
label | Frequency: Each Light
label | Acceptance Criteria:
label | • Submission of surveyed luminaire position to superintendent prior to practical completion
label | Reference Documents: -
label | Inspection/ Test Method: Verify
label | Record of conformity: SCP
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
text | Date: