## QA Folder Structure
QA Folder Structure |  |  |  | Checklists | NOTES
Union Quarter - Block B
Hydraulic Services
Penetrations (includes Cast In)
|  | NORTH B1 - Level 7 |  |  | Please expand out so there is a folder for each Level from B1, Ground, Level 1, Level 2 etc)
Peno - Floor
Peno - Syphonic
Peno - Wall
Peno - Cast In
|  | SOUTH B1 - Level 7 |  |  | Please expand out so there is a folder for each Level from B1, Ground, Level 1, Level 2 etc)
Peno - Floor
Peno - Syphonic
Peno - Wall
Peno - Cast In
Drains, Stacks & Vents
NORTH Ground
|  |  | TH01 - TH05 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Townhouse (TH) TH01, TH02, TH03 etc
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
NORTH Level 1
|  |  | 106 - 109 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment 106, 107, 108 etc
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
SOUTH Level 1
|  |  | 101 - 105 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment 101, 102, 103 etc
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
NORTH Level 2
|  |  | 208 - 225 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment 208 upto 225
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
SOUTH Level 2
|  |  | 201 - 207 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment from 201 upto 207
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
|  |  | 226 - 246 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment from 226 upto 246
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
NORTH Level 3
|  |  | 308 - 324 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment 308 upto 324
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
SOUTH Level 3
|  |  | 301 - 307 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment from 301 upto 307
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
|  |  | 325 - 346 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment from 325 upto 346
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
NORTH Level 4
|  |  | 408 - 428 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment 408 upto 428
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
|  |  | 451 | UQ Drains: Sewer, Stormwater & Vent - Underslung
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
SOUTH Level 4
|  |  | 401 - 407 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment from 401 upto 407
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
|  |  | 429 - 450 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment from 429 upto 450
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
SOUTH Level 5
|  |  | 501 - 529 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment from 501 upto 529
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
SOUTH Level 6
|  |  | 601 - 640 | UQ Drains: Sewer, Stormwater & Vent - Underslung | Please expand out so there is a folder for each Apartment from 601 upto 640
UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
UQ Drains: Trade Waste - Underslung
Syphonic
|  | B1 - Level 7 |  |  | Please expand out so there is a folder for each Level from B1, Ground, Level 1, Level 2 etc)
UQ Drains: Syphonic - Underslung
UQ Stack Riser: Syphonic
Corridor Rough In
|  | Level 1 - 6 |  |  | Please expand out so there is a folder for each Level from B1, Ground, Level 1, Level 2 etc)
NORTH Corridor - McLister St
UQ Corridor Rough In (Cold Water)
UQ Corridor Rough In (Hot Water)
UQ Corridor Rough In (Gas)
UQ Corridor Rough In (Non Potable/Rainwater)
UQ Corridor - Meter Manifold Install
|  |  | NORTH Corridor - Carpark West | As above
|  |  | SOUTH Corridor - Carpark West | As above
|  |  | SOUTH Corridor - Middle of Block | As above
|  |  | SOUTH Corridor - Macindoe St | As above
Risers
NORTH - Ground Floor
|  |  | Riser - McLister Lobby Stair | UQ Risers (CW, HW, Gas, Non Potable)
|  |  | Riser - McLister Lobby Opp Lift | As above
|  | SOUTH - Ground Floor | Riser - Macindoe Lobby | UQ Risers (CW, HW, Gas, Non Potable)
NORTH - Level 1
|  |  | Riser (near Apt 109) | UQ Risers (CW, HW, Gas, Non Potable)
SOUTH - Level 1
|  |  | Riser Opp Lifts | UQ Risers (CW, HW, Gas, Non Potable)
NORTH - Level 2
|  |  | Riser (near Apt 212) | UQ Risers (CW, HW, Gas, Non Potable)
SOUTH - Level 2
|  |  | Riser Opp Lifts | UQ Risers (CW, HW, Gas, Non Potable)
|  |  | Riser (near 231) | As above
NORTH - Level 3
|  |  | Riser (near Apt 312) | UQ Risers (CW, HW, Gas, Non Potable)
SOUTH - Level 3
|  |  | Riser Opp Lifts | UQ Risers (CW, HW, Gas, Non Potable)
|  |  | Riser (near 330) | As above
NORTH - Level 4
|  |  | Riser (near Apt 412) | UQ Risers (CW, HW, Gas, Non Potable)
SOUTH - Level 4
|  |  | Riser Opp Lifts | UQ Risers (CW, HW, Gas, Non Potable)
|  |  | Riser (near 434) | As above
SOUTH - Level 5
|  |  | Riser Opp Lifts | UQ Risers (CW, HW, Gas, Non Potable)
|  |  | Riser (near 513) | As above
SOUTH - Level 6
|  |  | Riser Opp Lifts | UQ Risers (CW, HW, Gas, Non Potable)
|  |  | Riser (near 613) | As above
High Level Rough In
NORTH Ground
|  |  | TH01 - TH05 | UQ High Level Rough In | Please expand out so there is a folder for each Townhouse (TH) TH01, TH02, TH03 etc
NORTH Level 1
|  |  | 106 - 109 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment 106, 107, 108 etc
SOUTH Level 1
|  |  | 101 - 105 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment 101, 102, 103 etc
NORTH Level 2
|  |  | 208 - 225 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment 208 upto 225
SOUTH Level 2
|  |  | 201 - 207 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment from 201 upto 207
|  |  | 226 - 246 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment from 226 upto 246
NORTH Level 3
|  |  | 308 - 324 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment 308 upto 324
SOUTH Level 3
|  |  | 301 - 307 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment from 301 upto 307
|  |  | 325 - 346 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment from 325 upto 346
NORTH Level 4
|  |  | 408 - 428 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment 408 upto 428
|  |  | 451 | UQ High Level Rough In
SOUTH Level 4
|  |  | 401 - 407 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment from 401 upto 407
|  |  | 429 - 450 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment from 429 upto 450
SOUTH Level 5
|  |  | 501 - 529 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment from 501 upto 529
SOUTH Level 6
|  |  | 601 - 640 | UQ High Level Rough In | Please expand out so there is a folder for each Apartment from 601 upto 640
Low Level Rough In
NORTH Ground
|  |  | TH01 - TH05 | UQ Low Level Rough In | Please expand out so there is a folder for each Townhouse (TH) TH01, TH02, TH03 etc
NORTH Level 1
|  |  | 106 - 109 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment 106, 107, 108 etc
SOUTH Level 1
|  |  | 101 - 105 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment 101, 102, 103 etc
NORTH Level 2
|  |  | 208 - 225 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment 208 upto 225
SOUTH Level 2
|  |  | 201 - 207 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment from 201 upto 207
|  |  | 226 - 246 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment from 226 upto 246
NORTH Level 3
|  |  | 308 - 324 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment 308 upto 324
SOUTH Level 3
|  |  | 301 - 307 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment from 301 upto 307
|  |  | 325 - 346 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment from 325 upto 346
NORTH Level 4
|  |  | 408 - 428 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment 408 upto 428
|  |  | 451 | UQ Low Level Rough In
SOUTH Level 4
|  |  | 401 - 407 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment from 401 upto 407
|  |  | 429 - 450 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment from 429 upto 450
SOUTH Level 5
|  |  | 501 - 529 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment from 501 upto 529
SOUTH Level 6
|  |  | 601 - 640 | UQ Low Level Rough In | Please expand out so there is a folder for each Apartment from 601 upto 640
Fit Off/ Install
NORTH Ground
|  |  | TH01 - TH05 | UQ Fit Off/ Fixture Install Toilets & Cisterns | Please expand out so there is a folder for each Townhouse (TH) TH01, TH02, TH03 etc
UQ Fit Off/ Fixture Install - Showers & Tapware
UQ Fit Off/ Fixture Install - Vanity Basin/s & Tapware
UQ Fit Off/ Fixture Install - Kitchen sink & Tapware
UQ Fit Off/ Fixture Install - Laundry trough & Tapware
UQ Fit Off/ Fixture Install - Bath & Tapware
UQ Fit Off/ Fixture Install - Dishwasher
UQ Fit Off/ Fixture Install - Wall Tundish
UQ Fit Off/ Fixture Install - Hose Taps
UQ Fit Off/ Fixture Install - TMV
UQ Fit Off/ Fixture Install - Tempering Valve
UQ Fit Off/ Fixture Install - Gas Cooktop
UQ Fit Off/ Fixture Install - RPZD
NORTH Level 1
|  |  | 106 - 109 | As above | Please expand out so there is a folder for each Apartment 106, 107, 108 etc
SOUTH Level 1
|  |  | 101 - 105 | As above | Please expand out so there is a folder for each Apartment 101, 102, 103 etc
NORTH Level 2
|  |  | 208 - 225 | As above | Please expand out so there is a folder for each Apartment 208 upto 225
SOUTH Level 2
|  |  | 201 - 207 | As above | Please expand out so there is a folder for each Apartment from 201 upto 207
|  |  | 226 - 246 | As above | Please expand out so there is a folder for each Apartment from 226 upto 246
NORTH Level 3
|  |  | 308 - 324 | As above | Please expand out so there is a folder for each Apartment 308 upto 324
SOUTH Level 3
|  |  | 301 - 307 | As above | Please expand out so there is a folder for each Apartment from 301 upto 307
|  |  | 325 - 346 | As above | Please expand out so there is a folder for each Apartment from 325 upto 346
NORTH Level 4
|  |  | 408 - 428 | As above | Please expand out so there is a folder for each Apartment 408 upto 428
|  |  | 451 | As above
SOUTH Level 4
|  |  | 401 - 407 | As above | Please expand out so there is a folder for each Apartment from 401 upto 407
|  |  | 429 - 450 | As above | Please expand out so there is a folder for each Apartment from 429 upto 450
SOUTH Level 5
|  |  | 501 - 529 | As above | Please expand out so there is a folder for each Apartment from 501 upto 529
SOUTH Level 6
|  |  | 601 - 640 | As above | Please expand out so there is a folder for each Apartment from 601 upto 640
Testing
NORTH Ground
|  | Corridor & Apts - NORTH - McLister St |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | TH01 - TH05 |  |  | Please expand out so there is a folder for each Townhouse (TH) TH01, TH02, TH03 etc
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
NORTH Level 1
|  | Corridor & Apts - NORTH - McLister St |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | Corridor & Apts - NORTH Carpark West |  | As above
|  | 106 - 109 |  |  | Please expand out so there is a folder for each Apartment 106, 107, 108 etc
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
NORTH Level 2
|  | Corridor & Apts - NORTH - McLister St |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | Corridor & Apts - NORTH Carpark West |  | As above
|  | 208 - 225 |  |  | Please expand out so there is a folder for each Apartment 208 upto 225
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
SOUTH Level 2
|  | SOUTH Corridor - Carpark West |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | SOUTH Corridor - Middle of Block |  | As above
|  | SOUTH Corridor - Macindoe St |  | As above
|  | 201 - 207 |  |  | Please expand out so there is a folder for each Apartment from 201 upto 207
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
|  | 226 - 246 |  | As above | Please expand out so there is a folder for each Apartment from 226 upto 246
NORTH Level 3
|  | Corridor & Apts - NORTH - McLister St |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | Corridor & Apts - NORTH Carpark West |  | As above
|  | 308 - 324 |  |  | Please expand out so there is a folder for each Apartment 308 upto 324
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
UQ Testing - Tempering Valve
As above
SOUTH Level 3
|  | SOUTH Corridor - Carpark West |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | SOUTH Corridor - Middle of Block |  | As above
|  | SOUTH Corridor - Macindoe St |  | As above
|  | 301 - 307 |  |  | Please expand out so there is a folder for each Apartment from 301 upto 307
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
|  | 325 - 346 |  | As above | Please expand out so there is a folder for each Apartment from 325 upto 346
NORTH Level 4
|  | Corridor & Apts - NORTH - McLister St |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | Corridor & Apts - NORTH Carpark West |  | As above
|  | 408 - 428 |  |  | Please expand out so there is a folder for each Apartment 408 upto 428
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
UQ Testing - Tempering Valve
|  | 451 |  | As above
SOUTH Level 4
|  | SOUTH Corridor - Carpark West |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | SOUTH Corridor - Middle of Block |  | As above
|  | SOUTH Corridor - Macindoe St |  | As above
|  | 401 - 407 |  |  | Please expand out so there is a folder for each Apartment from 401 upto 407
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
|  | 429 - 450 |  | As above | Please expand out so there is a folder for each Apartment from 429 upto 450
NORTH Level 5
|  | Corridor & Apts - NORTH Carpark West |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
SOUTH Level 5
|  | SOUTH Corridor - Carpark West |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | SOUTH Corridor - Middle of Block |  | As above
|  | SOUTH Corridor - Macindoe St |  | As above
|  | 501 - 529 |  |  | Please expand out so there is a folder for each Apartment from 501 upto 529
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
SOUTH Level 6
|  | SOUTH Corridor - Carpark West |  | UQ Testing - Potable Water - 1500kpa water test (not an air test)
UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
UQ Testing - Natural Gas
|  | SOUTH Corridor - Middle of Block |  | As above
|  | SOUTH Corridor - Macindoe St |  | As above
|  | 601 - 640 |  |  | Please expand out so there is a folder for each Apartment from 601 upto 640
UQ Testing - Water Hold - Sewer & Stormwater Underslung
UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - Air Test - Sewer & Stormwater Underslung
UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
UQ Testing - TMV
UQ Testing - Tempering Valve
Plant & Equipment
Meters
Commissioning/Handover

## Checklists
type | name | values | prefix | postfix | usage count | user addable
checklist-flat | Peno - Floor
checkpoint | Installation complies with current IFC shop drawing
checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint | Collars are firmly secured into formwork
checkpoint-no-status | Concrete pour details
text | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | Peno - Syphonic
checkpoint | Installation complies with current IFC shop drawing
checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint | Collars are firmly secured into formwork
checkpoint | Overlflow peno cast in to top of slab (no fall required)
checkpoint | Primary peno outlet is set down 10-15mm
checkpoint-no-status | Concrete pour details
text | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | Peno - Wall
checkpoint | Installation complies with current IFC shop drawings
text | Document invert level wall peno has been installed at |  |  | mm
checkpoint | Collars and sleeves are capped & sealed
checkpoint-no-status | Concrete pour details
text | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | Peno - Cast In
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Collar & pre-fab elements free of damage prior to install
checkpoint | Where practical, pipes water tested prior to the pour
checkpoint | Pipe grades and size have been checked
checkpoint | Invert levels and finished levels have been checked
checkpoint | PVC has been lagged (add photos)
checkpoint | HDPE fusion welds are witness marked
checkpoint | RWO body installed level
checkpoint | Clips, fixings & anchor points are correct and secure
checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status | Concrete pour details
text | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | UQ Drains: Sewer, Stormwater & Vent - Underslung
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/grade meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Drains: Trade Waste - Underslung
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Drains: Syphonic - Underslung
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Stack Riser: Sewer, Vent, Trade Waste Vent & Stormwater
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Clips, fixings & anchor points are correct and secure (includes independent clipping (no piggy backed clips)
checkpoint | Peno has been caulked (top and underside of slab)
checkpoint | Branch junction/s & off set invert levels have been checked and are correct
checkpoint | Pipes & junctions are clear of debris
checkpoint | Inspection opening caps have been tightened and duct tape applied
checkpoint | Expansion joint clipped and spacer removed (to allow for expansion)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Stack Riser: Syphonic
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Specific clipping method & anchor points are correct
checkpoint | HDPE fusion welds are witness marked
checkpoint | Pipes & junctions are clear of debris
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Peno has been caulked (top and underside of slab)
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Corridor Rough In (Cold Water)
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Connected to meter manifold and pipe labelled with destination
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Flexible connections are correct
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Corridor Rough In (Hot Water)
checkpoint-no-status | Existing work by previous plumbing contractor
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips, fixings & furrel blocks are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Hot water meter has been installed
checkpoint | Extension points have sacrificial valves
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Corridor Rough In (Gas)
checkpoint-no-status | Existing work by previous plumbing contractor
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Corridor Rough In (Non Potable/Rainwater)
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Flexible connections are correct
checkpoint | Labels have been applied where required
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Corridor - Meter Manifold Install
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation in accordance with Water Authority requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Connected to meter manifold and pipe labelled
checkpoint | All manifold points are capped
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Risers (CW, HW, Gas, Non Potable)
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings, schematics & AS/NZS 3500 (2021)
checkpoint | Expansion loop position and length comply with IFC schematics & AS/NZS 3500 (2021)
checkpoint | Clips, fixings & anchor points are correct (etc - fixed anchor, slide guide clamp, spring clip)
checkpoint | Clips used are not dissimilar metals and will not corrode an element
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Torque rates of all roll-groove joints are correct
checkpoint | Flange connection gasket is fibre and not rubber
checkpoint | Flange connection bolts are to the required torque rates
checkpoint | Branch junctions & off-set levels are correct
checkpoint | Pipe joints & witness marks are correct
checkpoint | Check for damage or leaks
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint | Penos have been caulked and meet fire rating requirements (top and underside of slab)
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ High Level Rough In
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct
checkpoint | Clips and fixings are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | TMV/TV have been installed correctly and in the location for future access
checkpoint | Sharp edge pipe protection is secure and will not lead to pipe abrasion in future
checkpoint | Couta fittings have been visually inspected to ensure pex is in correct location and crimped correctly
checkpoint | Final check for cross connections has been undertaken
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Low Level Rough In
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct
checkpoint | Clips and fixings are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | TMV/TV have been installed correctly and in the location for future access
checkpoint | Mixer bodies & lugged are installed at the correct height and on a nog
checkpoint | In-wall pan & cistern brackets are correct and there is reinforcement behind flush pipe
checkpoint | Sharp edge pipe protection is secure and will not lead to pipe abrasion in future
checkpoint | Couta fittings have been visually inspected to ensure pex is in correct location and crimped correctly
checkpoint | Final check for cross connections has been undertaken
checkpoint | RSG demarcation sticker has been applied to work zone (if connecting to previous contractor works)
checklist-flat | UQ Fit Off/ Fixture Install Toilets & Cisterns
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Installation is aligned, level and secure
checkpoint | Flush pipe has been measured to suit the pan prior to being cut to size
checkpoint | Button flush plate is in working order and not damaged/scratched
checkpoint | Seat and accessories are secure and correct
checkpoint | DDA suite back rest installed correctly
checkpoint | Full function of installed toilet suite has been checked
checkpoint | Pan trap is clear of debris
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - Showers & Tapware
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Wall plates & mixer are aligned, level and secure
checkpoint | Wall outlet is installed correctly
checkpoint | Full function of installed mixer and shower head/s has been checked
checkpoint | Floor grate is correctly fitted & aligned
checkpoint | Floor waste trap is clear of debris
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - Vanity Basin/s & Tapware
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Installation is aligned, level and secure
checkpoint | Plug & washers are correct for the fixtures being installed
checkpoint | Waste and trap connections are tight
checkpoint | Trap is clear of debris
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Any stop valves have been capped for future use
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - Kitchen sink & Tapware
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Installation is aligned, level and secure
checkpoint | Plug & washers are correct for the fixtures being installed
checkpoint | Waste and trap connections are tight
checkpoint | Trap is clear of debris
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Any stop valves have been capped for future use
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - Laundry trough & Tapware
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Installation is aligned, level and secure
checkpoint | Plug & washers are correct for the fixtures being installed
checkpoint | Waste and trap connections are tight
checkpoint | Trap is clear of debris
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Any stop valves have been capped for future use
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - Bath & Tapware
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Bath has been installed aligned, level and secure
checkpoint | Bath frame has been adjusted correctly
checkpoint | Wall plate, spout & mixer are aligned, level and secure
checkpoint | Wall outlet is installed correctly
checkpoint | Full function of installed mixer and spout has been checked
checkpoint | Waste and trap connections are tight
checkpoint | Trap is clear of debris
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - Dishwasher
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Dishwasher has been installed aligned, level and secure
checkpoint | Full function of dishwasher has been checked
checkpoint | Trap is clear of debris
checkpoint | Trap nuts are tight
checkpoint | Mini stop is installed
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Pressure reducing valve have been installed
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - Wall Tundish
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Tundish has been installed aligned, level and secure
checkpoint | Trap connection is clear of debris
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - Hose Taps
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Hose Taps have been installed aligned, level and secure
checkpoint | Backflow prevention device has been installed
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - TMV
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint | Wall box has been installed correctly
checkpoint | Function and controls have been checked
checklist-flat | UQ Fit Off/ Fixture Install - Tempering Valve
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint | Valve been installed correctly and in the correct location
checkpoint | Function and controls have been checked
checklist-flat | UQ Fit Off/ Fixture Install - Gas Cooktop
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint | Cooktop has been installed aligned, level and secure
checkpoint | Surrounding wall material is fire rated and complies with manufacturer specs
checkpoint | Distance from cooktop flame to underside of overhead joinery/rangehood complies with manufacturer specs
checkpoint | Isolation valve has been installed
checkpoint | Gas regulator has been installed
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Full function of cooktop has been checked
checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | UQ Fit Off/ Fixture Install - RPZD
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint | Valve has been installed correctly and securely
checkpoint | Valve is functioning correctly
checkpoint | Valve discharges to tundish
checkpoint | Water connections installed correctly
checklist-flat | UQ Testing - Water Hold - Sewer & Stormwater Underslung
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Pipe has been checked and is clear of blockage
checkpoint | Pipe work is securely clipped and ready to hold water
checkpoint | Open ends have been sealed
checkpoint | Test was conducted from stack riser 1m above the highest overflow point
checkpoint | Test was successful as it held water at an unchanged level for at least 30mins
checkpoint | Water was drained from the pipe at the end of the test
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | UQ Testing - Water Hold - Sewer, Stormwater & Down Pipe Stacks
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Pipe has been checked and is clear of blockage
checkpoint | Pipe work is securely clipped and ready to hold water
checkpoint | Open ends have been sealed
checkpoint | Test was conducted from stack riser 1m above the highest overflow point
checkpoint | Test was successful as it held water at an unchanged level for at least 30mins
checkpoint | Water was drained from the pipe at the end of the test
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | UQ Testing - Potable Water - 1500kpa water test (not an air test)
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Water test is being conducted on material that is rated to withstand 1500kpa
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Test consisted of slowly increasing the pressure to 1500kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | UQ Testing - Potable Water - 900kpa water test pressure sensitive valves (not an air test)
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Water test is being conducted on material that is rated to withstand only 1000kpa
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Test consisted of slowly increasing the pressure to 900kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | UQ Testing - Natural Gas
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Water test is being conducted on material that is rated to withstand only 1000kpa
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends are securely capped off
checkpoint | Feeder valve was slowly opened & the test zone has filled with air until completely purged
checkpoint | Pressure testing device was connected to the nominated test point
checkpoint | Pressure testing device is calibrated
checkpoint | For high pressure test: Test consisted of slowly increasing pressure to 1.5 kPa above working pressure
checkpoint | For low pressure test: Test consisted of slowly increasing pressure no greater than 7 kPa
checkpoint | Testing was deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | UQ Testing - Air Test - Sewer & Stormwater Underslung
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Pipe has been checked and is clear of blockage
checkpoint | Pipe work is securely clipped and ready for test
checkpoint | Open ends have been sealed
checkpoint | Temporary valved test point with union fitting was used
checkpoint | Pressure testing device connected to temporary valve point
checkpoint | Test consisted of slowly increasing pressure to 30 kPa
checkpoint | Pressurization was discontinued to allow system to stabilise over 3 minutes
checkpoint | Testing was deemed successful if the pressure drop of less than or equal to 5 kPa over at least 30mins
checklist-flat | UQ Testing - Air Test - Sewer, Stormwater & Down Pipe Stacks
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
checkpoint | Pipe has been checked and is clear of blockage
checkpoint | Pipe work is securely clipped and ready for test
checkpoint | Open ends have been sealed
checkpoint | Temporary valved test point with union fitting was used
checkpoint | Pressure testing device connected to temporary valve point
checkpoint | Test consisted of slowly increasing pressure to 30 kPa
checkpoint | Pressurization was discontinued to allow system to stabilise over 3 minutes
checkpoint | Testing was deemed successful if the pressure drop of less than or equal to 5 kPa over at least 30mins
checklist-flat | UQ Testing - TMV
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
text | Hot water delivery time from cold to stable hot to be logged
text | Hot water delivery temperature to be logged |  |  | degrees
checkpoint | System has been returned to working conditions
text | Temp and Time reading photos must be taken at start & finish of test
checklist-flat | UQ Testing - Tempering Valve
checkpoint-no-status | Is there existing work by previous plumbing contractor within workfront? (Pass = Yes)
text | Photos of prior works BEFORE RSG commencement must be included here
text | Hot water delivery time from cold to stable hot to be logged
text | Hot water delivery temperature to be logged |  |  | degrees
checkpoint | System has been returned to working conditions
text | Temp and Time reading photos must be taken at start & finish of test