## Resources
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Installation Pump Station or Tank (In-ground) |  | Installation Pump Station or Tank (In-ground) | 054f7384-e160-4e37-9ac4-836e01c4e12b
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Plant & Equipment Installation checked off as below
| checkpoint | Installation complies with current AS/NZS-3500
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check connections to pits, tanks, & pump stations, etc
| checkpoint | Check covers, venting, & electrical conduits, etc
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check inspection openings
| checkpoint | Check open ends are sealed
| checkpoint | If trench is to be left open, make ensure pipe can not float
| checkpoint | Check trench backfill & compaction
| checkpoint | Must provide photo
| checklist | Commission Fixture Group |  | Commission Fixture Group | 0a4a6cf1-7335-4610-a725-497992f960b1
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS-5601 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for any damage, leaks or missing components
| checkpoint | Check level & alignment of all fixtures
| checkpoint | Check all fixtures, seats & covers are securely fastened
| checkpoint | Check all valves are fully open
| checkpoint | Check all flexible connections are not twisted or kinked
| checkpoint | Check for water for cross connections
| checkpoint | Check fixture wastes & connections
| checkpoint | Check pipework & all traps are clear of debris
| checkpoint | Check AAV is installed to correct height
| checkpoint | Check future connection water valves are securely capped
| checkpoint | Check TV do not exceed 50°C
| checkpoint | Check TMV do not exceed 45°C
| checkpoint | Check dishwasher function
| checkpoint | Check gas valves & regulators
| checkpoint | Check all gas burner functions
| checkpoint | Check balcony hose tap
| checkpoint | Check balcony floor grate & downpipe
| checkpoint | Check all fixtures & tapware are operating as specified
| checkpoint | Confirm area has been left clean
| checklist | Commission Water Storage Tank |  | Commission Water Storage Tank | 0c5da859-9e71-4766-9e35-f76d344d6428
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check valves are fully open
| checkpoint | Check water level sensor set points
| checkpoint | Check tank fill valve
| checkpoint | Check low level fault
| checkpoint | Check high level fault
| checkpoint | Check passive over-flow
| checkpoint | Check statutory warning signage
| checkpoint | Check control panel display & set points
| checkpoint | Check BMS connection as specified
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Suction Line |  | Installation Suction Line | 0d32f531-a574-48ca-bfef-9c23bc0b0627
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Fit-off Shower & Tapware |  | Fit-off Shower & Tapware | 0fd02e1a-12d8-48d7-9413-2878fe8051ba
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check wall plates, mixers & diversion valves
| checkpoint | Check outlets, wall rails & hand showers
| checkpoint | Check special DDA accessories (if applicable)
| checkpoint | Check waste & trap connections
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check floor grate level & alignment
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Testing Recycled Water Pipework |  | Testing Recycled Water Pipework | 143cf1c5-cad2-46f6-b8a6-e67342696236
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check installation is clean and ready for testing
| checkpoint | Are all valves, meters, etc , rated for the test pressure required
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 1 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checkpoint | R3 certification has taken place (Provide photo of or attach PDF copy of the Authority acceptance report)
| checklist | Commission Drainage Pump Station |  | Commission Drainage Pump Station | 18ce7b61-b98b-40ef-a0e4-214f15dea2eb
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check lifting rails & chains
| checkpoint | Check water level sensor set points
| checkpoint | Check pump motor rotation
| checkpoint | Check dry pump fault
| checkpoint | Check low water level fault
| checkpoint | Check high water level fault
| checkpoint | Check auto pump roll-over
| checkpoint | Check pump package operational set points
| checkpoint | Check control panel display & set points
| checkpoint | Check fault warning alarms
| checkpoint | Check BMS connection as specified
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Gas Service (Rough-ins) |  | Installation Gas Service (Rough-ins) | 1b80951c-4f9b-4878-b3ba-d9de1eabbb67
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check pipework can not be holed by plaster screws
| checkpoint | Check crimp fittings
| checkpoint | Check for cross connections
| checkpoint | Check alignment & levels
| checkpoint | Check materials & joining methods
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check lugged elbows
| checkpoint | Check noggings for future fixture
| checkpoint | Check sharp edge pipe protection
| checkpoint | Check pipe colour coding
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Testing Drainage Pipework (Water Test) |  | Testing Drainage Pipework (Water Test) | 1c176709-2e15-48b2-bfe0-4a272e5ca1e1
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Installation Authority Main to Meter |  | Installation Authority Main to Meter | 1fd448db-2687-45f5-a8a2-30e294d1baaf
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check valve connections
| checkpoint | Check pipework is clear of debris
| checkpoint | Check pipe trench marking tape (if specified)
| checkpoint | Check trench backfill & compaction
| checkpoint | Check water meter assemblies
| checkpoint | Check RPZD assemblies (if specified)
| checkpoint | Check pipe labelling
| checklist | Fit-off Hose Tap |  | Fit-off Hose Tap | 33cfa065-c45e-498f-9467-88fa155c24dd
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Vacuum breaker fitted
| checkpoint | Check pipe colour coding
| checklist | Installation Penetration |  | Installation Penetration | 43be0415-ea9a-423d-9c57-4e5a39e041ef
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & missing penos
| checkpoint | Check penetration sizes, locations & finished levels are correct
| checkpoint | Check fire collars types & ratings are correct
| checkpoint | Check blank sleeves are correct
| checkpoint | Check cast-in outlets location & finished levels are correct
| checkpoint | Check open ends are sealed
| checklist | Installation Water Storage Tank |  | Installation Water Storage Tank | 48ae6775-d581-46a5-8cc6-600b1b6055fb
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Tank Details:
d4db202b-c5da-5bd9-bc38-0c989d145786 | dropdown | Tank Type: | Potable Water Above Ground,Rain Water Above Ground,Potable Water In-ground,Rain Water In-ground,Fire Water Above Ground,Other
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check inlet/outlet connections & vents
| checkpoint | Check covers, venting, & electrical conduits, etc
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check inspection openings
| checkpoint | Check open ends are sealed
| checkpoint | Check trench backfill & compaction
| checklist | Installation Water Service (Mains/Risers) |  | Installation Water Service (Mains/Risers) | 4e5dbad6-2668-489e-a6fb-aab5bb8b7e59
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check crimp fittings
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check isolation & pressure reduction valves & meter assemblies
| checkpoint | Check hot water pipe clips & thermal insulation (if specified)
| checkpoint | Check pipework is clear of debris
| checkpoint | Check for cross connections
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe labelling
| checkpoint | Check pipe colour coding
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Fit-off Toilet & Cistern |  | Fit-off Toilet & Cistern | 51acb52c-5522-4291-acf5-41679ba8f4d4
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check special DDA accessories (if applicable)
| checkpoint | Check all functions, controls & remote sensors for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Installation Pump Line |  | Installation Pump Line | 56683928-9785-4112-8dc9-18f7e9a45f88
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Commission Water Pressure Pump Set |  | Commission Water Pressure Pump Set | 5d7ba783-c559-453d-ab39-e2d16f466d7c
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check water supply fault
| checkpoint | Check pump motor rotation
| checkpoint | Check dry pump fault
| checkpoint | Check auto pump roll-over
| checkpoint | Check pump package operational set points
| checkpoint | Check control panel display & set points
| checkpoint | Check fault warning alarms
| checkpoint | Check BMS connection as specified
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Water Pressure Pump Set |  | Installation Water Pressure Pump Set | 5e688d30-78b8-4380-bbe1-9cb9719d7b0e
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Pump Set Details:
dbb13c7b-78da-5575-b79c-e2ba3c1332f6 | dropdown | Pump Set Type: | Potable Cold Water,Potable Hot Water,Recycled Rain Water,Non-Potable Water,Other
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check isolation valves & non-return valves
| checkpoint | Check feed & delivery pipe connections
| checkpoint | Check back-up water supply by-pass (if specified)
| checkpoint | Check Control Panel
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check electrical power is available
| checkpoint | Check BMS is available
| checklist | Testing Drainage Pipework (Air Test) |  | Testing Drainage Pipework (Air Test) | 67e16762-68f0-4f7c-b077-ccc47e7e209c
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Installation Gas Service (Mains/Risers) |  | Installation Gas Service (Mains/Risers) | 6ae8eea0-33ac-416c-9faf-84fe13ea2ac0
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check crimp fittings
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check valves & meter assemblies
| checkpoint | Check valves & meter assemblies fixings & brackets
| checkpoint | Check pipework is clear of debris
| checkpoint | Check for cross connections
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Fit-off Gas Appliance |  | Fit-off Gas Appliance | 6eb0476b-0915-4e21-8b72-b2716c2f2ce9
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment is correct
| checkpoint | Check surrounding wall material is fire rated
| checkpoint | Check distance from cook-top to range hood complies with manufacturer specification
| checkpoint | Check surrounding walls to closest burner distance complies with manufacturer specification
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check gas isolation valve
| checkpoint | Check gas pressure regulator
| checkpoint | Check all functions & controls for correct operation
| checklist | Testing Gas Pipework (7kPa or Less) |  | Testing Gas Pipework (7kPa or Less) | 6f7ce3af-cdb5-4927-beb3-c1930179e9f3
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-5601
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-5601 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Testing Drainage Pipework (Hydrostatic Test) |  | Testing Drainage Pipework (Hydrostatic Test) | 7015aac3-aa0f-46f9-85e6-1ba285d449ca
| section | Details:
| checkpoint | Installation complies with current AS/NZS-3500
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check installation is clean and ready for testing
| checkpoint | Apply water pressure test as per AS/NZS-3500
| checkpoint | Must provide test start & finish photos
| checklist | Fit-off Wash Basin & Tapware |  | Fit-off Wash Basin & Tapware | 827b15c7-54f8-4216-bb21-5e612a2d25c4
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check special DDA accessories (if applicable)
| checkpoint | Check waste & trap connections
| checkpoint | Check all functions, controls & remote sensors for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Installation Drainage (In-ground) |  | Installation Drainage (In-ground) | 8d87f56a-1721-4a83-9743-1767c0311f4d
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check connections to pits, tanks, & pump stations, etc
| checkpoint | Check covers, venting, & electrical conduits, etc
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check inspection openings
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe trench marking tape (if specified)
| checkpoint | Check trench backfill & compaction
| checklist | Installation Water Meter |  | Installation Water Meter | 919b5706-5174-42a4-9fbd-a7e2e105285d
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Water Meter Details:
cfe26dbb-19c5-556b-aff5-d5a049ba0725 | textbox | Meter Type:
cd821c70-f9f9-5dd8-984b-06bb99a8bfa9 | textbox | Meter Number:
346bc941-5b73-5396-9c8e-a63e4c192e6f | textbox | Meter Location:
673eb70f-07f6-5222-9121-c139d0d97f22 | dropdown | Meter Size: | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checklist | Installation Gas Service (In-ground) |  | Installation Gas Service (In-ground) | 94a5aa0d-4424-4c45-af80-d0a68fb7accf
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check valve connections
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe trench marking tape (if specified)
| checkpoint | Check trench backfill & compaction
| checklist | Fit-off Washing Machine Stops |  | Fit-off Washing Machine Stops | 982d807f-09df-4b4a-b997-1cfc8ab00559
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check level & alignment
| checkpoint | Check stops hose connections are capped off
| checklist | Fit-off Tundish |  | Fit-off Tundish | 9b9aec78-a2e3-49e5-843d-b2822e5e6ece
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check waste & trap connections
| checkpoint | Check trap is clear of debris
| checklist | Fit-off Cleaners Sink & Tapware |  | Fit-off Cleaners Sink & Tapware | 9f0dbdbd-b00c-4d4e-ad99-d69b7de74706
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check tapware for fit & function
| checkpoint | Check wall brackets & fixings
| checkpoint | Check bucket grate
| checkpoint | Check waste & trap connections
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Installation Water Service (In-ground) |  | Installation Water Service (In-ground) | a8e23405-9418-46fb-aa5e-b1f5bf0c1581
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check valve connections
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe trench marking tape (if specified)
| checkpoint | Check trench backfill & compaction
| checklist | Installation Hot Water Unit |  | Installation Hot Water Unit | a8e445df-a6d4-4cb1-a082-41bed58bb545
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with current AS/NZS-3500
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check level & alignment
| checkpoint | Check safe tray (if specified)
| checkpoint | Check isolation valves & non-return valves
| checkpoint | Check pressure reduction valve (if specified)
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check waste & water connections
| checkpoint | Check operation & controls
| checkpoint | Check water temperatures are as specified
| checkpoint | Check electrical power is available
| checkpoint | Check solar connecting pipework & fittings
| checkpoint | Check solar pump operation
| checkpoint | Check solar panels & mounting brackets
| checkpoint | Must provide photo
| checklist | Fit-off Kitchen Sink & Tapware |  | Fit-off Kitchen Sink & Tapware | ad2a42fa-387b-4e77-9f27-c7681a28592e
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check waste & trap connections
| checkpoint | Check dishwasher waste & water connections
| checkpoint | Check stop valves for future connections are capped
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Add New Task |  | Add New Task | b21280b1-866e-4691-8f97-6229ada4256f
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | New task checked off (Add brief description of this task and take photos)
| checklist | Commission Thermostatic Mixing Valves |  | Commission Thermostatic Mixing Valves | bab90a16-e109-4083-b12d-7c5e1ee16c01
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check water temperature does not exceed 45°C
| checklist | Commission Reduced Pressure Zone Device |  | Commission Reduced Pressure Zone Device | c1a7953f-fc0a-4810-bfe2-187d2546bafc
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | RPZD Details:
d7ca90c7-008e-5369-a1a7-7c4540d72953 | textbox | RPZD Serial Number:
4b7cc0ea-c1b3-53c6-b662-3a63abc77882 | textbox | RPZD Location:
35e4ceff-f4cb-5455-8f15-31464e541550 | dropdown | RPZD Size: | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
| checkpoint | Check valves are fully open
| checkpoint | Check inlet water pressure does not exceed manufacturer specification
| checkpoint | Check outlet water pressure is as per manufacturer specification
| checkpoint | Check exhaust tundish drain sized to accept a full flush
| checkpoint | Provide the commissioning report & all plant documentation to this checkpoint
| checklist | Cast-in Waste & Vent |  | Cast-in Waste & Vent | c1c90ad7-9104-41aa-bd5f-fbbcb7b0b8c1
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check pipe expansion lagging
| checkpoint | Check open ends are sealed
| checklist | Commission Rain Water Diversion Valve |  | Commission Rain Water Diversion Valve | c3d9d147-3e35-4d9a-9c1c-bc3b1951cd40
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check valve operation
| checkpoint | Check valve defaults to storm-water if no power or tank full
| checkpoint | Check control panel display & set points
| checkpoint | Check BMS connection as specified
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Commission Rain Water Pressure Pump Set |  | Commission Rain Water Pressure Pump Set | c963be1f-022c-495d-b4fb-e824576910a2
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check water supply fault
| checkpoint | Check pump motor rotation
| checkpoint | Check dry pump fault
| checkpoint | Check auto pump roll-over
| checkpoint | Check ultra violet lamps
| checkpoint | Check filters & backwash
| checkpoint | Check back-up water supply
| checkpoint | Check pump package operational set points
| checkpoint | Check control panel display & set points
| checkpoint | Check fault warning alarms
| checkpoint | Check BMS connection as specified
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Pump Station |  | Installation Pump Station | c9b5c128-9d56-46e1-9ef2-417860afc502
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Pump Station Details:
21fbf836-4d5d-5ba4-aad0-386cb8f69d1a | dropdown | Pump Station Type: | Sewer Above Ground,Stormwater Above Ground,Sewer In-ground,Stormwater In-ground,Other
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check inlet/outlet connections & vents
| checkpoint | Check covers, venting, & electrical conduits, etc
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check inspection openings
| checkpoint | Check open ends are sealed
| checkpoint | Check trench backfill & compaction
| checklist | Testing Gas Pipework (Above 7kPa) |  | Testing Gas Pipework (Above 7kPa) | cb563923-5f47-4766-a6c7-1e32a21ba525
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-5601
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-5601 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Fit-off Laundry Trough & Tapware |  | Fit-off Laundry Trough & Tapware | cba06ec7-0dc6-407c-9ee6-921205b0f758
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check waste & water connections
| checkpoint | Check stop valves for future connections are capped
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Fit-off Dishwasher |  | Fit-off Dishwasher | cf660277-8071-4c05-bcd3-721f8f1e6e80
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check isolation valves & non-return valves
| checkpoint | Check pressure reduction valve (if specified)
| checkpoint | Check flexible waste & water hoses are not twisted or kinked
| checkpoint | Check flexible waste hose height under cabinet
| checkpoint | Check waste connection to trap
| checkpoint | Check all functions & controls for correct operation
| checklist | Installation Waste & Vent |  | Installation Waste & Vent | d7009d27-fd1c-42ab-bf98-5b0cc4b4572f
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check in-wall fixture mounting brackets & concealed cisterns (if specified)
| checkpoint | Check in-wall waste pipes & vents
| checkpoint | Check inspection openings
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check acoustic insulation (if specified)
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checkpoint | Check vents are run to atmosphere and weather proofing is complete
| checklist | Commission Hot Water Generating Plant |  | Commission Hot Water Generating Plant | d999e01e-f940-4e29-a49c-b0fe90aaefc2
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS-5601 (Note: Commissioning photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check valves are fully open
| checkpoint | Check water filters are clean
| checkpoint | Check gas supply
| checkpoint | Check circulating pumps
| checkpoint | Check flue operation
| checkpoint | Check system auto start
| checkpoint | Check flow & return temperatures
| checkpoint | Check control panel display & set points
| checkpoint | Check BMS connection (if specified)
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Downpipe & Overflow |  | Installation Downpipe & Overflow | dd828ade-82ff-407e-8fe5-17585993a335
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check connection to roof & floor outlets
| checkpoint | Check inspection openings
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check acoustic insulation (if specified)
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Fit-off Bath & Tapware |  | Fit-off Bath & Tapware | e06fc2d7-1a96-4b98-9e59-fdbc370f61b7
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check wall plates, mixers & diversion valves
| checkpoint | Check outlets, wall rails & hand showers
| checkpoint | Check special DDA accessories (if applicable)
| checkpoint | Check waste & trap connections
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check floor grate level & alignment
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Installation Waste Water Tank |  | Installation Waste Water Tank | e30ba22e-2191-498e-abe6-417a0c2bd545
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Tank Details:
a3e2d56c-ba15-58b5-8c8e-8177203a7cf3 | dropdown | Tank Type: | Grease Interceptor,Neutralizing Pit,POI Interceptor,SW Detention Tank,SW Filtration Pit,Other
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check inlet/outlet connections & vents
| checkpoint | Check covers, venting, & electrical conduits, etc
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check inspection openings
| checkpoint | Check open ends are sealed
| checkpoint | Check trench backfill & compaction
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check installation is clean and ready for testing
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Installation Plant & Equipment |  | Installation Plant & Equipment | e5d99ad1-a38a-45e3-aea3-8633787b6d9c
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Plant & Equipment Installation checked off as below
| checkpoint | Installation complies with current AS/NZS-3500 & AS/NZS-5600
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check tundishes are correct
| checkpoint | Check electrical power is available
| checkpoint | Check BMS is available
| checkpoint | Must provide photo
| checklist | Testing Potable Water Pipework |  | Testing Potable Water Pipework | e68247e5-96db-423b-bf02-eddc287943fc
| section | Details:
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check installation is clean and ready for testing
| checkpoint | Check all valves, mixers, meters, etc , in the test zone are rated for the test pressure required
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 1 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Installation Backflow Prevention Device |  | Installation Backflow Prevention Device | e869746d-bc79-474e-bf79-bc228b4305a9
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | RPZD Details:
211bbd3d-a453-517c-8b72-dce8c005cf44 | textbox | RPZD Serial Number:
ab345092-20ae-55f4-a0de-df8856b63a41 | textbox | RPZD Location:
178f0064-1eea-5f8d-8353-1713fbe6487a | dropdown | RPZD Size: | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm,300mm
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check pressure relief pipe to tundish
| checklist | Installation Hot Water Plant/Unit |  | Installation Hot Water Plant/Unit | ed552afd-b058-48fe-be33-40ebdf0e30fd
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4, &/or AS/NZS-5601 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check level & alignment
| checkpoint | Check safe tray (if specified)
| checkpoint | Check isolation valves & non-return valves
| checkpoint | Check pressure reduction valve (if specified)
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check waste & water connections
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check water temperatures are as specified
| checkpoint | Check electrical power is available
| checkpoint | Check solar panels & mounting brackets
| checkpoint | Check solar connecting pipework & fittings
| checkpoint | Check solar pump operation
| checklist | Installation Water Service (Rough-ins) |  | Installation Water Service (Rough-ins) | ef7ee840-ae91-4d71-af83-f10fe064613e
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check pipework can not be holed by plaster screws
| checkpoint | Check crimp fittings
| checkpoint | Check for cross connections
| checkpoint | Check alignment & levels
| checkpoint | Check materials & joining methods
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check TMV/TV
| checkpoint | Check in-wall mixer bodies & lugged elbows
| checkpoint | Check in-wall fixture mounting brackets & concealed cisterns (if specified)
| checkpoint | Check noggins for future fixture
| checkpoint | Check sharp edge pipe protection
| checkpoint | Check heat trace (if specified)
| checkpoint | Check hot water pipe clips & thermal insulation (if specified)
| checkpoint | Check pipe colour coding
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Fit-off Urinal & Cistern |  | Fit-off Urinal & Cistern | efa8ecc5-47bc-4625-9c1c-07a16cdf6b46
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Fit-off photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check button assembly
| checkpoint | Check all functions, controls & remote sensors for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking is correct
| checklist | Installation Stack & Vent |  | Installation Stack & Vent | f4ac3eeb-d34a-4433-84bc-12fe54676b8d
| section | Details:
| checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation or additional work. If not, mark as 'N/A'. You must still action all remaining checkpoints
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 (Note: Installation photos to be taken only within this Checkpoint)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Check for damage & leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings (correct size, spacing & separation)
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check inspection openings
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check acoustic insulation (if specified)
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checkpoint | Check vents are run to atmosphere and weather proofing is complete