## Resources
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Installation Sewer/Trade Waste Drainage (In-ground) |  | Installation Sewer/Trade Waste Drainage (In-ground) | 00178d3a-73f6-41a6-aa18-b9bfa20efe89
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Details:
11973da9-b579-52b0-b7b5-32a1e10e64f2 | textbox | Service Type:
61e976af-5059-5a7e-b102-44c7ffcce9a7 | dropdown |  | Sewer Drainage,Trade Waste Drainage,Other
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments, levels, grades, etc
| checkpoint | Check bedding & clearances
| checkpoint | Check BT shafts, inspection shafts, inspection openings, etc
| checkpoint | Check pump station chambers, interceptor tanks, manholes, drainage pits, etc
| checkpoint | Check grates/covers, chamber venting, trap venting, cable conduits, etc
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checklist | Commissioning Monitored Water Valve |  | Commissioning Monitored Water Valve | 071fce80-1231-4c24-a4b4-69703fe36cb2
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Valve Details:
db77f4f1-5b3d-5e56-b5b1-33653fa03c10 | textbox | Serial Number:
df40f0a2-fbf5-5531-bd87-c98a775c26c5 | textbox | Location:
80bd09f0-33c9-5f96-b3c1-152bb5ff3db9 | textbox | Size:
b78c6a61-1319-5f5d-98c1-95383053fb61 | dropdown |  | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check BMS connection
| checkpoint | Check pipe labelling
| checklist | Installation Water Service (In-ground) |  | Installation Water Service (In-ground) | 0825b51b-13af-44df-96cc-0d20a5711c43
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check isolation valves, connections, etc
| checkpoint | Check thrust blocks
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checklist | Installation Fire Service (In-ground) |  | Installation Fire Service (In-ground) | 0d2df46c-288a-4086-9d2b-771d3324661b
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-1221
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check pipe specification markings are visible
| checkpoint | Check PE fusion joints
| checkpoint | Check roll-groove couplings
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check isolation valves, connections, valve covers, etc
| checkpoint | Check monitored valves & connections
| checkpoint | Check thrust blocks
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checklist | Fit-off Bath & Tapware |  | Fit-off Bath & Tapware | 0fdfab38-d25e-454c-ae22-52f50f9b17f8
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check wall plates, mixers & diversion valves
| checkpoint | Check outlets, wall rails & hand showers
| checkpoint | Check special DDA accessories
| checkpoint | Check waste & trap connections
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check floor grate level & alignment
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Installation Backflow Prevention Device |  | Installation Backflow Prevention Device | 1038073b-e8aa-4197-9471-b026f5a73f85
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check isolation valves, filters, connections, etc
| checkpoint | Check pressure relief to drainage
| checklist | Fit-off Hose Tap |  | Fit-off Hose Tap | 1dc848fd-6886-4df3-a128-fd1874b0f667
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check tap is securely fixed
| checkpoint | Vacuum breaker fitted
| checkpoint | Check pipe colour coding
| checklist | Add New Task |  | Add New Task | 25a436ec-e9fe-4e54-8757-e000e39d322a
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | New task checked off (Add brief description of this task. Add photos & attach any documentation)
| checklist | Fit-off Wash Basin & Tapware |  | Fit-off Wash Basin & Tapware | 262f7f1d-8c53-40f0-92e5-843ecd903dd7
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check special DDA accessories
| checkpoint | Check waste & trap connections
| checkpoint | Check all functions, controls & remote sensors for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Fit-off Cleaners Sink & Tapware |  | Fit-off Cleaners Sink & Tapware | 2739eb87-b4a2-4590-bee5-034184d1d421
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check tapware for fit & function
| checkpoint | Check wall brackets & fixings
| checkpoint | Check bucket grate
| checkpoint | Check waste & trap connections
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Commission Backflow Prevention Device |  | Commission Backflow Prevention Device | 2ceae05a-12bc-4fa7-9441-8276785ed860
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Backflow Prevention Details:
53ac29aa-e53d-5d03-8204-a50924b1c89f | textbox | Valve Type:
a90e7052-d395-551f-b3d8-a564afa2b05c | dropdown |  | Reduced Pressure Zone Device,Double Check Valve,Single Check Valve
7118afec-b28b-5287-95da-8649da4712c9 | textbox | Hazard Type:
94623e4b-04ec-55c0-8b27-14b46b7cdb06 | dropdown |  | High Hazard,Medium Hazard,Low Hazard
fc21abd8-1c3a-50e7-a344-7e86b8a34b82 | textbox | Serial Number:
3e457310-a64a-55e2-917c-bf1b65632664 | textbox | Location:
709fc9c9-27c7-5545-bfc9-d07c8fd06329 | textbox | Size:
97f7dab0-a909-5818-b2e6-b786c6db67fe | dropdown |  | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check valves are fully open
| checkpoint | Check inlet water pressure does not exceed manufacturer specification
| checkpoint | Check outlet water pressure is as per manufacturer specification
| checkpoint | Check exhaust drain is sized to accept a full flush
| checkpoint | Provide the commissioning report & all plant documentation to this checkpoint
| checklist | Commission Hot Water Generating Plant |  | Commission Hot Water Generating Plant | 2dca079c-b3e2-4754-ac09-2465054c8ad6
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Hot Water Plant Details:
e1ef533c-3093-5674-b94f-30e30f1af616 | textbox | Type:
49a47a5c-1402-5e8b-bd05-b8627cc7ee30 | dropdown |  | Bulk Gas Hot Water Plant,Bulk Gas Warm Water Plant,Elec Commercial Heat Pump,Elec Domestic Heat Pump,Gas Instantaneous Domestic,Elec Domestic Storage,Gas Domestic Storage,Other
3b98ff17-ccf1-5272-8676-94e11e6aafba | textbox | Solar Preheat:
de16c7ee-2132-5f2b-bb1b-595b5cd31bc6 | dropdown |  | Yes,No
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check isolation valves are fully open & non-return valves flow direction
| checkpoint | Check water filters are clean
| checkpoint | Check gas supply
| checkpoint | Check circulating pumps
| checkpoint | Check flue system & operation
| checkpoint | Check system auto start
| checkpoint | Check flow & return temperatures
| checkpoint | Check control panel display
| checkpoint | Check programmed set points
| checkpoint | Check BMS connection
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Water Service (Mains/Risers) |  | Installation Water Service (Mains/Risers) | 325c6ae2-4293-4bce-b53b-89b48dae58e3
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check crimp fittings & joints
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check isolation valves, pressure reduction valves, meter assemblies, connections,etc
| checkpoint | Check hot water pipe clips & thermal insulation
| checkpoint | Check pipework is clear of debris
| checkpoint | Check for cross connections
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Installation Fire Booster Assembly |  | Installation Fire Booster Assembly | 3cd5a731-e930-4443-b930-fd7efa09d6b2
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe brackets & supports are correctly positioned & bedded
| checkpoint | Check thrust blocks
| checkpoint | Check bedding & clearances
| checkpoint | Check suction valve assembly
| checkpoint | Check booster valve assembly
| checkpoint | Check hose connection screw caps
| checkpoint | Check monitored valves & connections
| checkpoint | Check isolation valves, connections, etc
| checkpoint | Check pipework is clear of debris
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checkpoint | Check pipe labelling
| checklist | Fit-off Laundry Trough & Tapware |  | Fit-off Laundry Trough & Tapware | 3d643d79-ce91-4f58-85ac-26c6a52d9937
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check waste & water connections
| checkpoint | Check stop valves for future connections are capped
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Fit-off Kitchen Sink & Tapware |  | Fit-off Kitchen Sink & Tapware | 3f59e73b-5c12-411f-89a0-d6577bd11f13
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check waste & trap connections
| checkpoint | Check dishwasher waste & water connections
| checkpoint | Check stop valves for future connections are capped
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Installation Gas Service (Mains/Risers) |  | Installation Gas Service (Mains/Risers) | 4699707d-ac04-4cbf-9008-d7292e483e01
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check crimp fittings & joints
| checkpoint | Check for cross connections
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check isolation valves, pressure regulators, meter assemblies, connections,etc
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Commission Potable Water Pressure Pump Set |  | Commission Potable Water Pressure Pump Set | 4770fc96-7cc2-4352-8016-7ca1d476d334
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Pump Station Details:
2a7250b9-d5f1-5084-8a77-318fe7a98895 | textbox | Service Type:
16eb7515-519e-584d-986d-ffb8a0d554ee | dropdown |  | Potable Cold Water,Potable Hot Water,Fire Water,Other
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check isolation valves are fully open & non-return valves flow direction
| checkpoint | Check water supply fault
| checkpoint | Check pump motor rotation
| checkpoint | Check dry pump fault
| checkpoint | Check auto pump roll-over
| checkpoint | Check control panel display
| checkpoint | Check programmed set points
| checkpoint | Check BMS connection
| checkpoint | Check fault warning alarms
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Commissioning Water Check Meter |  | Commissioning Water Check Meter | 4b97b0f0-330c-4a6c-8643-3da8a516c65d
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Meter Details:
1ec5af3d-9e43-588e-b15a-2fa96fd3bafc | textbox | Type:
37bfdf0b-2ef2-5566-afa3-96569c122f4f | dropdown |  | Magflow Meter,Digital Pulse Meter,Analogue Meter,Other
a2d40227-a682-56e3-80d6-1e439f5abb35 | textbox | Serial Number:
c75b3fb2-0a94-5a39-8b9e-c8d0cb660027 | textbox | Location:
8e9c081d-9b31-56d1-b66e-d2be6a357825 | dropdown |  | Outdoors,Meter Box,Ceiling Access,Meter Manifold,Other
80fdcd23-abd4-56cf-93d0-091d2a6cd7bf | textbox | Size:
67d5b94c-26e2-5e59-8758-43adfe423135 | dropdown |  | 20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check correct meter spacing if installed in a manifold assembly
| checkpoint | Check isolation valves, pressure reduction valves, water filters, connections, etc
| checkpoint | Check access panel for ceiling mounted meter
| checkpoint | Check analogue display can be read manually
| checkpoint | Check BMS connection
| checkpoint | Check digital pulse rate is as specified
| checkpoint | Check pipe labelling
| checklist | Fit-off Tundish |  | Fit-off Tundish | 4f935216-a799-4a8a-ab0e-40c45a1220aa
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check waste & trap connections
| checkpoint | Check trap is clear of debris
| checklist | Installation Hot Water Plant/Unit |  | Installation Hot Water Plant/Unit | 52d49ede-27f7-4b11-bca0-62eab6067977
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4, &/or AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check level & alignment
| checkpoint | Check all pipework, isolation valves, non-return valves, pressure reduction valves, water filters & connections, etc
| checkpoint | Check bold-down & fixing points are secure
| checkpoint | Check cable conduits
| checkpoint | Check thermal pipe lagging
| checkpoint | Check PTR valve, safe tray & drainage
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check solar panels & mounting brackets
| checkpoint | Check solar connecting pipework & fittings
| checkpoint | Check circulation pump installation
| checkpoint | Check installation of flue system if applicable
| checkpoint | Check control panel is installed
| checkpoint | Check power & data cables are run to the control panel
| checkpoint | Check electrical power is available
| checkpoint | Check BMS connection is available
| checklist | Installation Fire Service (Hose Reels) |  | Installation Fire Service (Hose Reels) | 57ba3b6a-a2ac-4fb5-bfc8-872e5347e9b5
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-1221
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check hose reel is mounted securely
| checkpoint | Check hose reel spindle heights are 1500mm above FSL
| checkpoint | Check hose reel cabinets conform (if specified)
| checkpoint | Check roll-groove couplings
| checkpoint | Check crimp fittings & joints
| checkpoint | Check materials & joining methods
| checkpoint | Check pipe specification markings are visible
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check isolation valves, connections,etc
| checkpoint | Check pipe labelling
| checklist | Installation Pump Lines |  | Installation Pump Lines | 57c990a6-8f99-450c-bffe-597e963f6c0a
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments, levels, grades, etc
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Commission Non-Potable/Rain Water Pressure Pump Set |  | Commission Non-Potable/Rain Water Pressure Pump Set | 5a95ba50-e8dc-404f-92b9-3448ac3cc131
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Pump Station Details:
67a44415-1ccb-5b75-8417-5dc95443717b | textbox | Service Type:
297d290c-4dbc-56f0-b675-87effdc8b9c3 | dropdown |  | Non-Potable Water,Rain Water,Fire Water,Other
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check isolation valves are fully open & non-return valves flow direction
| checkpoint | Check water supply fault
| checkpoint | Check pump motor rotation
| checkpoint | Check dry pump fault
| checkpoint | Check auto pump roll-over
| checkpoint | Check ultra violet lamps
| checkpoint | Check filters & backwash
| checkpoint | Check back-up water supply
| checkpoint | Check control panel display
| checkpoint | Check programmed set points
| checkpoint | Check BMS connection
| checkpoint | Check fault warning alarms
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Potable/Rain Water Pressure Pump |  | Installation Potable/Rain Water Pressure Pump | 61b0a62b-222e-482a-9ad2-d8cd31fe117d
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check bold-down & fixing points are secure
| checkpoint | Check cable conduits
| checkpoint | Check level & alignment
| checkpoint | Check all pipework, isolation valves, non-return valves, pressure reduction valves, water filters & connections, etc
| checkpoint | Check water by-pass water supply
| checkpoint | Check water filter back-wash drainage
| checkpoint | Check control panel is installed
| checkpoint | Check power & data cables are run to the control panel
| checkpoint | Check electrical power is available
| checkpoint | Check BMS is available
| checklist | Commission Thermostatic Mixing Valves |  | Commission Thermostatic Mixing Valves | 6203ece8-d540-4673-99f0-3668f768a946
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check TMV has been installed in a lockable wall box
| checkpoint | Check TMV has been installed in the room it services and can be readily accessed from floor level
| checkpoint | Check water temperature does not exceed 45°C for disabled persons
| checkpoint | Check water temperature does not exceed 43°C for special need persons
| checklist | Testing Drainage Pipework (In-ground) |  | Testing Drainage Pipework (In-ground) | 6659217e-410c-43c5-8a61-847ab7b875ff
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing Details:
852085be-f985-542e-8089-d703631f6d0f | textbox | Service Type:
21a79ad2-9f0f-5990-be2a-bf6b4cf4413a | dropdown |  | Sewer Drainage,Trade Waste Drainage,Storm Water Drainage,Other
b891c5ad-67be-5826-9f9e-01a3f7c28a24 | textbox | Test Type:
3195337e-df17-5659-9b29-67954dfbd5ab | dropdown |  | Static Water Test,Static Air Test,Other
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Installation Authority Primary Non-Potable Water Meter Assembly |  | Installation Authority Primary Non-Potable Water Meter Assembly | 66d4adba-07db-4e87-8ce0-15c9e6959631
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe brackets & supports are correctly positioned & bedded
| checkpoint | Check thrust blocks
| checkpoint | Check bedding & clearances
| checkpoint | Check isolation valves, filters, connections, etc
| checkpoint | Check pipework is clear of debris
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checklist | Installation Sewer/Trade Wastes & Vents |  | Installation Sewer/Trade Wastes & Vents | 674e7e2a-2dd9-4a3d-8609-b57ef0f9ca56
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Details:
c7aa339d-65e4-528d-b5b9-f6675afc9651 | textbox | Service Type:
e52913d7-9886-5ed6-8c08-b11f6d56ae3b | dropdown |  | Sewer Drainage,Trade Waste Drainage,Other
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments, levels, grades, etc
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check in-wall fixture mounting brackets & concealed cisterns
| checkpoint | Check in-wall waste pipes & vents
| checkpoint | Check inspection openings
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check acoustic insulation
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checkpoint | Check vents are run to atmosphere and weather proofing is complete
| checklist | Installation Penetration |  | Installation Penetration | 693284af-93ba-4f6a-9edb-ee6dd18f46a6
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check for damage & missing penos
| checkpoint | Check penetration sizes, locations & finished levels are correct
| checkpoint | Check fire collars types & ratings are correct
| checkpoint | Check blank sleeves are correct
| checkpoint | Check cast-in outlets location & finished levels are correct
| checkpoint | Check open ends are sealed
| checklist | Commission Rain Water Diversion Valve |  | Commission Rain Water Diversion Valve | 6a3dab88-6555-4509-8354-2b5deeb1457c
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check valve operation
| checkpoint | Check valve defaults to storm-water drainage on power loss or tank full
| checkpoint | Check control panel display
| checkpoint | Check programmed set points
| checkpoint | Check BMS connection
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Downpipes & Overflows |  | Installation Downpipes & Overflows | 71788d00-b2d1-4276-80bc-c83684a9fd8c
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments, levels, grades, etc
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check connections to cast-in: roof outlets, balcony outlets, overflow outlets, planter boxes, terrace drains, etc
| checkpoint | Check connections to metal roof: sumps, overflows, rain heads, etc
| checkpoint | Check inspection openings
| checkpoint | Check sprinkler service test point junction assembly
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check acoustic insulation
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Installation Water Service (Rough-ins) |  | Installation Water Service (Rough-ins) | 719ff36c-0790-4433-897f-812851f68687
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check pipework can not be holed by plaster screws
| checkpoint | Check crimp fittings & joints
| checkpoint | Check for cross connections
| checkpoint | Check alignment & levels
| checkpoint | Check materials & joining methods
| checkpoint | Check isolation valves, pressure reduction valves, meter assemblies, connections,etc
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check TMV/TV
| checkpoint | Check in-wall mixer bodies & lugged elbows
| checkpoint | Check in-wall fixture mounting brackets & concealed cisterns
| checkpoint | Check noggins for future fixture
| checkpoint | Check sharp edge pipe protection
| checkpoint | Check heat trace & control boxes
| checkpoint | Check hot water pipe clips & thermal insulation
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Commission Fixture Group |  | Commission Fixture Group | 73854fa9-002e-4ab1-a4e3-2662d90b25ee
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Thoroughly check all pipework, fittings, connections, etc for damage or water leaks
| checkpoint | Check for any damage or missing components
| checkpoint | Check level & alignment of all fixtures & tapware
| checkpoint | Check all fixtures, tapware & components are securely fixed
| checkpoint | Check all mini-stops and valves are fully open
| checkpoint | Check all pressure reduction & non-return valves
| checkpoint | Check all flexible connections are not twisted or kinked
| checkpoint | Check for water for cross connections
| checkpoint | Check fixture wastes & connections
| checkpoint | Check dishwasher drain hose is looped hard-up under bench-top
| checkpoint | Check pipework & all traps are clear of debris
| checkpoint | Check AAV is installed hard-up under bench-top
| checkpoint | Check future connection water valves are securely capped (fridge/washing machine stops)
| checkpoint | Check all hot water units are functioning correctly
| checkpoint | Check solar collectors are fitted & securely fixed
| checkpoint | Check solar circulation pump is functioning correctly
| checkpoint | Check TV do not exceed 50°C
| checkpoint | Check TMV do not exceed 45°C
| checkpoint | Check dishwasher function through short cycle
| checkpoint | Check gas valves & regulators
| checkpoint | Check gas flame stop device
| checkpoint | Check all gas burner functions
| checkpoint | Check balcony hose tap is securely fixed
| checkpoint | Check balcony floor grate is clear
| checkpoint | Check all downpipes & overflows are fitted correctly
| checkpoint | Check all vents are finished & weather proofed
| checkpoint | Check all fixtures & tapware function correctly
| checkpoint | Confirm area has been left clean
| checklist | Testing Drainage Pipework (Above Ground) |  | Testing Drainage Pipework (Above Ground) | 7536dee8-4cf0-454f-9b18-56e17bc56262
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing Details:
7578c3ad-7121-5804-8877-28f1436ae3db | textbox | Service Type:
ee9d9b9e-d9a9-55c0-9706-9c9b63cccb78 | dropdown |  | Sewer Drainage,Trade Waste Drainage,Storm Water Drainage,Other
3e0c5e72-376c-5780-861c-2d6ac26b4fdb | textbox | Test Type:
3db6b683-27a8-54c4-a7b9-33c661aa2e60 | dropdown |  | Active Water Flow,Static Water Test,Static Air Test,Other
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 2 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Fit-off Washing Machine Stops |  | Fit-off Washing Machine Stops | 7589f00d-75c8-4641-96ad-286e0a60c823
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check level & alignment
| checkpoint | Check stops hose connections are capped off
| checklist | Commission Water Storage Tank (Above Ground) |  | Commission Water Storage Tank (Above Ground) | 7a14cb28-45f1-4995-95d0-19e7f1e0e764
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Water Storage Tank Details:
94bd33cf-110b-528c-9f09-deaf90e64454 | textbox | Type:
ba5a75a4-36e1-5137-9530-f792a2b642ce | dropdown |  | Above Ground Potable Water,Above Ground Rain Water,Above Ground Fire Water,Other
f70e1b65-1bce-517a-99b7-28111d81adb4 | textbox | Capacity:
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check isolation valves are fully open & non-return valves flow direction
| checkpoint | Check access covers & hatches
| checkpoint | Check access ladders & statutory signage
| checkpoint | Check pipe connections & venting
| checkpoint | Check float tree or water level sensor is not impeded by water inflow
| checkpoint | Check water level set points
| checkpoint | Check back-up mains water supply
| checkpoint | Check 'Bermad' tank fill valve
| checkpoint | Check low level fault
| checkpoint | Check high level fault
| checkpoint | Check passive over-flow
| checkpoint | Check statutory warning signage
| checkpoint | Check control panel display
| checkpoint | Check programmed set points
| checkpoint | Check BMS connection
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Fit-off Gas Appliance |  | Fit-off Gas Appliance | 8b56bab1-c226-4bda-b103-5b702129d3b1
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment is correct
| checkpoint | Check surrounding wall material is fire rated
| checkpoint | Check distance from cook-top to range hood complies with manufacturer specification
| checkpoint | Check surrounding walls to closest burner distance complies with manufacturer specification
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check gas isolation valve
| checkpoint | Check gas pressure regulator
| checkpoint | Check flame failure device
| checkpoint | Check all functions & controls for correct operation
| checklist | Installation Potable/Rain Water Storage Tank |  | Installation Potable/Rain Water Storage Tank | 8f246ed9-0708-4a8f-88ab-04d1ef0b43cb
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check bold-down & fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check all pipework, fittings, valves & connections
| checkpoint | Check control panel is installed
| checkpoint | Check power & data cables are run to the control panel
| checkpoint | Check electrical power is available
| checkpoint | Check BMS is available
| checklist | Testing Gas Pipework |  | Testing Gas Pipework | 975e5a06-47dd-438d-8a89-8f238a77b5d5
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022) & ESV Regulations
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing Details:
0cd9290f-7e23-5291-bf96-dc8358d2b6e4 | textbox | Type:
879f9d92-26a0-55e4-a9f1-3d6bbab48fb6 | dropdown |  | Low Pressure,High Pressure
5bb0fbee-909c-5864-840a-122e2f3b5ad0 | textbox | Pressure:
a5c7604e-e087-5454-b879-93ead5b95b37 | dropdown |  | 7kPa,10kPa,20kPa,30kPa,40kPa,50kPa,1.5 x MWP,Other
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS 5601.1 (2022) & ESV Regulations (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Installation Suction Lines |  | Installation Suction Lines | 990eba49-02bc-4e8c-ac4a-008035d2503b
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments, levels, grades, etc
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Fit-off Toilet & Cistern |  | Fit-off Toilet & Cistern | 9bfee0a1-237b-45a4-ada1-d83d17fd98b1
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check special DDA accessories
| checkpoint | Check all functions, controls & remote sensors for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Installation Trade Waste Water Interceptor/Tank |  | Installation Trade Waste Water Interceptor/Tank | 9d65cbff-8e2b-47f4-96bd-21dd20966192
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check all pipework connections
| checkpoint | Check bedding & clearances
| checkpoint | Check inlet/outlet connections & vents
| checkpoint | Check covers & levels
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check inspection openings
| checkpoint | Check open ends are sealed
| checkpoint | Check trench backfill & compaction
| checklist | Installation Gas Service (In-ground) |  | Installation Gas Service (In-ground) | 9edbe792-2bef-4d6d-b0c2-fe4dc8a3948f
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check isolation valves, connections, etc
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checklist | Installation Stormwater Drainage (In-ground) |  | Installation Stormwater Drainage (In-ground) | 9effdbd3-2a9f-4ae6-b279-11f29f1fe9f1
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Details:
c413c473-9381-5e03-be12-1ad42b0e038a | textbox | Service Type:
ada1c4a8-5b66-5267-b388-3129a47621aa | dropdown |  | Sewer Drainage,Trade Waste Drainage,Other
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments, levels, grades, etc
| checkpoint | Check bedding & clearances
| checkpoint | Check AG drainage, geofabric wrap, spoon drain outlets, clear-outs, etc
| checkpoint | Check pump station chambers, detention/storage tanks, filtration tanks, drainage pits, etc
| checkpoint | Check pit grates/covers, trench grates, pump station cable conduits, etc
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check inspection openings
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checklist | Commission Storm Water Tank (In-ground) |  | Commission Storm Water Tank (In-ground) | a0e3ff51-b9ed-4517-83ef-528f399cbe14
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Water Storage Tank Details:
1adb1089-439a-54ee-8b44-282e90f17235 | textbox | Type:
fc00a95d-9dc4-5242-ae69-320b7cf60108 | dropdown |  | In-ground Storm Water,In-ground Storm Water Detention,In-ground Storm Water Filtration,Other
2b3813cf-a011-5404-8675-9752cc6b3117 | textbox | Capacity:
| checkpoint | Check access covers & hatches
| checkpoint | Check access ladders & statutory signage
| checkpoint | Check pipe connections & venting
| checkpoint | Check passive over-flow
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Installation Gas Service (Rough-ins) |  | Installation Gas Service (Rough-ins) | adf9afa1-64d6-4d76-86fe-cbde9e934039
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check pipework can not be holed by plaster screws
| checkpoint | Check crimp fittings & joints
| checkpoint | Check for cross connections
| checkpoint | Check alignment & levels
| checkpoint | Check materials & joining methods
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check isolation valves, pressure regulators, meter assemblies, connections,etc
| checkpoint | Check lugged elbows & in-wall valves, etc
| checkpoint | Check noggings for future fixture
| checkpoint | Check sharp edge pipe protection
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist | Installation Sewer/Stormwater Pump Station |  | Installation Sewer/Stormwater Pump Station | b979ba3b-1b71-478d-9e6f-8f86f3977c07
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check bold-down & fixing points are secure
| checkpoint | Check cable conduits
| checkpoint | Check level & alignment
| checkpoint | Check all pipework, fittings, valves & connections
| checkpoint | Check chamber vents
| checkpoint | Check control panel is installed
| checkpoint | Check power & data cables are run to the control panel
| checkpoint | Check electrical power is available
| checkpoint | Check BMS is available
| checklist | Installation Fire Service (Hydrants) |  | Installation Fire Service (Hydrants) | baa589fb-59ab-493e-adc1-6ea00b04a055
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-1221
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check hydrant is mounted securely.
| checkpoint | Check above ground hydrants height are between 750mm to 1200mm above FSL
| checkpoint | Check hydrant cabinets conform (if specified)
| checkpoint | Check in-ground hydrant heads & covers conform
| checkpoint | Check roll-groove couplings
| checkpoint | Check materials & joining methods
| checkpoint | Check pipe specification markings are visible
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check isolation valves, connections, valve covers, etc
| checkpoint | Check monitored valves & connections
| checkpoint | Check pipe labelling
| checklist | Installation Authority Primary Potable Water Meter Assembly |  | Installation Authority Primary Potable Water Meter Assembly | bb49475d-ef6c-4c06-8d5c-c535a3e0930f
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe brackets & supports are correctly positioned & bedded
| checkpoint | Check thrust blocks
| checkpoint | Check bedding & clearances
| checkpoint | Check isolation valves, filters, connections, etc
| checkpoint | Check pipework is clear of debris
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checkpoint | Check pipe labelling
| checklist | Installation Sewer/Trade Waste Stacks & Vents |  | Installation Sewer/Trade Waste Stacks & Vents | bcf595b8-1307-468f-8295-486024fce923
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Details:
a0624263-f96b-5360-8263-ff6382b08580 | textbox | Service Type:
f12b4275-c47d-5396-bcb9-e736b4fdfbaa | dropdown |  | Sewer Drainage,Trade Waste Drainage,Other
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments, levels, grades, etc
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check inspection openings
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check acoustic insulation
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checkpoint | Check vents are run to atmosphere and weather proofing is complete
| checklist | Installation Non-Potable Water Check Meter |  | Installation Non-Potable Water Check Meter | c96ed7af-fb99-4ec0-8993-d32cc3601383
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check correct meter spacing if installed in a manifold assembly
| checkpoint | Check isolation valves, pressure reduction valves, water filters, connections, etc
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checklist | Fit-off Shower & Tapware |  | Fit-off Shower & Tapware | cd552081-e60c-41d7-aaa6-713d247c27af
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check wall plates, mixers & diversion valves
| checkpoint | Check outlets, wall rails & hand showers
| checkpoint | Check special DDA accessories
| checkpoint | Check waste & trap connections
| checkpoint | Check all functions & controls for correct operation
| checkpoint | Check floor grate level & alignment
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking
| checklist | Testing Non-Potable/Rain Water Pressure Pipework |  | Testing Non-Potable/Rain Water Pressure Pipework | d2501701-3f63-4cad-8610-291d5008fde0
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing Details:
02464f84-f435-5a5c-98f3-d98f67c34f0f | textbox | Service Type:
cc10aebc-a604-56c8-8e67-89913dd7bf41 | dropdown |  | Non-Potable Water,Rain Water,Combined NPW RW,Other
c1d82cce-e392-581c-ba60-203fd550bf1c | textbox | Test Type:
0b4ca399-fe1b-50bc-8173-650ee1fa66b2 | dropdown |  | Mains Pressure,Manual Bucket Pump,Electric Bucket Pump,Other
e9733bcd-8390-5c5c-ac2a-4e47be0271f0 | textbox | Pressure:
6f388ac3-2896-5476-b640-67a159026043 | dropdown |  | 500kPa,900kPa,1200kPa,1500kPa,Other
| checkpoint | Check all valves, mixers, meters, fittings, etc in the test zone are rated for the test pressure required
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 1 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checkpoint | Authority sign-off has taken place (Provide photo of or attach PDF copy of the Authority acceptance report)
| checklist | Installation Cast-in Wastes & Vents |  | Installation Cast-in Wastes & Vents | daeaec56-1894-4347-8998-0a5a112193ce
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Details:
dd2739de-ae5f-5ff2-a10a-c8cd979f48f2 | textbox | Service Type:
8ec8ec91-6270-519d-b8d9-35b77ee3b446 | dropdown |  | Sewer Drainage,Trade Waste Drainage,Other
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments, levels, grades, etc
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check surface & floor grated outlets
| checkpoint | Check pipework & traps are clear of debris
| checkpoint | Check pipe expansion lagging
| checkpoint | Check open ends are sealed
| checklist | Fit-off Dishwasher |  | Fit-off Dishwasher | de1c715a-bcb2-4b06-aebb-f05de9bc10ce
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check isolation valves & non-return valves
| checkpoint | Check pressure reduction valve
| checkpoint | Check flexible waste & water hoses are not twisted or kinked
| checkpoint | Check flexible waste hose height under cabinet
| checkpoint | Check waste connection to trap
| checkpoint | Check all functions & controls for correct operation
| checklist | Fit-off Urinal & Cistern |  | Fit-off Urinal & Cistern | e8fb99cb-8dd6-4f0c-bcc4-89e875b57fd8
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment
| checkpoint | Check mini stops
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check button assembly
| checkpoint | Check all functions, controls & remote sensors for correct operation
| checkpoint | Check trap is clear of debris
| checkpoint | Check caulking is correct
| checklist | Commission Drainage Pump Station |  | Commission Drainage Pump Station | ec980fec-fbe3-4573-ac28-ebb2f364a6a5
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Pump Station Details:
83addede-b86a-5db5-80ca-b193db862edb | textbox | Type:
497b635d-8350-56a2-87ce-cef07a676d71 | dropdown |  | In-ground Sewer,In-ground Stormwater,Above Ground Sewer,Above Ground Stormwater,Other
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check access covers & hatches
| checkpoint | Check access ladders & statutory signage
| checkpoint | Check pipe connections & venting
| checkpoint | Check all pipework, fittings, valves & connections
| checkpoint | Check lifting rails & chains
| checkpoint | Check float tree or water level sensor is not impeded by water inflow
| checkpoint | Check water level set points
| checkpoint | Check pump motor rotation
| checkpoint | Check dry pump fault
| checkpoint | Check low water level fault
| checkpoint | Check high water level fault
| checkpoint | Check auto pump roll-over
| checkpoint | Check control panel display
| checkpoint | Check programmed set points
| checkpoint | Check BMS connection
| checkpoint | Check fault warning alarms
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist | Testing Fire Service Pressure Pipework |  | Testing Fire Service Pressure Pipework | f5cb3b6e-2fcc-412d-be85-dab0b5ccf2bf
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS-1221
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing Details:
065038f4-c364-5d59-b6e4-5860b2a58251 | textbox | Service Type:
f357082b-6aae-577b-a4fb-d5705d0b4905 | dropdown |  | Fire Hydrants Only,Fire Hose Reels Only,Fire Hydrants & Hose Reels,Other
87530c9c-172a-59e9-a80e-f81d83b326bf | textbox | Test Type:
aa0b2a19-3476-58bf-a7e9-8fe43a8c5932 | dropdown |  | Mains Pressure,Manual Bucket Pump,Electric Bucket Pump,Other
3973223b-bbc2-5934-956d-5002eb312475 | textbox | Pressure:
6f1aa623-2dfc-59e6-9822-ad273b7c1699 | dropdown |  | 500kPa,900kPa,1200kPa,1500kPa,Other
| checkpoint | Check all valves & fittings in the test zone are rated for the test pressure required
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-1221 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Testing Water Pressure Pipework |  | Testing Water Pressure Pipework | f86cc23f-acf2-44f0-9e25-85a88386b3dc
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing Details:
0dbc33b4-7bbc-5025-b4f2-6a61964816c4 | textbox | Service Type:
3340f089-292e-52bc-bdfd-cd7ee527f4ef | dropdown |  | Potable Cold Water,Potable Hot Water,Non-Potable Water,Rain Water,Combined CW HW NPW RW,Fire Service,Other
f2ad3426-153e-501c-8a47-ec6a3d185641 | textbox | Test Type:
f6db5dd5-0dd4-5cb0-8005-b58a5ad507d1 | dropdown |  | Mains Pressure,Manual Bucket Pump,Electric Bucket Pump,Other
8b897bb2-9936-5745-b4b2-d8c6df3e1d20 | textbox | Pressure:
e9b2a117-fa23-58d3-b92d-1b88e34ac8b4 | dropdown |  | 500kPa,900kPa,1200kPa,1500kPa,Other
| checkpoint | Check all valves, mixers, meters, fittings, etc in the test zone are rated for the test pressure required
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS-3500 Part 1 (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist | Installation Potable Water Check Meter |  | Installation Potable Water Check Meter | fb432d2e-b1f5-4fb6-bba8-7a77bead6003
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check correct meter spacing if installed in a manifold assembly
| checkpoint | Check isolation valves, pressure reduction valves, water filters, connections, etc
| checkpoint | Check pipe labelling
| checklist | Installation Fire Service (Mains/Risers) |  | Installation Fire Service (Mains/Risers) | fc629a68-04c3-4ef8-8e09-8a28898e6141
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-1221
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check roll-groove couplings
| checkpoint | Check crimp fittings & joints
| checkpoint | Check materials & joining methods
| checkpoint | Check pipe specification markings are visible
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check expansion joints and anchor points
| checkpoint | Check isolation valves, connections,etc
| checkpoint | Check monitored valves & connections
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing