## res
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist-flat | Commission Hot Water Generating Plant |  | Commission Hot Water Generating Plant | 2dca079c-b3e2-4754-ac09-2465054c8ad6
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Hot Water Plant Details:
e1ef533c-3093-5674-b94f-30e30f1af616 | textbox | Type:
49a47a5c-1402-5e8b-bd05-b8627cc7ee30 | dropdown |  | Bulk Gas Hot Water Plant,Bulk Gas Warm Water Plant,Elec Commercial Heat Pump,Elec Domestic Heat Pump,Gas Instantaneous Domestic,Elec Domestic Storage,Gas Domestic Storage,Other
3b98ff17-ccf1-5272-8676-94e11e6aafba | textbox | Solar Preheat:
de16c7ee-2132-5f2b-bb1b-595b5cd31bc6 | dropdown |  | Yes,No
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check isolation valves are fully open & non-return valves flow direction
| checkpoint | Check water filters are clean
| checkpoint | Check gas supply
| checkpoint | Check circulating pumps
| checkpoint | Check flue system & operation
| checkpoint | Check system auto start
| checkpoint | Check flow & return temperatures
| checkpoint | Check control panel display
| checkpoint | Check programmed set points
| checkpoint | Check BMS connection
| checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
| checklist-flat | Installation Gas Service (Mains/Risers) |  | Installation Gas Service (Mains/Risers) | 4699707d-ac04-4cbf-9008-d7292e483e01
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check crimp fittings & joints
| checkpoint | Check for cross connections
| checkpoint | Check alignments & levels
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check isolation valves, pressure regulators, meter assemblies, connections,etc
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing
| checklist-flat | Installation Hot Water Plant/Unit |  | Installation Hot Water Plant/Unit | 52d49ede-27f7-4b11-bca0-62eab6067977
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4, &/or AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check level & alignment
| checkpoint | Check all pipework, isolation valves, non-return valves, pressure reduction valves, water filters & connections, etc
| checkpoint | Check bold-down & fixing points are secure
| checkpoint | Check cable conduits
| checkpoint | Check thermal pipe lagging
| checkpoint | Check PTR valve, safe tray & drainage
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check solar panels & mounting brackets
| checkpoint | Check solar connecting pipework & fittings
| checkpoint | Check circulation pump installation
| checkpoint | Check installation of flue system if applicable
| checkpoint | Check control panel is installed
| checkpoint | Check power & data cables are run to the control panel
| checkpoint | Check electrical power is available
| checkpoint | Check BMS connection is available
| checklist-flat | Commission Fixture Group |  | Commission Fixture Group | 73854fa9-002e-4ab1-a4e3-2662d90b25ee
| checkpoint | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Thoroughly check all pipework, fittings, connections, etc for damage or water leaks
| checkpoint | Check for any damage or missing components
| checkpoint | Check level & alignment of all fixtures & tapware
| checkpoint | Check all fixtures, tapware & components are securely fixed
| checkpoint | Check all mini-stops and valves are fully open
| checkpoint | Check all pressure reduction & non-return valves
| checkpoint | Check all flexible connections are not twisted or kinked
| checkpoint | Check for water for cross connections
| checkpoint | Check fixture wastes & connections
| checkpoint | Check dishwasher drain hose is looped hard-up under bench-top
| checkpoint | Check pipework & all traps are clear of debris
| checkpoint | Check AAV is installed hard-up under bench-top
| checkpoint | Check future connection water valves are securely capped (fridge/washing machine stops)
| checkpoint | Check all hot water units are functioning correctly
| checkpoint | Check solar collectors are fitted & securely fixed
| checkpoint | Check solar circulation pump is functioning correctly
| checkpoint | Check TV do not exceed 50°C
| checkpoint | Check TMV do not exceed 45°C
| checkpoint | Check dishwasher function through short cycle
| checkpoint | Check gas valves & regulators
| checkpoint | Check gas flame stop device
| checkpoint | Check all gas burner functions
| checkpoint | Check balcony hose tap is securely fixed
| checkpoint | Check balcony floor grate is clear
| checkpoint | Check all downpipes & overflows are fitted correctly
| checkpoint | Check all vents are finished & weather proofed
| checkpoint | Check all fixtures & tapware function correctly
| checkpoint | Confirm area has been left clean
| checklist-flat | Fit-off Gas Appliance |  | Fit-off Gas Appliance | 8b56bab1-c226-4bda-b103-5b702129d3b1
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check fixing points are secure
| checkpoint | Check level & alignment is correct
| checkpoint | Check surrounding wall material is fire rated
| checkpoint | Check distance from cook-top to range hood complies with manufacturer specification
| checkpoint | Check surrounding walls to closest burner distance complies with manufacturer specification
| checkpoint | Check flexible connections are not twisted or kinked
| checkpoint | Check gas isolation valve
| checkpoint | Check gas pressure regulator
| checkpoint | Check flame failure device
| checkpoint | Check all functions & controls for correct operation
| checklist-flat | Testing Gas Pipework |  | Testing Gas Pipework | 975e5a06-47dd-438d-8a89-8f238a77b5d5
| checkpoint | IMPORTANT USER NOTES: Only FAIL a checkpoint after reporting the defect to Site Management for approval. If not, mark this checkpoint as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022) & ESV Regulations
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | Testing Details:
0cd9290f-7e23-5291-bf96-dc8358d2b6e4 | textbox | Type:
879f9d92-26a0-55e4-a9f1-3d6bbab48fb6 | dropdown |  | Low Pressure,High Pressure
5bb0fbee-909c-5864-840a-122e2f3b5ad0 | textbox | Pressure:
a5c7604e-e087-5454-b879-93ead5b95b37 | dropdown |  | 7kPa,10kPa,20kPa,30kPa,40kPa,50kPa,1.5 x MWP,Other
| checkpoint | Testing kit & equipment have current certification
| checkpoint | Apply test as per latest revision of AS/NZS 5601.1 (2022) & ESV Regulations (Note: Start & Finish testing photos to be taken only within this Checkpoint)
| checklist-flat | Installation Gas Service (In-ground) |  | Installation Gas Service (In-ground) | 9edbe792-2bef-4d6d-b0c2-fe4dc8a3948f
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check materials & joining methods
| checkpoint | Check alignments & levels
| checkpoint | Check bedding & clearances
| checkpoint | Check isolation valves, connections, etc
| checkpoint | Check pipework is clear of debris
| checkpoint | Check open ends are sealed
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe trench marking tape
| checkpoint | Check trench backfill & compaction
| checklist-flat | Installation Gas Service (Rough-ins) |  | Installation Gas Service (Rough-ins) | adf9afa1-64d6-4d76-86fe-cbde9e934039
| checkpoint | IMPORTANT USER NOTES: If you think this task should be a variation or is additional works, mark this checkpoint as 'FAIL' and add comment or photo. If not, mark as 'N/A'. You must still action all the following checkpoints as either PASS, FAIL or N/A. Only FAIL a checkpoint after reporting the defect to Site Management for approval.
| checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
| checkpoint | Installation complies with current drawings & specifications
| checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
| checkpoint | This checkpoint is for all photo recording. When finished taking your photos, mark this checkpoint as PASS
| checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
| checkpoint | Check pipework can not be holed by plaster screws
| checkpoint | Check crimp fittings & joints
| checkpoint | Check for cross connections
| checkpoint | Check alignment & levels
| checkpoint | Check materials & joining methods
| checkpoint | Check pipe clips, hangers & fixings for correct size, spacing & pipe separation
| checkpoint | Check isolation valves, pressure regulators, meter assemblies, connections,etc
| checkpoint | Check lugged elbows & in-wall valves, etc
| checkpoint | Check noggings for future fixture
| checkpoint | Check sharp edge pipe protection
| checkpoint | Check pipe colour coding
| checkpoint | Check pipe labelling
| checkpoint | Check floor/wall penetration fire proofing