## res
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | COM Commission Hot Water Unit |  | COM Commission Hot Water Unit | 06f7685e-41b1-4cf1-8bce-98b68864d2c0
| section | Details:
| checkpoint | Commission Hot Water Unit checked off as below:
14b2d6be-5080-51a1-874d-ee4483f09cc1 | dropdown | Type: | Domestic Electric Storage,Domestic Gas Storage,Domestic Heat Pump,Domestic Gas Instantaneous
5fb40405-d6a3-5f6b-b08d-bdefb0a41ebe | dropdown | Solar Preheat: | Yes,No
22c8f840-565e-55bd-b378-ede429164591 | dropdown | Location: | Indoors,Outdoors,Roof Mounted
7891720a-a648-5e85-9cdd-e004752f7c14 | button | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS 5601.1 (2022) | YES,NO,N/A
7e3855af-0d25-5c91-8930-8e4e8955e0bf | button | Installation complies with current drawings & specifications | YES,NO,N/A
1d60e3e6-e58d-5073-8dab-12294e8968e2 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
7a530a63-6fd3-5e72-9419-3b8da72c7bef | button | Check regulatory clearances & distances from building openings & air intakes (Gas HW Plants) | YES,NO,N/A
30bd4c64-de97-5119-ab6c-6e8d07c9ba4e | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
36bff062-1bba-5957-8861-3f784f561a36 | button | Check all fixing/hold down points | YES,NO,N/A
db992fe6-1c6d-5007-80cf-0fe68746f4c8 | button | Check isolation valves are fully open & non-return valves flow direction | YES,NO,N/A
5ec71b5c-bf2b-5b97-bad4-89ce79599d9b | button | Check water filters are clean | YES,NO,N/A
5099274f-a2de-547b-88eb-f97585ec2187 | button | Check gas valves & connections (if applicable) | YES,NO,N/A
00f9d503-0ef9-5d10-b27d-ac43430a1648 | button | Check flue system & operation (if applicable) | YES,NO,N/A
99a8ad43-47e2-5a1f-a3dc-a594f7a03377 | button | Check hot water delivery temperature | YES,NO,N/A
a51d7a9f-6924-50a1-8dbf-1e763a67c86d | button | Check solar panels & mounting brackets | YES,NO,N/A
2c31fb59-b341-56c9-8434-b848978d4511 | button | Check solar connecting pipework & fittings | YES,NO,N/A
c7da5e89-3295-5ac8-be56-94a3328d07b8 | button | Check solar circulation pump | YES,NO,N/A
| checklist | COM Commission Gas Appliance |  | COM Commission Gas Appliance | 17d0ab40-08fd-4188-b8b7-1ffd7a5d329b
| section | Details:
| checkpoint | Commission Gas Appliance checked off as below:
02814ae3-1e8f-5bea-be54-c1af03fd7f48 | textbox | Location:
06f06ad3-5cbc-5422-820b-36a2fced76ad | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) | YES,NO,N/A
f0b9eab8-6378-50d5-9663-d794a7a68f46 | button | Installation complies with current drawings & specifications | YES,NO,N/A
27b2507a-186a-5f15-80a8-cba358e35bf8 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
c2c2de6c-32f3-5908-8aae-9a5e1571d1f5 | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
d0325010-5b36-54e6-a7b1-6c2ee0498b20 | button | Check fixing points are secure | YES,NO,N/A
2ac3b28f-1508-554d-8141-57c1aa28b6c1 | button | Check level & alignment is correct | YES,NO,N/A
03d2590b-6402-50b7-88ae-88041505ca4d | button | Check surrounding wall material is fire rated | YES,NO,N/A
6d416cf7-25bc-5f1e-9984-b679e7e401ac | button | Check distance from cook-top to range hood complies with manufacturer specification | YES,NO,N/A
b0f2c03b-6f4a-5a61-bab7-b3731d14c608 | button | Check surrounding walls to closest burner distance complies with manufacturer specification | YES,NO,N/A
99954bdd-603f-51e5-965e-ea2fb24c52bc | button | Check gas service has been purged | YES,NO,N/A
f20fb233-b0b2-5cd0-8650-bc0181883ca3 | button | Check flame ignition device | YES,NO,N/A
73c40e0f-a8df-5a33-a371-7bdd5d02b5e7 | button | Check all burners for blockages, etc | YES,NO,N/A
225b7d02-083a-5367-9824-5ca2a31f1088 | button | Check all burners for correct flame operation, height, colour, etc | YES,NO,N/A
6f962439-05cd-5cb8-bc74-3258df380e06 | button | Check flame failure device | YES,NO,N/A
a7a7d58a-6cb3-5ed8-a8b1-f7b6e12b474f | button | Check all functions & controls for correct operation | YES,NO,N/A
| checklist | FO Fit-off Hot Water Unit |  | FO Fit-off Hot Water Unit | a626fa3c-c0f5-40c1-8d7f-c670d2296e3b
| section | Details:
| checkpoint | Fit-off Hot Water Unit checked off as below:
e11d3334-1278-5097-b7be-2d949cdee714 | button | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4, &/or AS/NZS 5601.1 (2022) | YES,NO,N/A
ca9caf46-763a-5e00-9e42-1163e21aea48 | button | Installation complies with current drawings & specifications | YES,NO,N/A
02987142-373a-571a-a1d4-2cc2042b6a55 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
48124776-5b89-5a16-a8fb-318c8d404853 | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
55a7961c-76fa-55fb-905a-3714dbdf641c | button | Check materials & joining methods | YES,NO,N/A
d3a85d13-6fc7-5b4b-a80b-059f38b8d65b | button | Check level & alignment | YES,NO,N/A
9f82b576-a8ee-5571-b8cf-75957aaca083 | button | Check all pipework, isolation valves, non-return valves, pressure reduction valves, water filters & connections, etc | YES,NO,N/A
666eaa0e-a797-5ac5-bdf6-f3a1c7e59e3d | button | Check bold-down & fixing points are secure | YES,NO,N/A
ba14cd8a-e133-50ad-b987-ce9efa1b06e5 | button | Check thermal pipe lagging | YES,NO,N/A
56f7cfb4-574b-5eb0-8b21-fc02c30542c5 | button | Check PTR valve, safe tray & drainage | YES,NO,N/A
3e6f136a-9187-5171-a88d-30c2b13eb0d8 | button | Check flexible connections are not twisted or kinked | YES,NO,N/A
9f01df94-be67-5d90-b5ab-39654d467c2d | button | Check solar panels & mounting brackets | YES,NO,N/A
0290a059-d423-5cfd-9f7d-fe7ae8cba839 | button | Check solar connecting pipework & fittings | YES,NO,N/A
fb176256-fd72-533b-9e4b-cf47358e9591 | button | Check solar circulation pump | YES,NO,N/A
307c734c-69be-5d03-8ab7-9e58763fcdce | button | Check gas valves, connections, fittings, etc (if applicable) | YES,NO,N/A
96e34ab5-bf6f-53ac-85c0-79377d7b0b54 | button | Check flue system (if applicable) | YES,NO,N/A
| checklist | COM Commissioning Final Handover |  | COM Commissioning Final Handover | cdbadb4e-e21c-4699-a766-cfa7d91b190c
| section | Details:
| checkpoint | Commissioning Final Handover checked off as below:
6b2a7bbb-7d84-57d6-b84d-1d3306762399 | textbox | Location/Lot Number:
fa2ea374-c292-566d-96a0-07a7d4b2a555 | button | Installation complies with latest revision of AS/NZS-3500 Parts 1 - 4 &/or AS/NZS 5601.1 (2022) | YES,NO,N/A
4ce5ef5e-31b3-5c6a-959f-78446fa44544 | button | Installation complies with current drawings & specifications | YES,NO,N/A
4f3af7d3-b1d8-5464-bcf6-8da0e9e4eba6 | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
565eb3e2-2821-5942-8ec4-8593dd3d9c42 | button | Check for any damage or missing components | YES,NO,N/A
2421ba6c-2fe0-5532-9964-fa143d350c94 | button | Check level & alignment of all fixtures & tapware | YES,NO,N/A
7bb1f1fb-031a-574d-b9ba-c30eb53847c3 | button | Check all fixtures, tapware & components are securely fixed | YES,NO,N/A
6bc67652-3a23-53f9-95ef-34259cf972e7 | button | Check all mini-stops and valves are fully open | YES,NO,N/A
33782244-469e-52d9-b64e-ee1570440a64 | button | Check all pressure reduction & non-return valves | YES,NO,N/A
50d79e60-6743-5041-9ced-eb0980d4c844 | button | Check all flexible connections are not twisted or kinked | YES,NO,N/A
36ccb04c-2953-5cbc-b5e8-6790e7615a46 | button | Check for water for cross connections | YES,NO,N/A
c8ee5908-72b7-5bb1-b6f7-90c2ec12c128 | button | Check fixture wastes & connections | YES,NO,N/A
ddb23791-441c-5a46-8296-660d1bca3ed8 | button | Check dishwasher drain hose is looped hard-up under bench-top | YES,NO,N/A
d5b8c925-d188-5e77-b2fc-fd0a9788ad4a | button | Check pipework & all traps are clear of debris | YES,NO,N/A
db66b81d-ba04-553a-a54a-7a4ce78b9bf9 | button | Check AAV is installed hard-up under bench-top | YES,NO,N/A
e402f184-8f2a-5240-94cd-39ddea07aeec | button | Check future connection water valves are securely capped (fridge/washing machine stops) | YES,NO,N/A
c831bd73-317b-5ddd-b5d4-13ab3e5fb90d | button | Check hot water unit is functioning correctly | YES,NO,N/A
cb865f44-e5ee-563e-93b8-88dc917c8aa7 | button | Check solar collectors are fitted & securely fixed | YES,NO,N/A
d775fcd6-e0fc-5c12-bc4c-93caa82d82fa | button | Check solar circulation pump is functioning correctly | YES,NO,N/A
6b3628ea-1f6a-504e-9f63-0676efe76d58 | button | Check hot water delivery temperature | YES,NO,N/A
878425d7-498f-5646-8c9d-97568a1cadf9 | button | Check dishwasher function through short cycle | YES,NO,N/A
25a96a4e-c6e7-567d-bbd5-6d17ade37a24 | button | Check gas valves & regulators | YES,NO,N/A
8a6cbfc7-d432-5788-a2d3-61e175edcdec | button | Check gas flame stop device | YES,NO,N/A
70d046b3-9d27-5373-9f71-563f5bc77097 | button | Check all gas burner functions | YES,NO,N/A
e2fa7dca-471a-56f0-9979-e42eb36559e8 | button | Check balcony hose tap is securely fixed | YES,NO,N/A
da4f81b1-9185-576d-be98-4af4cff0fc1a | button | Check balcony floor grate is clear | YES,NO,N/A
616a460d-ea21-5151-934e-c0ddcc23e38f | button | Check all downpipes & overflows are fitted correctly | YES,NO,N/A
947bae2a-29c8-5243-9aba-68c76eb8178c | button | Check all vents are finished & weather proofed | YES,NO,N/A
8a7a81d6-abd5-5b7d-b6b5-1f4a6ea3ccf6 | button | Check all fixtures & tapware function correctly | YES,NO,N/A
cf5a741b-1893-525f-8408-b644b984182c | button | Check receipt of all Authority sign-off & acceptance documentation | YES,NO,N/A
f963b8a2-9758-5831-bab0-f8b4678f95ac | button | Check receipt of all manufacturers warranty documentation & owners manuals | YES,NO,N/A
3ed03449-f069-591d-a707-be6bd8aed27b | button | Confirm area has been left clean | YES,NO,N/A
| checklist | TST Test Gas Services Pipework |  | TST Test Gas Services Pipework | d84d30f2-c2ee-49dc-a4b7-4fb904996d2b
| section | Details:
| checkpoint | Test Gas Services Pipework checked off as below:
9014dfc1-70bb-585c-87ab-b5aa6fb88d3a | dropdown | Test Pressure: | 7kPa,1.5 x MWP
e14f4c3e-5e88-520e-a2e6-bb1da3dc3893 | textbox | Location/Lot Number:
d42dedc7-b370-5760-b7f3-9395f53dad8b | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) & ESV Regulations | YES,NO,N/A
0dac14dc-6502-534b-a6e1-77cfd5eb1e18 | button | Installation complies with current drawings & specifications | YES,NO,N/A
0165bdfc-2f60-59c9-9645-f4f1035498ad | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
5c160ad2-c2b5-5b2a-90d3-e6fb1b01b90f | button | Testing kit & equipment have current certification | YES,NO,N/A
56cf3593-dc5a-53c1-b636-42b0f5861455 | button | Apply test as per latest revision of AS/NZS 5601.1 (2022) & ESV Regulations (Note: Start & Finish testing photos to be taken only within this Checkpoint) | YES,NO,N/A
| checklist | FO Fit-off Gas Appliance |  | FO Fit-off Gas Appliance | d88c359a-8bb3-4b5d-a45f-af67f485ea8c
| section | Details:
| checkpoint | Fit-off Gas Appliance checked off as below:
28bce096-3a4b-5326-b56e-f0e3663c4de3 | button | Installation complies with latest revision of AS/NZS 5601.1 (2022) | YES,NO,N/A
d6dabf0b-1c8c-59c7-8dd5-b80653e9d65f | button | Installation complies with current drawings & specifications | YES,NO,N/A
6ebb3fde-b73e-5548-9383-532538d502ed | button | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions | YES,NO,N/A
12f577e2-d303-5a61-b006-870e0f575c6f | button | Check all, pipework, fittings, connections, etc for damage or leaks | YES,NO,N/A
29c3e125-6bb1-54cb-b34b-79fe9d04edcb | button | Check fixing points are secure | YES,NO,N/A
e02d21a9-2cd4-50a7-afb8-f6ecc5d81e94 | button | Check level & alignment is correct | YES,NO,N/A
8ac51942-dfb5-529a-93d0-4f712548b45f | button | Check surrounding wall material is fire rated | YES,NO,N/A
1d02d20e-c1c4-5e72-99cd-1a7e229c6eef | button | Check distance from cook-top to range hood complies with manufacturer specification | YES,NO,N/A
0fd0e186-bb8e-51b1-a53b-685954e649b8 | button | Check surrounding walls to closest burner distance complies with manufacturer specification | YES,NO,N/A
b68d19ce-9847-53bf-be06-a48bfed38641 | button | Check flexible connections are not twisted or kinked | YES,NO,N/A
5160393f-0484-5535-aa00-2ea41a2d990a | button | Check gas isolation valve & cover plate | YES,NO,N/A
5bbbd8f8-4a83-57c8-a29f-15ed2f655595 | button | Check gas pressure regulator | YES,NO,N/A
60334c11-e206-5218-9ede-c6a42efbcb00 | button | Check flame failure device | YES,NO,N/A
fb70851a-6d25-54ec-8ee2-0fa26693167d | button | Check all functions & controls for correct operation | YES,NO,N/A