## Table 1
Inspection & Test Plan Project no.: Project name: Inspection Legend: H = Hold point; S = Surveillance; W = Witness Client: Water Authority Responsibility Legend: PM = Project Manager; SS = Site Supervisor; C = Client Rep; I = Inspector
No. | Inspection Activity | Specification / Drawing Reference | Inspection Procedure and Acceptance Criteria | Verification Document | Aquatec |  |  | Skerman Civil |  |  | Urban Utilities |  |  | Records / Comments
[5 empty] | Insp. | Resp. | Sign and date | Insp. | Resp. | Sign and date | Insp. | Resp. | Sign and date
1.0 SITE PRELIMINARIES
1.1 | Management Plans |  | □ Management Plans Submitted and approved |  | H | PM |  | H | C |  | H | I
1.2 | Permit to Work |  | □ All required permits received |  | H | PM |  | H | C |  | H | I
1.3 | Drawings | Aquatec Civil/Mech Drawings | □ IFC Drawings confirmed latest revision and approved | IFC Drawings | H | PM |  | H | C |  | H | I
1.4 | Backfill Design Approval | Aquatec Civil/Mech Drawings | □ Foundation and Backfill design has been reviewed and modified where necessary with letter of endorsement from RPEQ Geotech (Must be site- specific) | RPEQ Letter of Endorsement | H | PM |  | H | C
1.5 | Backfill Materials Approval | Aquatec Civil/Mech Drawings | □ All backfill material certificates submitted and approved for use by Geotechnical Engineer | Material Certificates | H | PM |  | W | C
2 | PRECAST CONCRETE INSTALLATION
2.1 | Excavation set-out | Aquatec Civil/Mech Drawings | □ Setout points established and offset for recovery |  | W | SS |  | W | C
2.2 | Excavation to Base R.L | Aquatec Civil/Mech Drawings | □ Shoring and benching completed as required □ Where over-excavation occurs, excavation shall be filled with suitable material to satisfaction of geotechnical engineer |  | W | SS |  | H | C |  | W | I
2.3 | Testing of Base | Aquatec Civil/Mech Drawings | □ 2 x DCP tests completed on excavation floor and bearing capacity of >100kPa confirmed □ If excavation base material deemed unsuitable, unsuitable foundation to be replaced with suitable material with approval. | DCP Report | H | SS |  | H | C |  | W | I
2.4 | Sub-Base Preparation | Aquatec Civil/Mech Drawings | □ Approved Sub-Base material placed and compacted □ Sump and pump set up to keep excavation dry (if required) □ Pump Station Base R.L, centre and orientation set out and confirmed |  | W | SS |  | W | C |  | W | I
2.5 | Testing of Sub-Base | Aquatec Civil/Mech Drawings | □ Sub-base confirmed at 98% compaction | Compaction Test Report | H | SS |  | H | C |  | W | I
2.6 | Precast Items Check | Aquatec Coring Drawings | □ Precast items checked for damage □ Precast items checked against drawings for correct dimensions, cast-ins, coatings and penetrations |  | S | SS |  | W | CS |  | W | I
2.7 | Base and Increment Placement | Craning and Excavation Plan Aquatec Civil/Mech Drawings | □ Precast items lifted into chamber as per craning and excavation plan □ Precast items jointed as per drawings □ Orientation of inlet stub and penetrations as per drawings |  | S | SS |  | W | CS |  | W | I
2.8 | Cover Slab Installation | Craning and Excavation Plan Aquatec Civil/Mech Drawings | □ Cover Slab lifted onto pump station as per craning and excavation plan □ Cover Slab orientation and alignment correct as per drawings □ Cover Slab sealed to pump station as per drawings |  | S | SS |  | W | CS
2.9 | Placement of Ballast Concrete | Aquatec Civil/Mech Drawings | □ 25MPa Concrete Used □ Correct Volume Used □ Sufficient Vibration | Concrete Dockets | S | SS |  | W | CS
2.1 | Placement and Compaction of Backfill | Aquatec Civil/Mech Drawings | □ Backfill placed and compacted in 200mm layers to 95% as per drawings □ Compaction test taken every 5th layer (1m) | Compaction Test Reports | S | SS |  | W | CS
2.11 | As Built Pickup | Aquatec Civil/Mech Drawings | □ Survey pickup completed □ All as-constructed data recorded. | Survey Pickups Redlined Drawings | S | SS |  | W | C
3 | PUMP STATION MECH FITOUT
3.1 | Materials check | Aquatec Civil/Mech Drawings | □ Pumps, Pipework, valves, fittings, fasteners, brackets, etc. as per drawings and specifications □ Materials checked for damage | Delivery Dockets Material Certificates | H | SS |  | W | C
3.2 | Pump and Pipeline set out | Aquatec Pipework Layout Drawings | □ Layouts and IL's are consistent with drawings |  | S | SS |  | W | C
3.3 | Pump Pedestal Installation | Aquatec Civil/Mech Drawings | □ Anchors installed to correct depth and as per manufacturers recommendation □ Pumps level □ Pedestal anchors torqued □ Guide rails installed and plumb |  | S | SS |  | W | C |  | W | I
3.4 | Pipe and Pipe Support Installation | Aquatec Civil/Mech Drawings | □ Pipe and fittings installed as per project drawings □ Pipe supports erected as per drawings with neoprene gaskets between metal and PE liner □ Fasteners torqued correctly and marked □ Dissimilar metals isolated □ Pipework flushed, drained and dried as required □ HDPE Vactor pipe vacuum tested to confirm no leaks □ PE Welding spark testing |  | S | SS |  | W | C
3.5 | Valve Installation | Aquatec Civil/Mech Drawings | □ Valves installed as per drawings □ Handles fitted and secure □ Valve operation checked □ Valve orientation correct □ Fasteners torqued correctly and marked |  | S | SS |  | W | C
3.6 | Ladders and misc. installation | Aquatec Civil/Mech Drawings | □ Anchors installed to correct depth and as per manufacturers recommendation □ Ladders and misc. steelwork plumb and level □ Bracket anchors torqued with neoprene gaskets between metal and PE liner |  | S | SS |  | W | C
3.7 | Grouting | Aquatec Civil/Mech Drawings | □ Confirm grout product has not passed expiry date □ Concrete surfaces scrabbled as required □ All penetrations and pipe supports grouted as per manufactures specification |  | S | SS |  | W | C
3.8 | Thrust Blocks | Aquatec Civil/Mech Drawings | □ Reinforcing placed as per drawings □ 2 x layers hydrotite used □ Walls scabbled □ Adequate Vibration used | Concrete Dockets | H | SS |  | H | C |  | H | I
3.9 | Trench Fill and Compaction | Aquatec Civil/Mech Drawings | □ Marker tape installed as required □ Trench backfilled with imported suitable trench fill |  | S | SS |  | W | C
3.1 | As Built Pickup | Aquatec Civil/Mech Drawings | □ Final inspection of mechanical works completed □ Survey pickup completed □ All as-constructed data recorded. | Survey Pickups Redlined Drawings | H | SS |  | H | C |  | H | I
4 | DRAINS, CONDUITS & VENTS
4.1 | Materials check | Aquatec Civil/Mech Drawings | □ Pipework, fittings and adhesives as per drawings |  | H | SS |  | W | C
4.2 | Pipeline set out | Aquatec Civil/Mech Drawings | □ Layouts and IL's are consistent with drawings |  | W | SS |  | W | C
4.3 | Pipework Connections | Aquatec Civil/Mech Drawings | □ Pipework installed as per project drawings □ Invert, grade and alignment checked □ Connections completed with no excessive loading exerted onto cast-ins. |  | S | SS |  | W | C
4.4 | Trench Fill and Compaction | Aquatec Civil/Mech Drawings | □ Marker tape installed as required □ Trench backfilled with imported suitable trench fill |  | W | SS |  | W | C
4.5 | As Built Pickup | Aquatec Civil/Mech Drawings | □ Survey pickup completed □ All as-constructed data recorded. | Survey Pickups Redlined Drawings | S | SS |  | W | C
5 | PUMP STATION CONCRETE SLABS
5.1 | Slab set-out | Aquatec Civil/Mech Drawings | □ Setout points established and offset for recovery |  |  |  |  | W | C
5.2 | Excavation for slab | Aquatec Civil/Mech Drawings | □ Bearing Capacity confirmed as per drawings □ If excavation base material deemed unsuitable, unsuitable foundation to be replaced with suitable material with approval. □ Where over-excavation occurs, excavation shall be filled with material to satisfaction of geotechnical engineer |  |  |  |  | W | C
5.3 | Formwork | Aquatec Civil/Mech Drawings | □ Formwork installed as per drawings □ Form release applied as required |  |  |  |  | W | C
5.4 | Reinforcement | Consultant Drawings MW Specifications | □ Correct reinforcing sizes and spacing □ Minimum cover as per drawing □ Appropriate lap / cog lengths □ Cover to conduits as per drawings |  |  |  |  | W | C
5.6 | Pre-Pour | Consultant Drawings MW Specifications | □ Relevant persons notified of pour □ Inspection and certification completed (as applicable) □ all debris removed from formwork □ Correct bar chairs and qty in place □ Conduits positioned correctly |  | W | SS |  | H | C |  | H | I
5.7 | Concrete Pours | Consultant Drawings MW Specifications | □ Concrete docket checked to confirm mix is as per drawings □ Free dropping not permitted □ Adequate vibration used □ Finish as per specification and drawings | Pour record /Docket |  |  |  | S | C
5.8 | Post-Pour | MW Specifications AS 3600 | □ Compressive strength adequate prior to stripping □ Curing agent applied immediately after stripping |  |  |  |  | W | C
5.9 | As Built Pickup | MW Specifications | □ Survey pickup completed as required □ All as-constructed data recorded. | Survey Pickups Redlined Drawings | W | SS |  | W | C
6 | ELECTRICAL INSTALLATION
6.1 | Switchboard check | Electrical Drawings | □ Switchboard and instruments as per drawings and specifications □ Materials checked for damage | Delivery Dockets Material Certificates | H | PM |  | H | C |  | H | I
6.2 | Switchboard check | Electrical Drawings | □ FAT test results received | FAT Results | H | PM |  | H | C |  | H | I
6.3 | Switchboard Installation | Aquatec Civil/Mech Drawings AS 3000 | □ Conduits are installed as per drawings □ Communications GeoSCADA □ Mastic sealant used on underside of switchboard □ Switchboard fixed down using correct dyna bolts |  | S | SS |  | S | C
6.4 | Switchboard Installation | Aquatec Civil/Mech Drawings AS 3000 | □ Pre SAT |  | S | SS |  | S | C |  | H | I
6.5 | Switchboard Installation | Aquatec Civil/Mech Drawings AS 3000 | □ SAT |  | S | SS |  | S | C |  | H | I
6.6 | Earthing | Electrical Drawings AS 3000 | □ Main earth stake correctly installed and labelled □ Earthing cables terminated safely and correctly |  | S | SS |  | S | C
6.7 | Consumer Mains | Electrical Drawings AS 3000 | □ Conduits meet AS 3000 requirements and are free of obstructions □ Conduit penetration into POS is sealed and at correct depth □ Consumer mains installed to conduits and labelled as requried □ Cable testing and terminations completed □ Sealing of conduits completed |  | S | SS |  | S | C
6.8 | Instrumentation and Control | Electrical Drawings AS 3000 | □ Flowmeter installed, labelled and terminated as per drawings □ Level control instrumentation installed, terminated and labelled as per drawings □ Pump controllers terminated and labelled as per drawings □ Sealing of conduits completed |  | S | SS |  | S | C
6.9 | Lighting and power | Aquatec Drawings Electrical Drawings AS 3000 | □ Lighting setout as per drawings □ Light & Power components are as per drawings |  | S | SS |  | S | C
7 | As Built Pickup |  | □ All as-constructed data recorded. | Redlined Drawings | S | SS |  | W | C
8 | CLOSEOUT
8.1 | Non Conformances |  | □ Non-conformances closed out |  | H | PM |  | H | C |  | H | I
8.2 | Hydrostatic Testing | AS3735 | □ AQT Test Record Documentation |  | H | PM |  | H | C |  | H | I
8.3 | Final Site Inspection | Project Specifications and Drawings | □ Site Clean and Clear of all Construction Waste and Debris disposed of legally and in accordance with legislation □ 100% Visual Inspection of install by PM, Client and MW □ Installation checked against drawings to confirm all works are as per design □ Site Reinstated to a standard equal to or better than existing in accordance with Project specification |  | H | PM |  | H | C |  | H | I
Project Completed Date…..................
Signed By Aquatec Representative Signed By Civil Contractor Representative ………………………………………………...… Date….................. ………………………………………………...…………… Date….................. Signed By Water Authority Representative ………………………………………………...……Date…..................