## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0375-ITP-025 Minor Concrete Structures - Rev.1 | itp |  |  |  |  | INF-HSEQ CC0375-ITP-025 Minor Concrete Structures - Rev.1
section | 1.0 Preliminaries
checkpoint | 1.1 - Documentation
label | Ref docs - Issued drawings / Site copy drawings
label | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 1.2 - Lot Traceability
label | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | Acceptance criteria - Prepare a lot map for traceability of the work area
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Lot map
checkpoint | 1.3 - Set out
label | Ref docs - Drawings
label | Acceptance criteria - Setout structure to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
section | 2.0 Formworks and Rebar Reinforcements
checkpoint | 2.1 - Blinding (if applicable)
label | Ref docs - Drawings
label | Acceptance criteria - Blinding (15MPa) for Reinforced Concrete Bases to be a 50mm thick mass concrete layer.
label | ○ Unreinforced bases can be poured directly on the earth
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 2.2 - Formwork
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3] Drawings
label | Acceptance criteria - Formwork installed as per drawings and adequately supported.
label | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
label | ○ Before Placing Concrete
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection
checkpoint | 2.3 - Steel reinforcement
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5] Drawings
label | Acceptance criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
label | ○ Concrete pre-pour inspection complete.
label | ○ Before Placing Concrete
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Pre-pour inspection
section | 3.0 Concrete placement
checkpoint | 3.1 - Concrete supply and placement
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
label | Acceptance criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
label | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
label | – – – – – – – – – – – – – – – –
label | Concrete temperature at time of discharge (°C) ¦¦ Maximum elapsed time (hours)
label | – – – – – – – – – – – – – – – –
label | 10 - 24 ¦¦ 2.00
label | 24 - 27 ¦¦ 1.50
label | 27 - 30 ¦¦ 1.00
label | 30 - 32 ¦¦ 0.75
label | – – – – – – – – – – – – – – – –
label | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
label | ○ Design slump shall not exceed 75mm unless shown otherwise on the drawings.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Delivery dockets
checkpoint | 3.2 - Concrete sampling
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
label | Acceptance criteria - The nominal rate of sampling shall be taken:
label | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
label | (b) Slump: One per batch of concrete
label | ○ Slump within tolerances specified in AS 1379
label | – – – – – – – – – – – – – – – –
label | Specified Slump (mm) ¦¦ Tolerance (mm)
label | – – – – – – – – – – – – – – – –
label | <60 ¦¦ ± 10
label | ≥60 ≤80 ¦¦ ± 15
label | >80 ≤110 ¦¦ ± 20
label | >110 ≤150 ¦¦ ± 30
label | >150 ¦¦ ± 40
label | – – – – – – – – – – – – – – – –
label | ○ Testing to be in a NATA accredited test facility
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Concrete pour record
checkpoint | 3.3 - Curing
label | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
label | Acceptance criteria - From completion of finishing; cure continuously with either curing compound, wet curing or form retention until 15MPa is achieved unless directed otherwise by the superintendent
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 3.4 - Concrete testing
label | Ref docs - Spec. 0002 [Cl 8.2]
label | Acceptance criteria - Certificates received, reviewed, and conforming to requirements for each pour. Average compressive strength at 28 days meets minimum design requirements
button | Acceptance | Yes,No,N/A
label | Key - R
label | HPP CON Key - R
label | HPP QA Key - R
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
section | 4.0 Conformance check
checkpoint | 4.1 - Survey Report
label | Ref docs - Spec. 0161 Quality [Cl 3.13]
label | Acceptance criteria - An as-built survey completed to ensure all structures are within construction tolerances.
label | ○ Plan: +/- 30mm
label | ○ Level: +/ 10mm
button | Acceptance | Yes,No,N/A
label | Key - R
label | HPP CON Key - R
label | HPP QA Key - R
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Survey report
checkpoint | 4.2 - Acceptance and closure of non-conforming items
label | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - H
label | HPP QA Key - H
holdpoint | AUTHORITY HOLDPOINT