## Project Structure
Main Folder | Subfolder | Subfolder | Subfolder | Checklist | Tier 7 | Instruction to CONQA | Checklist Name
Contact Energy - Te Huka Unit 3 J#39508
TOP-SEP-E-006 TH14 Tie-In
Instrument
|  |  | TH13/14 Control Valve-OPEN AND CLOSE FEED BACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH13/14 Control Valve-FEEDBACK AND SETPOINT |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH32 2-PH SEPARATOR, PRESSURE TRANSMITTER |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | U3 Separator Inlet Header , Pressure Transmitter |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
Cables
|  |  | Junction Box 3 | Junction Box 3 |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | TH00S030BHx10GY103-A01 | 1.5mm 6pr Multicore to JB03 |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L030NDA10AA110 -C01 | 1.5mm 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L030NDA10AA110 -A01 | 1.5mm 2pr CUSN ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L040NDA10CP010-A01 | 1.5mm2 1pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA10CP010-A01 | 1.5mm2 1pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000140NDA10AA080-P01 | 16mm2 3C+E CUsN XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000140NDA10AA072-P01 | 16mm2 3C+E CUsN XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000140NDA10AA080-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000140NDA10AA072-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJA10GS010_BOND12 | 120mm2 1C Earth |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-PTH32 -E-003 TH32 Field Lighting & Power
Cables
|  |  | TH000320BFA10GS010_-F52-P01 | 4mm2 2C+E CUSN PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
TOP-PTH32 -E-001 TH32 LV Power & Light Small Power
Earth Bonds
TH000320BFA10GS010_BOND01
|  |  | TH000320BFA10GS010_BOND02 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND03 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND05 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND06 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND07 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND08-1 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND08-2 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND11 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
Well Hut
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-114 Entec - UPS Installation |  |  | please add: | ITR-CL-1-114 Entec - UPS Installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-111 Electrical earthing |  |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
|  |  | ITR-CL-1-100 General Electrical Equipment Install |  |  | please add: | ITR-CL-1-100 General Electrical Equipment Install
|  |  | ITR-E-51A Entec - Cable tray and transits |  |  | please add: | ITR-CL-1-101C Cable Transits
|  |  | ITR-CL-1-106 - Junction Box |  |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | ITR-CL-1-105 Control Panel |  |  | please add: | ITR-CL-1-105 Control Panel
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
|  |  | ITR-CL-1-110 Generator Package (LV) |  |  | please add: | ITR-CL-1-110 Generator Package (LV)
Cables
|  |  | TH000320BFA10GS010_-F01-P01 | 95mm2 + 25mm2 4C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320BFA10GS010_-F05-P01 | 95mm2 + 25mm2 4C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320BFA10GS010-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320BFA10GS010-C02 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320BFA10GS010_-F01-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320BFA10GS010_-F05-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320BFA10GS010_-F37-P01 | 4mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320BFA10GS010_-F40-P01 | 6mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320BFA10GS010_-F44-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320BFA10GS010_-F46-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320BFA10GS010_-F53-P01 | 4mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320BFA10GS010_-F47-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320BFA10GS010_-F54-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
TOP-PTH32 -E-002 TH32 Process Equipment
Earth Bonds
|  |  | TH000320BFA10GS010_BOND04 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND09 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BFA10GS010_BOND10 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000320BHx10GY101-E01 | 120mm2 1C Cu PVC/PVC GE/YE
Instrument
|  |  | TH00L040NDA10CT010 - TH32 Wellpad Header - Temperature Transmitter |  |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH000320NDA10CP010 - TH32 Wellpad - Pressure Transmitter |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH000320NDA10CF010 - TH32 Branch Line - Flow Transmitter |  |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH000320NDA10CT010 - TH32 Branch Line - Temperature Transmitter |  |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH000320LFC10CL010 - TH32 Pond - Level Transmitter |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH000320NDA10CP020 - TH32 Pressure Indicating Transmitter |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00LO40NDA10AA010 - TH32 Low Point Silencer Purge Valve |  |  | please add: | ITR-CL-1-121 - Instrument Installation
Cables
|  |  | Junction Box 6 | Junction Box 6 |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | TH000320BHx10GY101-A01 | 1.5mm2 12Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320LFC10CL010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320NDA10CF010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320NDA10CP010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320NDA10CT010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L040NDA10CT010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320NDA10AA011-P01 | 6mm2 3C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320NDA10AA110_-P01 | 10mm2 3C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000320NDA10AA011-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000320NDA10AA110_-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
Fibre & Comms
|  |  | TH000320CRA10GH010-F01 | 24C OS2 Cable External Armoured L/Tube Gel PE/Nylon |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000320CRA10GH010-F02 | 24C OS2 Cable External Armoured L/Tube Gel PE/Nylon |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
TOP-ITH39 -E-003 TH39 Field Lighting & Power
Cables
|  |  | TH000390BFA10GS010_-F53-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
TOP-ITH39 -E-001 TH39 LV Power & Light Small Power
Well Hut
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-111 Electrical earthing |  |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
|  |  | ITR-CL-1-100 General Electrical Equipment Install |  |  | please add: | ITR-CL-1-100 General Electrical Equipment Install
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Cables
|  |  | TH000390BFA10GS010_-F01-P01 | 95mm2 + 25mm2 4C+E CuSn XLPE/PVC- TH39 400V Main Incomer |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010_-F05-P01 | 95mm2 + 25mm2 4C+E CuSn XLPE/PVC- TH39 400V Generator Incomer |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010-C01 | 1.5mm2 2C CuSn PVC/PVC-TH39 Switchboard Surge Protection Healthy |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390BFA10GS010-C02 | 1.5mm2 2C CuSn PVC/PVC-TH39 Phase Failure Relay Supply Healthy |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390BFA10GS010_-F01-C01 | 1.5mm2 4C CuSn PVC/PVC- TH39 MCCB F01 Opened, Closed, Tripped Feedback |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390BFA10GS010_-F05-C01 | 1.5mm2 4C CuSn PVC/PVC- TH39 MCCB F05 Opened, Closed, Tripped Feedback |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390BFA10GS010_-F37-P01 | 4mm2 4C+E CuSn PVC/PVC- TH39 H2S Scrubber Supply |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010_-F40-P01 | 2.5mm2 2C+E CuSn PVC/PVC- TH39 3 Phase Socket Outlet Supply |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TBC (TH39Lighting (Inside/Outside) Supply) | 2.5mm2 2C+E CuSn PVC/PVC- TH39 Lighting (Inside/Outside) Supply |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010_-F44-P01 | 2.5mm2 2C+E CuSn PVC/PVC-TH39 Single Phase Socket Outlet Supply |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010_-F46-P01 | 2.5mm2 2C+E CuSn PVC/PVC- TH39 Anti-Condenstation Heater Supply |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010_-F54-P01 | 4mm2 4C+E CuSn PVC/PVC- TH39 Wellpad Lightning Control Panel Supply |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010_-F47-P01 | 2.5mm2 2C+E CuSn PVC/PVC- TH39 Wellpad Lighting Inside |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010_-F52-P01 | 2.5mm2 2C+E CuSn PVC/PVC-TH39 Lighting Field |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000390BFA10GS010_-F40-C01 | 1.5mm2 12C CuSn PVC/PVC-TH39 H2S Scrubber Running, Healthy, Fault Feedback |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390CFx10CT010-C01 | 1.5mm2 1pr CuSn CS- TH39 Switchroom Temperature Feedback |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390SGY10EH010-C01 | 1.5mm2 2C CuSn PVC/PVC- TH39 Switchroom Smoke Alarm Feedback |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390CYP10EM010_QH01-C01 | 1.5mm2 2C CuSn PVC/PVC- TH39 Sitchroom Security Feedback |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
Earthing
|  |  | TH0003290BFA10GS010_BOND01 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH0003290BFA10GS010_BOND02 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH0003290BFA10GS010_BOND03 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH0003290BFA10GS010_BOND05 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH0003290BFA10GS010_BOND06 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH0003290BFA10GS010_BOND07 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH0003290BFA10GS010_BOND08-1 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH0003290BFA10GS010_BOND08-2 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH0003290BFA10GS010_BOND11 | 240mm2 1C CuSn(BAR CABLE) |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-ITH39 -E-002 TH39 Process Equipment
Instrument
|  |  | TH00XXXLFC10CL010 - TH39 Well Pad Pond - Level Transmitter |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH000390NDB10CF010 - TH39 Branch Line - Flow Transmitter |  |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00390NDB10CP010 - TH39 Wellhead - Pressure Transmitter |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00L260NDB10CP010 - TH39 Well Pad Reinjection - Pressure Transmitter |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00L260NDB10CT030 - TH39 Well Pad Reinjection - Temperature Transmitter |  |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00390NDB10AA110 - TH39 Control Valve |  |  | please add: | ITR-CL-1-121 - Instrument Installation
Cables
|  |  | Junction Box 7 | Junction Box 7 |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | TH000390BHx10GY101-A01 | 1.5mm2 12pr CuSn ESCS- Twisted Pair Multicore to Junction Box 07 |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390BHx10GY101-E01 | 120mm2 1C Cu PVC/PVC GE/YE- Feild Earth Bonding |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000390NDB10CF010-A01 | 1.5mm2 1pr CuSn CS- TH39 Pond, Level Transmitter |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00XXX0LFC10CL010-A01 | 1.5mm2 1pr CuSn CS- TH39 Branch Line, Pressure Transmitter |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L260NDB10CT030-A01 | 1.5mm2 1pr CuSn CS- TH39 Wellhead, Pressure Transmitter |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L260NDB10CP020-A01 | 1.5mm2 1pr CuSn CS- TH39 Branch Line, Temperature Transmitter |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390NDB10CP010-A01 | 1.5mm2 1pr CuSn CS- Wellpad Header Temperature Transmitter |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390NDB10AA110_-P01 | 10mm2 3C+E CuSn XLPE/PVC- Reinjeection Wellhead TH39 Control Valve |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000390NDB10AA110_-S01 | Profibus DP - Grey Sheath- Production Wellhead TH39 Control Valve |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
Fibre & Comms
|  |  | TH000320CRS20GN011-S01 | Single Mode Fibre Patch Lead- Internal Panel Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000320CRS20GN011-S02 | Single Mode Fibre Patch Lead- Internal Panel Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000320CRS20GN011-S03 | Single Mode Fibre Patch Lead- Internal Panel Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000320CRS20GN011-S04 | Single Mode Fibre Patch Lead- Internal Panel Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000390CRA20GU003-S01 | Single Mode Fibre Patch Lead- Internal Panel Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000390CRA20GU003-S02 | Profibus DP - Grey Sheath- Internal Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000390CRA20GU009-S01 | Single Mode Fibre Patch Lead- Internal Panel Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000390CRA20GU009-S02 | Profibus DP - Grey Sheath- Internal Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH39-RLM01-S01 | Profibus DP - Grey Sheath- Internal Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH39-RLM01-S02 | Profibus DP - Grey Sheath- Internal Wiring |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
TOP-SEP-E-007 Seperation Field Light & Power
Cables
|  |  | TH00S030BJB30GS010_-F01-P01 | 4mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | TH00S030BJB30GS010_-F12-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | SEPARATOR TASK LIGHITNG SUPPLY SECTION 2 - DUMP STATION | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | SEPARATOR TASK LIGHITNG SUPPLY SECTION 3 - TH14 | 35mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB30GS010_-F03-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB30GS010_-F14-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | SEPARATOR LIGHTING REMOTE SWITCHING Section 1 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | SEPARATOR LIGHTING REMOTE SWITCHING Section 2 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | SEPARATOR LIGHTING REMOTE SWITCHING Section 3 | 2.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
TOP-SEP-E-001 SEP LV Power
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-111 Electrical earthing |  |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
|  |  | ITR-CL-1-100 General Electrical Equipment Install |  |  | please add: | ITR-CL-1-100 General Electrical Equipment Install
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Cables
|  |  | TH00S030BJB10GS010_-F01-R01 | 500mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_-F01-W01 | 500mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_-F01-B01 | 500mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_-F01-N01 | 500mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_F01_E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_-F05-R01 | 240mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_-F05-W01 | 240mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_-F05-B01 | 240mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_-F05-N01 | 240mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB10GS010_-F05-E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB30GS010_-F04-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB30GS010_-F06-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB30GS010_-F07-P01 | 4mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BJB30GS010_-F10-P01 | 6mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
Earthing
|  |  | TH00S030BJA10GS010_BOND01 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BJA10GS010_BOND02 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BJA10GS010_BOND03 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BJA10GS010_BOND04 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BJA10GS010_BOND05 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BJA10GS010_BOND08-1 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BJA10GS010_BOND08-2 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BJA10GS010_BOND13 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-SEP-E-005 SEP Vent Station
Earthing
|  |  | TH00S030BJA10GS010_BOND09 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BJA10GS010_BOND10 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BHX10GY101-E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BHx10GY104-E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
Instrument
|  |  | TH00S030LFC20CL040 - Separator Station Silencer Weirbox, Level Transmitter | ITR-CL-1-131 Level Instrument Installation |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH00S030NAA10CT051 - U3 Steam Supply Rupture Disc Burst, Temperature Sensor 1 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00S030NAA10CT052 - U3 Steam Supply Rupture Disc Burst, Temperature Sensor 2 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00S030NAA10CT053 - U3 Steam Supply Rupture Disc Burst, Temperature Sensor 3 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00S030NAA10CT054 - U3 Steam Supply Rupture Disc Burst, Temperature Sensor 4 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00S030NAA10CT055 - U3 Steam Supply Rupture Disc Burst, Temperature Sensor 5 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00S030NAA10CT056 - U3 Steam Supply Rupture Disc Burst, Temperature Sensor 6 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00V030NAA10AA110 - Rock Muffler 1 Control Valve-Valve Position Analogue Feedback AND Valve Position Setpoint | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00V030NAA10AA120 - Rock Muffler 2 Control Valve-Valve Position Analogue Feedback AND Valve Position Setpoint | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NDA20AA110 - SGW Vent Valve (MDV)-FEED BACK AND Valve Position Setpoint | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NDA20CF010 - U3 ORC SGW Supply, Flow Transmitter(Orifice DP) | ITR-CL-1-129 Flow Meter Installation |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00S030NDA20CP010 - U3 ORC SGW Supply Strainer, Differential Pressure | ITR-CL-1-130 Pressure Instrument Installation |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NDA20AA110 - SGW Vent Valve (MDV)-SET POINT | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NDA20AA120 - SGW Vent Valve (EDV 1)- Valve Position Analogue Feedback AND Valve Position Setpoint | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NDA20AA130 - SGW Vent Valve (EDV 2)-Valve Position Analogue Feedback AND Valve Position Setpoint | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00V030NAA10AA110 - Rock Muffler 1 Control Valve | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00V030NAA10AA120 - Rock Muffler 2 Control Valve | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NDA20AA110 - SGW Vent Valve (MDV) | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NDA20AA120 - SGW Vent Valve (EDV 1) | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NDA20AA130 - SGW Vent Valve (EDV 2) | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030LFC10AA420 - SGW DRUM SOLIDS TRAP PURGE VALVE | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NAA10CF020 - U3 ORC Steam Supply Performance Monitoring, Flow Transmitter 1 | ITR-CL-1-129 Flow Meter Installation |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00S030NAA10CF030 - U3 ORC Steam Supply Performance Monitoring, Flow Transmitter 2 | ITR-CL-1-129 Flow Meter Installation |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00S030NDA20CF020 - FLOW TRANSMITTER, VENTURI, SGW PERFORMANCE TESTING 1 | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NDA20CF030 - U3 ORC SGW Supply Performance Monitoring 1, Flow Transmitter(Venturi DP) | ITR-CL-1-129 Flow Meter Installation |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00S030NDA20CF040 - U3 ORC SGW Supply Performance Monitoring 2, Flow Transmitter (Venturi DP) | ITR-CL-1-129 Flow Meter Installation |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00S030NDA20CP020 - U3 ORC SGW Supply Performance Monitoring , Pressure Transmitter | ITR-CL-1-130 Pressure Instrument Installation |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NDA20CT010 - U3 ORC SGW Supply Performance Monitoring , Temperature Transmitter | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00S030NAA10CT020 - U3 Steam Supply Performance monitoring, Temperature Transmitter 1 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00S030NAA10CT030 - U3 Steam Supply Performance monitoring, Temperature Transmitter 2 | ITR-CL-1-121 - Instrument Installation |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00S030NAA10CP010 - U3 ORC Steam Supply Performance Monitoring, Pressure Transmitter | ITR-CL-1-130 Pressure Instrument Installation |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NAA10CL010 - U3 Steam Supply CDP3, Level Transmitter | ITR-CL-1-131 Level Instrument Installation |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH00L260NDB10CF010 - U3 ORC SGW Return , Flow Transmitter | ITR-CL-1-129 Flow Meter Installation |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00L260NDB10CP010 - U3 ORC SGW Return , Pressure Transmitter | ITR-CL-1-130 Pressure Instrument Installation |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00L260NDB10CT010 - U3 ORC SGW Return , Temperature Transmitter 1 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00L260NDB10CT020 - Reinjection Line D/S EDP return, Temperature Transmitter 2 | ITR-CL-1-128 Temperature Instrument Installation |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
[6 empty] | please add: | ITR-CL-1-130 Pressure Instrument Installation
Cables
|  |  | TH00S030LFC20CL040-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | Junction Box 01 | Junction Box 01 |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | TH00S030BHX10GY101-A01 | 1.5mm2 12Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT051-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT052-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT053-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT054-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT055-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT056-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BHx10GY101-A02 | 1.5mm2 12Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00V030NAA10AA110-A01 | 1.5mm2 2Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00V030NAA10AA120-A01 | 1.5mm2 2Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20CF010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20CP010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA110-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA120-A02 | 1.5mm2 2Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA130-A02 | 1.5mm2 2Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BHx10GY101-C01 | 1.5mm2 27C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00V030NAA10AA110-C01 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00V030NAA10AA120-C01 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA110-C01 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA120-C02 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA130-C02 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030LFC10AA420-C01 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | Junction Box 04 | Junction Box 04 |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | TH00S030BHx10GY104-A01 | 1.5mm2 12Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BHx10GY104-A02 | 1.5mm2 12Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CF020-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CF030-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20CF020-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20CF030-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20CF040-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20CP020-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20CT010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT020-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT030-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CP010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CL010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L260NDB10CF010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L260NDB10CP010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L260NDB10CT010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L260NDB10CT020-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA120-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA130-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
TOP-SEP-E-002 SEP UPS A System
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-114 Entec - UPS Installation |  |  | please add: | ITR-CL-1-114 Entec - UPS Installation
Cables
|  |  | TH00S030BTA10-P02 | 25mm2 3C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030BUC10-A01 | 1.5mm2 2Pr CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BRA10-C01 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BRA10-P01 | 4mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030CRA10GW010_-G01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRA10GW020_-G01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRA10GW030_-G01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRA10GW011_-G01-P01 | 4mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030CRA10GW021_-G01-P01 | 4mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030CRA10GW031_-G01-P01 | 4mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
TOP-SEP-E-004 SEP Seperation Field
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-111 Electrical earthing |  |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | ITR-CL-1-106 - Junction Box |  |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Instrument
|  |  | TH00S030QFB10CP020 - INSTRUMENT AIR PRESSURE TRANSMITTER |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NAA10CP021 - Separator Discharge Steam, Pressure Transmitter 1 |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NAA10CP022 - Separator Discharge Steam, Pressure Transmitter 2 |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NAA10CP023 - Separator Steam Discharge, Pressure Transmitter 3 |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NAA10CF010 - U3 Separator Steam Line, Flow Transmitter |  |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00S030NAA10CT010 - Separator Steam Discharge, Temperature Transmitter |  |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00S030NDA10CL021 - SGW Drum, Level Transmitter, Differential Pressure 1 |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NDA10CL022 - SGW Drum, Level Transmitter, Differential Pressure 2 |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NDA10CL023 - LEVEL TRANSMITTER SGW DRUM DIFFERENTIAL PRESSURE 3 |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00S030NDA10CL024 - SGW Loop Seal, Level Transmitter |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH00S030NDA10CL011 - SIS LEVEL TRANSMITTER SGW DRUM RADAR 1 |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH00S030NDA10CL012 - SIS LEVEL TRANSMITTER SGW DRUM RADAR 2 |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH00S030NDA10CL013 - SIS LEVEL TRANSMITTER SGW DRUM RADAR 3 |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
Cables
|  |  | TH00S030QFB10CP020-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | Junction Box 02 | Junction Box 02 |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | TH00S030BHX10GY102-A01 | 1.5mm2 12Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CP021-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CP022-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CP023-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CF010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NAA10CT010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA10CL021-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA10CL022-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA10CL023-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA10CL024-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L040NDA10AA010-P01 | 35mm2 3C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00L040NDA10AA040-P01 | 16mm2 3C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030NDA10AA420-P01 | 16mm2 3C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030LFC10AA010-P01 | 16mm2 3C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030NDA20AA002-P01 | 16mm2 3C+E CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00L040NDA10AA010-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L040NDA10AA040-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA01AA420-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030LFC10AA010-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA20AA002-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA10CL011-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA10CL012-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030NDA10CL013-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
Earthing
|  |  | TH00S030BHX10GY102-E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH00S030BHX10GY103-E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-SEP-E-003 SEP DCS & Comms
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
Instruments and Control
|  |  | CSB PLC CABINET - CSB ACB F01 24V DC CONTROL FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | CSB PLC CABINET - CSB ACB F05 24V DC CONTROL FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR PLC CABINET - SEPARATOR ACB F01 24V DC CONTROL FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR PLC CABINET - SEPARATOR ACB F05 24V DC CONTROL FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR PLC CABINET - SEPARATOR SWITCHBOARD SURGE PROTECTION HEALTHY FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR PLC CABINET - SEPARATOR PHASE FAILURE RELAY SUPPLY HEALTHY FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR PLC CABINET - SEPARATOR SWITCHROOM TEMPERATURE FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR PLC CABINET - SEPARATOR SWITCHROOM SMOKE ALARM FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR PLC CABINET - SEPARATOR H2S SCRUBBER RUNNING, HEALTHY, FAULT, FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR PLC CABINET - SEPARATOR SWITCHROOM SECURITY FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - SIS CABINET ET1 24VDC MONITORING FEEDBACK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - SIS PSU1A 110V DC FEEDER |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - SIS 24VDC SYSTEM PSU1A OK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - SIS PSU1B 110V DC FEEDER |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - SIS 24VDC SYSTEM PSU1B OK |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - 10CL011 SIGNAL FROM SIS TO BPCS |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - 10CL011 SIS FEEDBACK AND RESET BETWEEN SIS AND BPCS |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - 10CL012 SIGNAL FROM SIS TO BPCS |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - 10CL012 SIS FEEDBACK AND RESET BETWEEN SIS AND BPCS |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - 10CL013 SIGNAL FROM SIS TO BPCS |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - 10CL013 SIS FEEDBACK AND RESET BETWEEN SIS AND BPCS |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | SEPARATOR SIS CABINET - AUX POWER SUPPLY FOR SIS PANEL |  |  | please add: | ITR-CL-1-121 - Instrument Installation
Cables
|  |  | TH000000BJB10GS010_-F01-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BJB10GS010_-F05-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB10GS010_-F01-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB10GS010_-F05-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB10GS010_-F01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB10GS010_-F05-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB10GS010-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB10GS010-C02 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CFX10CT010-C01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030SGY10EH010-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB30GS010_-F06-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CYP10EM010_QH01 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10EU101-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10GW011-P01 | 4mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030CRJ10GW011-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10GW021-P01 | 4mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00S030CRJ10GW021-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10CL011-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10CL011-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10CL012-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10CL012-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10CL013-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRJ10CL013-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030BJB20GS010-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
Fibre & Comms
|  |  | TH00S030CRA10GH010-F01 | 24C OS2 + 24C OM3 INSTALLED IN Emtelle 7 Tube Duct |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRA10GH010-F02 | 24C OS2 + 24C OM3 INSTALLED IN Emtelle 7 Tube Duct |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRR10GU201-S01 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRR10GU202-S01 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRR10GU201-S02 | Plastic Fibre Patch Lead - ABB TK8110VO POF Cable |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRR10GU202-S02 | Plastic Fibre Patch Lead - ABB TK8110VO POF Cable |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRR10EV201-S01 | Plastic Fibre Patch Lead - ABB TK8110VO POF Cable |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRR10EV201-S02 | Plastic Fibre Patch Lead - ABB TK8110VO POF Cable |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRS10GN008 -S01 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRS10GN008 -S02 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRS10GN008 -S03 | CAT 5E |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRS10GN008 -S04 | CAT 5E |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRA20GU011-S01 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRA20GU010-S01 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRA20GU012-S01 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030BJA10GS010_BOND06 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030BJA10GS010_BOND07 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030BJA10GS010_BOND11 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030BJA10GS010_BOND14 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
TOP-ASB-E-003 SEP DCS & Comms
Earthing
|  |  | JUNCTION BOX-08-E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
Cables
|  |  | Junction Box 08 | Junction Box 08 |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | JUNCTION BOX-08-C01 | 1.5mm2 27C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | JUNCTION BOX-08-C02 | 1.5mm2 27C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | JUNCTION BOX-08-C03 | 1.5mm2 27C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | JUNCTION BOX-08-C04 | 1.5mm2 27C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | JUNCTION BOX-08-A01 | 1.5mm2 12Pr CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F01-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F01-C02 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F05-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F05-C02 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F09-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F05-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F09-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFT20-C02 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFT20-C03 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010-C02 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F37-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F40-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F43-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F46-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F49-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BFA40GS010_-F52-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BRA20-A01 | 1.5mm2 2Pr CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BRA20-C01 | 1.5mm2 4C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BUC20GU101-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000MAJ20-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000SGY10EH010-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CFX10CT010-C01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
Fibre & Comms
|  |  | TH000000BFA40GS010-F01 | 8C OS2 + 8C OM3 INSTALLED IN Emtelle 7 Tube Duct |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRS10GN009-S01 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRS10GN009-S02 | OM3 Fibre Patch Lead |  | please add: | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH00S030CRS10GN009-S03 | CAT 5E |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
TOP-CSB-E-003 SEP DCS & Comms
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-114 Entec - UPS Installation |  |  | please add: | ITR-CL-1-114 Entec - UPS Installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-111 Electrical earthing |  |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
|  |  | ITR-CL-1-100 General Electrical Equipment Install |  |  | please add: | ITR-CL-1-100 General Electrical Equipment Install
|  |  | ITR-CL-1-106 - Junction Box |  |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | ITR-CL-1-105 Control Panel |  |  | please add: | ITR-CL-1-105 Control Panel
|  |  | ITR-CL-1-110 Generator Package (LV) |  |  | please add: | ITR-CL-1-110 Generator Package (LV)
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Cables
|  |  | TH000000BJB10GS010_-F01-P01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BJB10GS010_-F05-P01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BJB10GS010-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BJB10GS010-C02 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BUC10-A01 | 1.5mm2 2Pr CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BUD10-A01 | 1.5mm2 2Pr CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BUC10-C01 | 1.5mm2 4C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BUD10-C01 | 1.5mm2 4C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BRC10-A01 | 1.5mm2 2Pr CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BRD10-A01 | 1.5mm2 2Pr CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BRA10-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BRB10-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GW010_-G01-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GW011_-G01-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CYW10EU101-A01 | 1.5mm2 1Pr CuSn CS |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA20GW010_-G01-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA20GW011_-G01-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CYW20EU101-A01 | 1.5mm2 1Pr CuSn CS |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN001-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN002-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN003-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN004-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN005-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN006-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN007-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRS10GN009-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU003-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU002-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU011-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU010-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU009-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU008-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU012-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CYP20EH010-C01 | 1.5mm2 12C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CYP20EM010_QH01-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CYP20EM010_QH02-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CYP20EM010_QH03-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000SRxCF010_-S01-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CFX20CT010-C01 | 1.5mm2 1Pr CuSn CS |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000MAJ10-C01 | 1.5mm2 12C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000SGY20EH010-C01 | 1.5mm2 2C CuSn PVC/PVC |  |  | ITR-CL-1-132 - Instrument/Control Cables
Fibre & Comms
|  |  | TH000000CYW10GH002-F01 | 24C OS2 + 24C OM3 INSTALLED IN Emtelle 7 Tube Duct |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CYW10GH002-F02 | 24C OS2 + 24C OM3 INSTALLED IN Emtelle 7 Tube Duct |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN001-S01 | Single Mode Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN001-S02 | Single Mode Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN001-S03 | Cat 5E Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN002-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN002-S02 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN002-S03 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10EP001-S01 | Cat 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10EP001-S02 | Cat 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10EP002-S01 | Cat 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10EP002-S02 | Cat 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ001-S01 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ001-S02 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ001-S03 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ001-S04 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ001-S05 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU0GJ003-S01 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ003-S02 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ003-S03 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ003-S04 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRU10GJ003-S05 | Cat 5E Patch Lead |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN003-S01 | Single Mode Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN003-S02 | Single Mode Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN004-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN004-S02 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN005-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN005-S02 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRR10GU101-S01 | OM3 Fibre Cable |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRR10GU101-S02 | Plastic Fibre Patch Lead - ABB TK8110VO POF Cable |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRR10GU102-S01 | OM3 Fibre Cable |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRR10GU102-S02 | Plastic Fibre Patch Lead - ABB TK8110VO POF Cable |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10EP001-S04 | Plastic Fibre Patch Lead - ABB TK8110VO POF Cable |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10EP002-S05 | Plastic Fibre Patch Lead - ABB TK8110VO POF Cable |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN006-S01 | Single Mode Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN006-S02 | Single Mode Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN006-S03 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRS10GN006-S04 | CAT 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN006-S05 | CAT 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN006-S06 | CAT 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRS10GN006-S07 | CAT 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00S030CRS10GN007-S01 | CAT 5E |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU003-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10GU003-S02 | Profibus DP - Grey Sheath |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU002-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10GU002-S02 | Profibus DP - Grey Sheath |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU008-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10GU008-S02 | Profibus DP - Grey Sheath |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU009-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10GU009-S02 | Profibus DP - Grey Sheath |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU011-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10GU011-S02 | Profibus DP - Grey Sheath |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU010-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10GU010-S02 | Profibus DP - Grey Sheath |  |  | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000CRA10GU012-S01 | OM3 Fibre Patch Lead |  |  | ITR-I-44A Entec - Fibre Optic Cable
|  |  | TH000000CRA10GU012-S02 | Profibus DP - Grey Sheath |  |  | ITR-CL-1-132 - Instrument/Control Cables
Earthing
|  |  | TH000000BJB10GS010_BOND05 | 70mm2 1C Cu PVC/PVC GE/YE |  |  | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND06 | 70mm2 1C Cu PVC/PVC GE/YE |  |  | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND07 | 70mm2 1C Cu PVC/PVC GE/YE |  |  | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND08 | 70mm2 1C Cu PVC/PVC GE/YE |  |  | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND14 | 70mm2 1C Cu PVC/PVC GE/YE |  |  | ITR-CL-1-111 Electrical earthing
TOP- ASB-E-002 ASB UPS B System
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-114 Entec - UPS Installation |  |  | please add: | ITR-CL-1-114 Entec - UPS Installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-111 Electrical earthing |  |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
|  |  | ITR-CL-1-100 General Electrical Equipment Install |  |  | please add: | ITR-CL-1-100 General Electrical Equipment Install
|  |  | ITR-CL-1-105 Control Panel |  |  | please add: | ITR-CL-1-105 Control Panel
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Cables
|  |  | TH000000BFA40GS010_-F56 - R01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F56 - W01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F56 - B01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F56 - N01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F56 - E01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BRA20-P01 | 4mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
TOP-CSB-E-001 CSB LV Power
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-114 Entec - UPS Installation |  |  | please add: | ITR-CL-1-114 Entec - UPS Installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-111 Electrical earthing |  |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
|  |  | ITR-CL-1-100 General Electrical Equipment Install |  |  | please add: | ITR-CL-1-100 General Electrical Equipment Install
|  |  | ITR-CL-1-106 - Junction Box |  |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | ITR-CL-1-105 Control Panel |  |  | please add: | ITR-CL-1-105 Control Panel
|  |  | ITR-CL-1-110 Generator Package (LV) |  |  | please add: | ITR-CL-1-110 Generator Package (LV)
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Cables
|  |  | TH000000BJB10GS010_-F01 - R01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - W01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - B01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - R02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - W02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - B02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - R03 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - W03 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - B03 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - N01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F01 - N02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_F01 - N03 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F05 - R01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F05 - W01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F05 - B01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F05 - R02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F05 - W02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F05 - B02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F05 - N02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F05 - N03 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F40 - R01 | 240mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F40 - W01 | 240mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F40 - B01 | 240mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F40 - N01 | 240mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB20GS010_-F05-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_F01 _E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_-F05 - E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_-F40 - E01 | 95mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND01 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND02 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND03 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND04 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND17-1 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND17-2 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND18 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-CSB-E-002 CSB UPS A&B
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-114 Entec - UPS Installation |  |  | please add: | ITR-CL-1-114 Entec - UPS Installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
Cables
|  |  | TH000000BJB10GS010_-F34 - R01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F34 - W01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F34 - B01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F34 - N01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BJB10GS010_-F34 - E01 | 70mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BTL10-P02 | 150mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BTL10-P03 | 150mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BTL10-P04 | 150mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BTL10-P05 | 150mm2 1C Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BRA10-P01 | 16mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BRB10-P01 | 16mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BRA10-P02 | 16mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BRB10-P02 | 16mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000CRA10GW010_-G01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000CRA10GW010_-G01-P02 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000CRA20GW010_-G01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000CRA20GW010_-G01-P02 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000CRA30GW010_-G01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000CRA30GW010_-G01-P02 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000CRA30GW020_-G01-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000CRA30GW020_-G01-P02 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
Earthing
|  |  | TH000000BJB10GS010_BOND10 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND11 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND12 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND13 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND15 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND16 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
TOP- ASB-E-001 ASB HV & LV Power
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
|  |  | ITR-CL-1-100 General Electrical Equipment Install |  |  | please add: | ITR-CL-1-100 General Electrical Equipment Install
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Cables
|  |  | TH000000BFA40GS010_-F05-R01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-W01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-B01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-R02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-W02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-B02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-R03 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-W03 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-B03 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-N01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-N02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F05-N03 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F09-R01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F09-W01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F09-B01 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F09-R02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F09-W02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F09-B02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F09-N02 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F09-N03 | 630mm2 1C AL XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
Earthing
|  |  | TH000000BFA40GS010_-F05-E01 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BFA40GS010_BOND02 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BFA40GS010_BOND03 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BFA40GS010_BOND04 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BFA40GS010_BOND05 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BFA40GS010_BOND06 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-CSB-E-004 EDP Pump
Instrument
|  |  | TH00EDP3GMA10CL010 - Emergency Dump Pond, Level Transmitter 1 |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH00EDP3GMA10CL011 - Emergency Dump Pond, Level Transmitter 2 |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH00EDP3GMA10CL012 - Emergency Dump Pond, Level Transmitter 3 |  |  | please add: | ITR-CL-1-131 Level Instrument Installation
|  |  | TH00EDP3GNK10CP010 - EDP Pump Discharge, Pressure Transmitter |  |  | please add: | ITR-CL-1-130 Pressure Instrument Installation
|  |  | TH00EDP3GNK10CF010 - EDP Pump Discharge, Flow Transmitter(Orifice DP) |  |  | please add: | ITR-CL-1-129 Flow Meter Installation
|  |  | TH00EDP3GNK10CT010 - EDP PUMP DISCHARGE TEMPERATURE |  |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00EDP3GMA10CT010 - Emergency Dump Pond, Temperature Transmitter |  |  | please add: | ITR-CL-1-128 Temperature Instrument Installation
|  |  | TH00L040NDA10AA410 - TH32 Low Point Silencer Dump Valve |  |  | please add: | ITR-CL-1-121 - Instrument Installation
|  |  | TH00L040NDA10AA410 - TH32 Low Point Silencer Dump Valve |  |  | please add: | ITR-CL-1-121 - Instrument Installation
Cables
|  |  | Junction Box 05 | Junction Box 05 |  | please add: | ITR-CL-1-106 - Junction Box
|  |  | TH00EDP0BPA10AP010-P01 | 185mm2 +25mm2 3C+3E Varolex VSD CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00EDP0BPA10AP010-A01 | 1.5mm2 4Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP0BPA10AP010-C01 | 1.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP3GMA10AP010_-M01-P01 | 185mm2 +25mm2 3C+3E Varolex VSD CuSn XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00EDP3GMA10AP010_-M01-C01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP0BPA10AP010CP-P01 | 1.5mm2 2C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH000000BHx10GY101-A01 | 1.5mm2 12Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP3GMA10CL010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP3GMA10CL011-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP3GMA10CL012-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP3GNK10CP010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP3GNK10CF010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP3GNK10CT010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP3GMA10CT010-A01 | 1.5mm2 1Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00L040NDA10AA410-P01 | 70mm2 4C+E Cu XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH00L040NDA10AA410-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | TH00EDP0BPA10AP010-S01 | Profibus DP - Grey Sheath |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
Earthing
|  |  | TH000000BJB10GS010_BOND09 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND19 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND20 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BJB10GS010_BOND21 | 70mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BHx10GY101-E01 | 120mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-ORM-E-001 Ormat U3E Supply
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-111 Electrical earthing |  |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | ITR-CL-1-108 - Electrical Switch Room |  |  | please add: | ITR-CL-1-108 - Electrical Switch Room
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-109 Electrical Equipment Package |  |  | please add: | ITR-CL-1-109 Electrical Equipment Package
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Cables
|  |  | TH000000BFA40GS010_-F43-R01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F43-W01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F43-B01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F43-R02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F43-W02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F43-B02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F43-N01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F43-N02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
Earthing
|  |  | TH000000BFA40GS010_-F43-E01 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
|  |  | TH000000BFA40GS010_-F43-E02 | 240mm2 1C Cu PVC/PVC GE/YE |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-ORM-E-002 Ormat U3C Supply
Cables
|  |  | TH000000BFA40GS010_-F01-R01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-W01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-B01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-R02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-W02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-B02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-R03 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-W03 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-B03 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-N01 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-N02 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BFA40GS010_-F01-N03 | 630mm2 1C Al XLPE/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
Earthing
|  |  | TH000000BFA40GS010_BOND01 | 1.5mm2 2Pr CuSn ESCS |  | please add: | ITR-CL-1-111 Electrical earthing
TOP-ORM-E-003 Ormat SIS Interface
Cables
|  |  | ORMAT-A01 | 1.5mm2 12Pr CuSn ESCS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | ORMAT-A02 | 1.5mm2 12Pr CuSn CS |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | ORMAT-C01 | 2.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
|  |  | ORMAT-C02 | 2.5mm2 12C CuSn PVC/PVC |  | please add: | ITR-CL-1-132 - Instrument/Control Cables
TOP-ASB-E-004 Building Light and Power
Electrical Installations
|  |  | Cable Pre-installation |  |  | please add: | Cable Pre-installation
|  |  | ITR-CL-1-101B Cable Supports Above Ground |  |  | please add: | ITR-CL-1-101B Cable Supports Above Ground
|  |  | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  | please add: | ITR-CL-1-101A Conduit/Ducting Below Ground
|  |  | ITR-CL-1-102 - Distribution Board Installation |  |  | please add: | ITR-CL-1-102 - Distribution Board Installation
|  |  | ITR-CL-1-103 - Schedule of Test Results DB |  |  | please add: | ITR-CL-1-103 - Schedule of Test Results DB
|  |  | ITR-CL-1-100 General Electrical Equipment Install |  |  | please add: | ITR-CL-1-100 General Electrical Equipment Install
|  |  | Certificate of Compliance |  |  | please add: | Certificate of compliance
Cables
|  |  | TH000000BKB10GS010-F01-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BKB10GS010-F03-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BKB10GS010-F04-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BKB10GS010-F05-P01 | 2.5mm2 2C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BKB10GS010-F06-P01 | 4mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
|  |  | TH000000BKB10GS010-F09-P01 | 6mm2 4C+E CuSn PVC/PVC |  | please add: | ITR-CL-1-104 - Low Voltage Cable
Inground Earthing
Cadwelds
|  |  | TH32 Wellpad | Cadweld #1 |  | please add: | Cadweld
|  |  |  | Cadweld #2 |  | please add: | Cadweld
|  |  |  | Cadweld #3 |  | please add: | Cadweld
|  |  |  | Cadweld #4 |  | please add: | Cadweld
|  |  |  | Cadweld #5 |  | please add: | Cadweld
|  |  |  | Cadweld #6 |  | please add: | Cadweld
|  |  |  | Cadweld #7 |  | please add: | Cadweld
|  |  |  | Cadweld #8 |  | please add: | Cadweld
|  |  |  | Cadweld #9 |  | please add: | Cadweld
|  |  |  | Cadweld #10 |  | please add: | Cadweld
|  |  |  | Cadweld #11 |  | please add: | Cadweld
|  |  |  | Cadweld #12 |  | please add: | Cadweld
|  |  |  | Cadweld #13 |  | please add: | Cadweld
|  |  |  | Cadweld #14 |  | please add: | Cadweld
|  |  |  | Cadweld #15 |  | please add: | Cadweld
|  |  | TH14 Wellpad | Cadweld #1 |  | please add: | Cadweld
|  |  |  | Cadweld #2 |  | please add: | Cadweld
|  |  |  | Cadweld #3 |  | please add: | Cadweld
|  |  |  | Cadweld #4 |  | please add: | Cadweld
|  |  |  | Cadweld #5 |  | please add: | Cadweld
|  |  |  | Cadweld #6 |  | please add: | Cadweld
|  |  | Separator | Cadweld #1 |  | please add: | Cadweld
|  |  |  | Cadweld #2 |  | please add: | Cadweld
|  |  |  | Cadweld #3 |  | please add: | Cadweld
|  |  |  | Cadweld #4 |  | please add: | Cadweld
|  |  |  | Cadweld #5 |  | please add: | Cadweld
|  |  |  | Cadweld #6 |  | please add: | Cadweld
|  |  |  | Cadweld #7 |  | please add: | Cadweld
|  |  |  | Cadweld #8 |  | please add: | Cadweld
|  |  |  | Cadweld #9 |  | please add: | Cadweld
|  |  |  | Cadweld #10 |  | please add: | Cadweld
|  |  |  | Cadweld #11 |  | please add: | Cadweld
|  |  |  | Cadweld #12 |  | please add: | Cadweld
|  |  |  | Cadweld #13 |  | please add: | Cadweld
|  |  |  | Cadweld #14 |  | please add: | Cadweld
|  |  |  | Cadweld #15 |  | please add: | Cadweld
|  |  |  | Cadweld #16 |  | please add: | Cadweld
|  |  |  | Cadweld #17 |  | please add: | Cadweld
|  |  |  | Cadweld #18 |  | please add: | Cadweld
|  |  |  | Cadweld #19 |  | please add: | Cadweld
|  |  |  | Cadweld #20 |  | please add: | Cadweld
|  |  |  | Cadweld #21 |  | please add: | Cadweld
|  |  |  | Cadweld #22 |  | please add: | Cadweld
|  |  |  | Cadweld #23 |  | please add: | Cadweld
|  |  |  | Cadweld #24 |  | please add: | Cadweld
|  |  |  | Cadweld #25 |  | please add: | Cadweld
|  |  | Vent Station | Cadweld #1 |  | please add: | Cadweld
|  |  |  | Cadweld #2 |  | please add: | Cadweld
|  |  |  | Cadweld #3 |  | please add: | Cadweld
|  |  |  | Cadweld #4 |  | please add: | Cadweld
|  |  |  | Cadweld #5 |  | please add: | Cadweld
|  |  |  | Cadweld #6 |  | please add: | Cadweld
|  |  |  | Cadweld #7 |  | please add: | Cadweld
|  |  |  | Cadweld #8 |  | please add: | Cadweld
|  |  |  | Cadweld #9 |  | please add: | Cadweld
|  |  |  | Cadweld #10 |  | please add: | Cadweld
|  |  |  | Cadweld #11 |  | please add: | Cadweld
|  |  |  | Cadweld #12 |  | please add: | Cadweld
|  |  |  | Cadweld #13 |  | please add: | Cadweld
|  |  |  | Cadweld #14 |  | please add: | Cadweld
|  |  |  | Cadweld #15 |  | please add: | Cadweld
|  |  |  | Cadweld #16 |  | please add: | Cadweld
|  |  |  | Cadweld #17 |  | please add: | Cadweld
|  |  |  | Cadweld #18 |  | please add: | Cadweld
|  |  |  | Cadweld #19 |  | please add: | Cadweld
|  |  |  | Cadweld #20 |  | please add: | Cadweld
|  |  | Unit 3 Interface | Cadweld #1 |  | please add: | Cadweld
|  |  |  | Cadweld #2 |  | please add: | Cadweld
|  |  |  | Cadweld #3 |  | please add: | Cadweld
|  |  |  | Cadweld #4 |  | please add: | Cadweld
|  |  |  | Cadweld #5 |  | please add: | Cadweld
|  |  |  | Cadweld #6 |  | please add: | Cadweld
|  |  |  | Cadweld #7 |  | please add: | Cadweld
|  |  |  | Cadweld #8 |  | please add: | Cadweld
|  |  |  | Cadweld #9 |  | please add: | Cadweld
|  |  |  | Cadweld #10 |  | please add: | Cadweld
|  |  | TH39 Wellpad | Cadweld #1 |  | please add: | Cadweld
|  |  |  | Cadweld #2 |  | please add: | Cadweld
|  |  |  | Cadweld #3 |  | please add: | Cadweld
|  |  |  | Cadweld #4 |  | please add: | Cadweld
|  |  | ASB Building | Cadweld #1 |  | please add: | Cadweld
|  |  |  | Cadweld #2 |  | please add: | Cadweld
|  |  |  | Cadweld #3 |  | please add: | Cadweld
|  |  |  | Cadweld #4 |  | please add: | Cadweld
|  |  |  | Cadweld #5 |  | please add: | Cadweld
|  |  |  | Cadweld #6 |  | please add: | Cadweld
|  |  |  | Cadweld #7 |  | please add: | Cadweld
|  |  |  | Cadweld #8 |  | please add: | Cadweld
|  |  |  | Cadweld #9 |  | please add: | Cadweld
|  |  |  | Cadweld #10 |  | please add: | Cadweld
|  |  |  | Cadweld #11 |  | please add: | Cadweld
|  |  |  | Cadweld #12 |  | please add: | Cadweld
|  |  | Separator Station | Cadweld #1 |  | please add: | Cadweld
|  |  |  | Cadweld #2 |  | please add: | Cadweld
|  |  |  | Cadweld #3 |  | please add: | Cadweld
|  |  |  | Cadweld #4 |  | please add: | Cadweld
|  |  |  | Cadweld #5 |  | please add: | Cadweld
|  |  |  | Cadweld #6 |  | please add: | Cadweld
|  |  |  | Cadweld #7 |  | please add: | Cadweld
|  |  |  | Cadweld #8 |  | please add: | Cadweld
|  |  |  | Cadweld #9 |  | please add: | Cadweld
|  |  |  | Cadweld #10 |  | please add: | Cadweld
|  |  |  | Cadweld #11 |  | please add: | Cadweld
|  |  |  | Cadweld #12 |  | please add: | Cadweld

## Checklists
Type | Name | Values | Prefix | Postfix
checklist-flat | Test Equipment Details:
checkpoint-no-status | Details
textbox | Make
textbox | Model
textbox | Serial No
textbox | Calibration Expiry Date
checklist | JHA - Job Hazard Analysis
section | Job details
checkpoint-no-status | Job details
date | Date:
textbox | Permit No.
textbox | Job No.
textbox | Site
textbox | Activity Location
textbox | Asset:
textbox | Work Details:
section | Prompts for Hazards - Mark all that apply.
checkpoint-no-status | Prompts for Hazards - Mark all that apply.
tickbox | Sparks/Open flame
tickbox | Disabled safety device(s)
tickbox | Uneven surfaces
tickbox | Fatigue, over-exertion
tickbox | Crane movements
tickbox | Moving/Rotating parts
tickbox | Remote area, working alone
tickbox | Conflicting work/SIMOPS
tickbox | Electrical arc flash
tickbox | Sharp objects/materials
tickbox | Restricted/Difficult Entry/Exit
tickbox | Overhead obstacles
tickbox | Ignition sources (other)
tickbox | Access/Egress
tickbox | Water body
tickbox | Live equipment
tickbox | Slippery surfaces
tickbox | Suspended loads
tickbox | Hazardous substances (chemicals)
tickbox | Use of non-intrinsically safe equipment
tickbox | Weather extremes
tickbox | Moving vehicles
tickbox | Task related noise
tickbox | Engulfment
tickbox | General waste
tickbox | Hazardous waste
tickbox | Hazardous/toxic substance, fumes, gas
tickbox | Flammable materials - Gas, liquids, solids
tickbox | Reduced visibility, lighting
tickbox | Electricity
tickbox | Static electricity
tickbox | Work at height
tickbox | Underground services
tickbox | O2 Deficiency/Excess
tickbox | Temperature extremes
tickbox | Heavy objects
tickbox | Radiation
tickbox | Potential energy - Tension/Compression
tickbox | Flying particles/Dust/Objects
tickbox | Vehicle entry
tickbox | Exposure to process temperatures.
section | Prompts for Initial Consequences - Mark all that apply
checkpoint-no-status | Prompts for Initial Consequences - Mark all that apply
tickbox | Falling/Dropped objects
tickbox | Fall from height
tickbox | Trip/Slip/Fall
tickbox | Gas release
tickbox | Pressure release
tickbox | Struck by object
tickbox | Exceeding tool limits
tickbox | Overloading people
tickbox | Unplanned shutdown
tickbox | Exposure to O2 deficiency/excess
tickbox | Exposure to hazardous substance
tickbox | Entanglement
tickbox | Flying objects
tickbox | Loss of control
tickbox | Loss of containment
tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
tickbox | Loss of structural integrity
tickbox | Equipment failure
tickbox | Uncontrolled ignition source
tickbox | Collision
tickbox | Ignition/Fire
tickbox | Back strain/Injury
tickbox | Burns
tickbox | Heat exhaustion
section | Initial controls - Mark all that apply.
checkpoint-no-status | Initial controls - Mark all that apply.
note | People controls
tickbox | Safety/Fire watch person
tickbox | Barriers/Flagging
tickbox | Warning signs
note | Equipment controls
tickbox | Master tags and locks
tickbox | Scaffolding for access
tickbox | Radio communication
note | Environmental controls
tickbox | Ventilation
tickbox | Lighting
tickbox | Gas Testing
note | High risk controls
tickbox | WSCS Work permit
tickbox | WSCS Certificates
tickbox | Critical lift/Fall protection plan
tickbox | Specialised PPE
tickbox | Spill kit
tickbox | Fire extinguisher
section | Signatures
checkpoint-no-status | Signatures
signoff | Applicant signature
checklist | JHA - Job Step
section | Task Step - add task step for each individual task
checkpoint-no-status | Task Step - add task step for each individual task
date | Date:
textbox | Task step number (eg. Step 1, Step 2 etc):
textbox | Task details:
textbox | Hazards:
dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
textbox | Potential consequence:
textbox | Controls:
textbox | Recovery steps:
dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist | Toolbox Meeting
section | Toolbox meeting
checkpoint-no-status | Toolbox meeting
date | Date:
textbox | Meeting location:
textbox | Meeting conducted by:
textbox | Meeting attendees:
textbox | Today's work scope/Hazards
textbox | Hazard controls:
signoff | PICWS Signoff
checklist | As-Built Drawings
section | As-Built Drawings - attach scanned documents
checkpoint-no-status | As-Built Drawings - attach scanned documents
textbox | Drawing no.
checklist-flat | Cable Test Record
checkpoint | Upload completed ITR scans
checklist-flat | Earth Pegs
checkpoint | Mold type identified
dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee
checkpoint | Cadweld Visual test
note | Please attach photo
checkpoint | Cadweld Ductor test
textbox | Result:
note | Please attach photo
checkpoint | Continuity test [Peg to Earth Bar]
textbox | Result:
checkpoint | 3 Wire Earth test
textbox | Result:
note | Pass if <1 ohm
checklist-flat | Cadwelds
checkpoint | Mold type, # and cable size identified
dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee, PC 240mm SQ N/C Run to 120mm SQ TAP, TA 250mm SQ N/C Run to 240mm SQ Flex B140A Shim TAP * GAP Cable 3mm *, GT 120mm SQ N/C to 19mm Ground Rod, TA 120mm SQ N/C Run to 120mm Flex in B140A Shim TAP, TA 240mm SQ Run x TAP, TA 120mm SQ Run to 70mm TAP Horizontal Tee, TA 70mm SQ Run to 120mm TAP Horizontal Tee, TA 70mm SQ Run x TAP
dropdown | Select mold # | GTC-312C, XBQ-2C2C, TAC-2C2C, ZC-11159Z, TAC-3D2C, XAC-3D3D, ZC-11160Z, TAC-3D2V, TAC-3D3D, TAC.3Q3Q, ZC.11170Z, GTC.182V, ZC.1174Z, PCC.3Q2V, TAC.2V2G, TAC.2G2V, TAC.2G2G
dropdown | Select cable size | 50mm to 16mm Earth Rod, 50mm to 50mm Tee, 50mm to 50mm Cross, 185mm to 185mm Tee, 185mm to 120mm Tee, 185mm to 120mm Cross, 185mm to 185mm Cross, 185mm to 50mm to 50mm Cross, 50mm to 70mm, 50mm to 50mm flex Tee, 240mm to 240mm Tee, 240mm to 120mm Tee, 70mm to 70mm Tee, 70mm to 120mm Tee, 120mm to 70mm Tee
checkpoint | Cadweld Visual test
note | Please attach photo
checkpoint | Cadweld Ductor test
textbox | Result :
note | Pass if <50 micro ohms
note | Please attach photo
checkpoint | Cadweld wrapped in 3M SCOTCH 23 RUBBER, 3M TEMFLEX 1500 GREEN TAPE
note | Please attach photo
checkpoint | GPS coordinates taken
textbox | Notes:
checklist-flat | Cable Pre-installation
checkpoint | Cable Pre-Installation
tickbox | Check cable details are correct and in accordance with cable schedule.
tickbox | Cable has been tested for insulation resistance and is safe to install
tickbox | Sufficient rollers in place to prevent excessive cable rubbing, (if applicable).
tickbox | If using winch - ensure it is being used in accordance with Entec Winch SOP 2023-03
tickbox | In all cases, ensure the cable minimum bending radius is not exceeded.
tickbox | Check cable installed undamaged & cable ends are sealed to prevent the ingress of moisture.
tickbox | Cable ties, clamps, cleats etc. are of suitable type and spacing as per the requirements.
tickbox | Segregation from other electrical systems, pipes or structures has been by separation, barriers, or distance (a minimum of 300mm).
checklist | ITR-CL-1-114 - UPS Installation
checkpoint -MANDATORY PHOTO | UPS Installation
tickbox | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule.
tickbox | Check for mechanical damage.
tickbox | Panel IP rating is correct.
tickbox | Holding down arrangement and seat alignment correct.
tickbox | Panels aligned correctly.
tickbox | External bonding correct
tickbox | Phase identification correct.
tickbox | Instrument, indication lamps & interlocks correct.
tickbox | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings.
tickbox | Check Main Isolator and Bypass switch operation
tickbox | COM Interface & Mod Link.
tickbox | Padlocking facilities correct.
tickbox | Check internals for cleanliness.
tickbox | Check manual operation of selector switch, MCB, push button, etc.
tickbox | Incoming cable correctly installed, terminated & supported.
tickbox | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed.
tickbox | Drawings marked up with relevant changes and As-builts complete.
checkpoint | Test results
textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
checklist-flat | ITR-CL-1-100 General Electrical Equipment Install
checkpoint - Mandatory photo | Electrical Equipment Install
tickbox | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule.
Check all external cabling and internal wiring is correctly installed and labelled.
tickbox | Fixings are the correct type and maintain IP rating of equipment. Spare entries have been plugged with correctly certified plug.
tickbox | Installed undamaged
tickbox | All relevant drawings marked “As-Built”.
checkpoint | Test results
textbox | Earth Continuity, Earth Bond, Insulation Resistance, Phase Rotation, Polarity, Fault loop Z
checklist | ITR-CL-1-115 Lightning Protection
checkpoint - Mandatory photo | Lightning Protection Earthing system
tickbox | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007
textbox | Lightning conductor is 2 metres or more above the entire protected area
tickbox | Check the materials and equipment used for the down conductors are suitable
tickbox | Check the down conductors are routed, located and electrically bonded as required
tickbox | Check all installed components are firmly secured
tickbox | Check the method of protection against electric shock, including the measurement of distances
tickbox | Check earth termination systems are interconnected
tickbox | Check isolating and switching devices correctly located
tickbox | Check warning signs and diagrams are installed
tickbox | Check accessibility for operation and maintenance
checkpoint | Test Results
textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  | Ohm
textbox | Earth termination system resistance is correct and record value |  |  | Ohm
textbox | Record the insulation resistance of the electrical installation |  |  | MegaOhm
textbox | Continuity of the main and supplementary equipotential bonding: |  |  | Ohm
checklist | ITR-CL-1-108 ENTEC - Electrical Switch Room
checkpoint - Mandatory photo | Electrical Switchroom
tickbox | Ensure all equipment is installed in accordance with layout drawings and equipment schedule.
tickbox | Ensure all equipment is installed as per manufacturers instructions.
tickbox | Ensure there is no visible damage to installed equipment.
tickbox | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation.
tickbox | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified.
tickbox | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar.
tickbox | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar.
tickbox | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s).
tickbox | Check sealing of all cable penetration (where applicable).
tickbox | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel.
tickbox | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable).
tickbox | Confirm panel is readily accessible for inspection and maintenance.
tickbox | Equipment IP, Ex ratings correct. Check tightness for all circuit connections
tickbox | All internal cables and wiring is correctly numbered, colour coded and terminated
tickbox | Check internals for cleanliness
tickbox | Relays Metering and Protection ratings are correct as per design
tickbox | As-builts complete
checklist | ITR-CL-1-102 - Distribution Board Installation
checkpoint - Mandatory photo | Distribution Board Installation
tickbox | Inspect for mechanical damage from freight and handling
tickbox | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct.
tickbox | Check type, size and number of breakers is correct as per drawings
tickbox | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
tickbox | Confirm main isolator operates with associated switches and auxiliaries
tickbox | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
tickbox | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete
tickbox | Check sealing of all cable penetration (where applicable).
tickbox | Active, Neutral and Earth bar properly identified and labelled
tickbox | Confirm panel is readily accessible for inspection and maintenance.
checkpoint | Test Results
textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  | MegaOhms
textbox | Earth Continuity |  |  | Ohms
textbox | Earth Bond |  |  | Ohms
textbox | Fault Loop Impedance, PSSC.
textbox | RCD Test results (1/2x I, 1x I, 5x I)
textbox | Voltage and Phase Rotation
checklist | ITR-CL-1-111 Electrical earthing
Checkpoint | Electrical earthing system installation
tickbox | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built
tickbox | Ensure that all metal work is earthed as required.
tickbox | Check welding of earth bosses and associated surface finish.
tickbox | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure.
tickbox | Ensure that brazing or welding of all joints has been completed correctly.
tickbox | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses
tickbox | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating.
tickbox | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly.
tickbox | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements.
tickbox | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar.
tickbox | Ensure that earth cable identification markings are in place.
tickbox | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible.
tickbox | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable)
checkpoint | Test Results
textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
textbox | 3-Wire earth test results (If applicable).
textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
checklist-flat | ITR-CL-1-121 - Instrument Installation
checkpoint - Mandatory photo | Instrument Installation
tickbox | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet.
tickbox | Instrument is suitably rated for area. (Ex Rating, IP Rating)
tickbox | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration.
tickbox | Instrument is accessible for maintenance and clear of obstruction and debris.
tickbox | Vent lines are directed into a safe area.
tickbox | Cable/s glanded and installed correctly, IP washers fitted, cable label installed.
tickbox | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported.
tickbox | Spare entries plugged correctly, using certified plug.
tickbox | Instrument earthed in accordance with project specification.
checklist-flat | ITR-CL-1-132 - Instrument/Control Cables
checkpoint | Instrument Cable
tickbox | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
tickbox | Check dressing / cleating, cable undamaged
tickbox | Cable mechanically protected
tickbox | Cable terminated with correct lugs and crimped with the correct die.
tickbox | Screen correctly made off
tickbox | Glanding / Locknuts correctly installed.
textbox | Gland type - from: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Gland type - to: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
tickbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
checklist-flat | ITR-CL-1-104 - Low Voltage Cable
checkpoint | Low Voltage Cable
tickbox | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
tickbox | Check dressing / cleating, cable undamaged
tickbox | Check cable cores correctly identified and labelled.
tickbox | Cable terminated with correct lugs and crimped with the correct die.
tickbox | Check Armour / Screen correctly made off.
tickbox | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable)
tickbox | Glanding / Locknuts correctly installed.
textbox | Gland type - from: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
textbox | Gland type - to: |  | Haz. Area Rating
textbox | Haz. Area Cert Details.
checkpoint | Test Results
tickbox | Polarity correct
textbox | Insulation Resistance (P-P, P-N, P-E, N-E) |  |  | MegaOhms
textbox | Earth Continuity |  |  | Ohms
checklist-flat | ITR-I-44A Entec - Fibre Optic Cable
checkpoint | Fibre Optic Cable
tickbox | Verify cable type, size, colour code and tag is in accordance with the Cable Schedule.
tickbox | Check cable optical fibre loss and record data in the attached report.
tickbox | Check fibres correctly identified and labelled.
tickbox | Check fibres correctly terminated and secure.
tickbox | Upload Contractor OTDR report
checklist-flat | ITR-CL-1-103 - Schedule of Test Results DB
checkpoint | Upload completed ITR scans
checklist-flat | ITR-E-17A Entec - Electrical Cable LV Power and control cable test record
checkpoint | Upload completed ITR scans
checklist-flat | ITR-CL-1-106 - Junction Box
checkpoint | Junction Box
tickbox | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule
tickbox | Check mechanical damage
tickbox | Earthing installed correctly and as per drawing
tickbox | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable)
tickbox | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating
tickbox | Check all Cables & Cores are correctly identified
tickbox | Check internals for cleanliness
tickbox | Check manual operation of selector switch, MCB, push button, etc
tickbox | Check MCB/Fuse ratings (If applicable)
textbox | Record earth bar resistance to earth bond
checklist-flat | Test Equipment Details:
checkpoint - No status | Details
textbox | Make
textbox | Model
textbox | Serial No
textbox | Calibration Expiry Date
checklist-flat | Record of inspection
checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist-flat | Certificate of compliance
checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-flat | ITR-CL-1-122 - Instrument Calibration - Pre-Install
checkpoint | Calibration Certificate Details
textbox | Certificate No:
textbox | Customer:
textbox | Customer Address:
textbox | Instrument Location/Plant:
textbox | Instrument Range/Units:
textbox | Instrument Loop ID:
textbox | Date of Calibration:
textbox | Calibration Expiry:
checkpoint | Calibration Results
note | 4.00 mA
textbox | As Read: |  |  | mA
textbox | Correction: |  |  | mA
textbox | Notes:
note | 8.00 mA
textbox | As Read: |  |  | mA
textbox | Correction: |  |  | mA
textbox | Notes:
note | 12.00 mA
textbox | As Read: |  |  | mA
textbox | Correction: |  |  | mA
textbox | Notes:
note | 16.00 mA
textbox | As Read: |  |  | mA
textbox | Correction: |  |  | mA
textbox | Notes:
note | 20.00 mA
textbox | As Read: |  |  | mA
textbox | Correction: |  |  | mA
textbox | Notes:
checkpoint | Certified Calibration Equipment Used
textbox | Equipment:
textbox | Serial No:
textbox | Certificate No:
textbox | Date Calibrated:
checkpoint | Additional Calibration Equipment Used
textbox | Equipment:
textbox | Serial No:
textbox | Certificate No:
textbox | Date Calibrated:
checkpoint | Additional Calibration Equipment Used
textbox | Equipment:
textbox | Serial No:
textbox | Certificate No:
textbox | Date Calibrated:
checkpoint | Calibration Staff
textbox | Tested by; |  |  | Instrument Technician
textbox | Checked by; |  |  | Quality Manager
note | All above results were compared with IANZ certified reference equipment that is traceable to national and international standards.
checklist-flat | Fence Bond
checkpoint | Continuity test from Fence to Bond cable
textbox | Results: |  |  | Pass if <0.5Ω
note | Upload photo of bond connection
checkpoint | Record location of fence bond
texbox | GPS coordinates N: E:
checklist | ITR-CL-1-101A Conduit/Ducting Below Ground
checkpoint | Conduit/Ducting Installation Below Ground
tickbox | Check equipment details are correct and in accordance with the data sheet and equipment schedule.
tickbox | Check conduit cable enclosure installation is as-per design, layout drawings and specifications.
tickbox | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed.
tickbox | Confirm that there are no obstructions, and that the installation will be accessible for maintenance.
tickbox | Check all fixings are tight and secure.
tickbox | Check bends do not exceed the maximum cable bend radius.
checklist | ITR-CL-1-101B Cable Supports Above Ground
checkpoint | Cable Supports Above Ground
tickbox | Verify cable support has been installed as per relevant drawings, and is correct size and type.
tickbox | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection.
tickbox | All covers fitted if applicable.
tickbox | Check cable support structures are adequately fixed and present no hazard to personnel.
tickbox | Welded support brackets have been wire-brushed and painted to completion.
tickbox | Splice plates, barriers, earthing system secure.
tickbox | Trays / ladders, supports, brackets not interfering with other disciplines.
tickbox | Check bends do not exceed the maximum cable bending radius.
tickbox | Cables have adequate mechanical protection as and where required.
tickbox | Inspect for system rigidity, and check levels to correct plane.
tickbox | Earth bonding straps have been fitted to any sections that are split, hinged or flexible.
tickbox | Tray bonded to structure at correct locations.
textbox | Earth bonding continuity tested – record result:
checklist | ITR-CL-1-101C Cable Transits
checkbox | Cable Transits
tickbox | Transit frame installed as per drawings.
tickbox | Transit frame identification marked correctly and visible.
tickbox | Frame correctly packed with correct sized blocks and infills.
tickbox | Correct stay plates fitted (non-ferrous for single core power cables.)
tickbox | Rated insulation installed to transit (where required.)
tickbox | Cables entering and leaving transits adequately supported and protected.
tickbox | Cables pass through frames without strain on blocks.
tickbox | All cables identified on both sides of transit and visible.
checklist | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation)
checkpoint | Equipment
tickbox | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
tickbox | Equipment checked for additional items as applicable
checkpoint | Valve
tickbox | Valve Size:
tickbox | Flange type:
tickbox | Material certification correct
tickbox | Trim material correct
textbox | Rating:
textbox | Service:
tickbox | Body material correct
textbox | Leakage class:
checkpoint | Actuator
textbox | Input range: |  |  | kPa
tickbox | Failure action
tickbox | Hand wheel operation correct
checkpoint | Positioner
textbox | Signal range
textbox | Output range
checkpoint | I/P Converter
textbox | Signal range
textbox | Output range
checkpoint | Filter/Regulator/On-Off Valve
textbox | Range |  |  | kPa
textbox | Pressure setting |  |  | kPa
tickbox | Stroke Time correct
textbox | Open |  |  | sec
textbox | Close |  |  | sec
button | Open/Close times conform to commissioning specifications
checkpoint | Fail Action
dropdown | Electrical Fail Action | FO, FC, FL
dropdown | Motive Force | FO, FC, FL
checkpoint | Valve Field Calibration and Hysteresis Check
tickbox | Confirm test equipment is within calibration period prior to testing
note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
tickbox | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100%
checkpoint | Proximity Detectors
tickbox | Open switch set, correct mode setting
tickbox | Closed switch set, correct mode setting
tickbox | Electrical connections and certification correct
checkpoint | Solenoid Valve
tickbox | Operation correct
tickbox | Electrical connections correct
tickbox | Electrical certification correct
textbox | Voltage: |  |  | V
tickbox | Pneumatic connections correct
textbox | Pneumatic pressure |  |  | kPa
checkpoint | Pilot Valve
tickbox | Pneumatic connections correct
tickbox | Operation correct
tickbox | Action/Lockup
checkpoint | Hydraulic Actuator
textbox | Working pressure
textbox | Manifold pressure
textbox | Fluid type
tickbox | Hydraulic connections correct
textbox | Regulator pressure setting
tickbox | Pilot operation correct
checkpoint | Accumulator
tickbox | N2 Charge required
textbox | N2 Pre-charge pressure
textbox | Pressure switch setting
textbox | Working pressure
textbox | Output range
tickbox | Volume tank & check valve installed correctly
checkpoint | Electric Actuator
textbox | Voltage:
tickbox | Electrical certification correct
tickbox | Electrical connections correct
tickbox | Remote operation correct
tickbox | Local hand operation correct
tickbox | Torque switches and travel stops set
checkpoint | Miscellaneous Equipment
textbox | Description
textbox | Manufacturer
textbox | Model No:
textbox | Serial No:
textbox | Range:
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation)
checkpoint | Equipment
tickbox | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No.
tickbox | Equipment checked for additional items as applicable
checkpoint | Valve
textbox | Valve Size:
textbox | Flange type:
tickbox | Material certification correct
tickbox | Trim material correct
textbox | Rating:
textbox | Service:
tickbox | Body material correct
textbox | Leakage class:
checkpoint | Actuator
textbox | Input range: |  |  | kPa
tickbox | Failure action
tickbox | Hand wheel operation correct
checkpoint | Positioner
textbox | Signal range
textbox | Output range
checkpoint | I/P Converter
textbox | Signal range
textbox | Output range
checkpoint | Filter/Regulator
textbox | Range |  |  | kPa
textbox | Pressure setting |  |  | kPa
section | Fail Action
dropdown | Electrical Fail Action | FO, FC, FL
dropdown | Motive Force | FO, FC, FL
checkpoint | Proximity Detectors
tickbox | Open switch set, correct mode setting
tickbox | Closed switch set, correct mode setting
tickbox | Electrical connections and certification correct
checkpoint | Solenoid Valve
tickbox | Operation correct
tickbox | Electrical connections correct
tickbox | Electrical certification correct
textbox | Voltage: |  |  | V
tickbox | Pneumatic connections correct
textbox | Pneumatic pressure |  |  | kPa
checkpoint | Pilot Valve
tickbox | Pneumatic connections correct
tickbox | Operation correct
tickbox | Action/Lockup
checkpoint | Hydraulic Actuator
textbox | Working pressure
textbox | Manifold pressure
textbox | Fluid type
tickbox | Hydraulic connections correct
textbox | Regulator pressure setting
tickbox | Pilot operation correct
checkpoint | Accumulator
tickbox | N2 Charge required
textbox | N2 Pre-charge pressure
textbox | Pressure switch setting
textbox | Working pressure
textbox | Output range
tickbox | Volume tank & check valve installed correctly
checkpoint | Electric Actuator
textbox | Voltage:
tickbox | Electrical certification correct
tickbox | Electrical connections correct
tickbox | Remote operation correct
tickbox | Local hand operation correct
tickbox | Torque switches and travel stops set
checkpoint | Miscellaneous Equipment
textbox | Description
textbox | Manufacturer
textbox | Model No:
textbox | Serial No:
textbox | Range:
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-CL-1-128 Temperature Instrument Installation
checkpoint | Temperature Instrument Installation
tickbox | Check Instrument Nameplate details are correct in accordance with the instrument index.
tickbox | Temperature instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
tickbox | Thermowell details including flange size are correct in accordance with the specifications
tickbox | Internal depth of thermowell checked and recorded
textbox | Depth:
tickbox | Bar material and tag number stamped on thermowell flange/exposed surface
tickbox | Thermowell CE marked
tickbox | EOL resistor fitted and correctly rated where applicable
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-CL-1-129 Flow Meter Installation
checkpoint | Flow Meter Installation
tickbox | Check instrument nameplate details are correct in accordance with the instrument index
tickbox | Flow meter calibrated before installation (ITR-CL-1-123 Instrument Calibration)
tickbox | Ensure location and tapping point is verified as per P&ID & location drawings
tickbox | Ensure direction of flow is correct with respect to flow meter
tickbox | Check mechanical clearance is adequate for installation of flow meter
tickbox | Verify type and size of gasket is correct between process line and measuring unit flange
tickbox | Ensure correct nut and bolt grade and material for connecting unit to process line
tickbox | Verify display/cover is oriented for ease of use for operators and access for technicians
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-CL-1-130 Pressure Instrument Installation
checkpoint | Pressure Instrument Installation
tickbox | Check Instrument Nameplate details are correct in accordance with the instrument index.
tickbox | Pressure Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
tickbox | Instrument mounted as per hook-up drawings
tickbox | Air line/Impulse line are correct material to site specifications
tickbox | Air line/Impulse line are routed tidily and as per hook-up drawings
tickbox | Correct bolt size and material/grade used
tickbox | Local indicator is mounted and easy to read, easy access for technicians
tickbox | Instrument and tubing are adequately supported as per drawings
tickbox | Isolation valve installed
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-CL-1-131 Level Instrument Installation
checkpoint | Level Instrument Installation
tickbox | Check Instrument Nameplate details are correct in accordance with the instrument index.
tickbox | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration)
tickbox | Level instrument mounting equipment is adequately sturdy and correct materials used
tickbox | Bolts and studs are to site specification
tickbox | Ensure location and tapping point is verified per relevant drawings
tickbox | Ensure gasket and studs are used as per specifications
tickbox | Verify contact type sensor probes are installed without any resistance
tickbox | Verify antenna/source are installed correctly
tickbox | Ensure display is easily readable by operations and access is easy for technicians
signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist | ITR-CL-1-110 Generator Package (LV)
checkpoint | Generator Package (LV)
tickbox | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
tickbox | No mechanical damage and paintwork in good condition.
tickbox | Check terminal boxes and glanding correct.
tickbox | Instruments correctly installed.
tickbox | Heaters correctly installed.
tickbox | Check unit for cleanliness.
tickbox | Check manual operation of selector switches, MCB, push buttons etc.
tickbox | External cabling correctly installed.
tickbox | Protection of live parts adequate.
tickbox | Main terminal box complete and terminations correct torque.
tickbox | Ensure direction of rotation is clearly marked.
tickbox | Check gasket and seals are not damaged.
tickbox | Unused cable entries are correctly sealed.
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
textbox | Heater circuit insulation resistance:
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-CL-1-105 Control Panel
checkpoint | Control Panel
tickbox | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
tickbox | Check holding down/mounting arrangement is correct.
tickbox | Check for mechanical damage.
tickbox | Check tightness of circuit connections.
tickbox | All internal cabling and wiring is correctly numbered, colour coded and terminated
tickbox | Ammeter scale and current transformer correct.
tickbox | Check internals for cleanliness.
tickbox | Check manual operation of selector switches, MCB, push buttons, etc.
tickbox | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug
tickbox | Heaters correctly installed.
tickbox | Fuse rating correct.
checkpoint | Electrical Checks
textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-CL-1-109 Electrical Equipment Package
checkpoint | Electrical Equipment Package
tickbox | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule.
tickbox | Check equipment is correctly rated for the area.
tickbox | Check if package is complete with all accessories.
tickbox | No mechanical damage and paintwork in good condition.
tickbox | All transportation supports, stops and fastenings removed.
tickbox | Package fixing down bolts/shims/washers installed and tensioned.
tickbox | Check package is installed on a level plane.
tickbox | External cabling (if required) correctly installed.
tickbox | Internal equipment installed and all tests complete and accepted.
tickbox | Verify package using vendor and/or project P&IDs.
tickbox | Check that equipment is correctly earthed.
textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm
signoff | Installed by:
signoff | Client Representative:
checklist | ITR-CL-1-113 Motor Control
checkpoint | General Motor Control
tickbox | Check all labelling and warning signs are correctly installed and visible
tickbox | Check control equipment is clean and free from dust, debris and tools, no mechanical damage
tickbox | Check preservation and transit items are removed
tickbox | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor
tickbox | Check all cabling to control gear and motor is undamaged, supported and tidy
tickbox | Check earthing bar and connections are correct and tight
tickbox | Check incoming and outgoing power cables are terminated and glanded correctly
tickbox | Check phase identification on power cables is correct and visible
tickbox | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque
tickbox | Check all other nuts and bolts are tight
tickbox | Check spare gland entries are plugged with correct rated plugs
tickbox | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected
checkpoint | Variable Speed Drives (VSD)
note | Record VSD Details
textbox | Volts (Input)
textbox | Amps (Input)
textbox | Amps (Output)
tickbox | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input)
tickbox | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used.
tickbox | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged
tickbox | Check control signal cables use twisted pairs
tickbox | Check control signal and profibus cables shield is earthed at one end
tickbox | Check analogue and digital signals are run in separate cables
checkpoint | Voltage segregation
tickbox | Distance between input power and motor cable >300mm
tickbox | Distance between input power and control signal cable >200mm
tickbox | Distance between motor cable and control signal cable >500mm
tickbox | Check there are no power factor compensation capacitors installed on the outgoing power cables
tickbox | Check gland plates with single core power cables are non-magnetic at VSD and LIS
tickbox | Check mains voltage cannot be applied to the VSD output by means of a bypass connection
tickbox | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC
tickbox | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position)
signoff | Installed by:
signoff | Client Representative:

## Mold And Cable Info
Mold Number | GTC-312C | XBQ-2C2C | TAC-2C2C | ZC-11159Z | TAC-3D2C | XAC-3D3D | ZC-11160Z | TAC-3D2V | TAC-3D3D | ZC-11161Z | TAC.2G2C | ZC-11162Z | ZC-11163Z | GTC.312V | SSC.3D | XAC.3D2G | GTC.312G | NCR.312G | GTC.312G | NCR.312G | XAC.3D2V | PCC.3Q2V | ZC-1174Z | GTC.182V | ZC.11170Z | TAC.3Q3Q | TAC.2V2G | TAC.2G2V | TAC.2G2G
Type | GT 50mm SQ to 16mm S/S vertical rod | XBQ - 50mm SQ to 50mm SQ crossover | TA 50mm SQ Horrizontal Tee | XA 185mm N/C run to 185mm N/C4 120mm | T.A. 185mm N/C run to 50mm Horizontal Tee | X.A. 185mm N/C run to 185mm N/C Tap | X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap | T.A 185mm N/C Run to 120mm N/C Horizontal Tee | T.A. 185mm N/C Horizontal Tee | T.A 50mm conduit run to 50mm flex in B-133.2L.F Sleeve tap | T.A 70mm run to 50mm hoorizontal tee | T.A 70mm conduit run to 50mm flex in B1332LF | T.A Tinned bare 185mm run to 185mm flex in B.140A | GT 120mm N/C to 16mm vertical S/S Rod | SS 185mm N/C horizontal end splice | XA 185mm N/C run to 70mm TAP Cross | GT 70mm Run to 16mm SS rod | NC 70mm R x T on top of 16mm SS verticle rod | GT 70mm run to 16mm SS rod | NC 70mm R x T on top of 16mm SS vertical Rod | XA 185mm SQ N/S Run to 120mm SQ N/C TAP | PC 240mm SQ N/C Run to 120mm SQ TAP | TA 250mm SQ N/C Run to 240mm SQ Flex B140A Shim TAP * GAP Cable 3mm * | GT 120mm SQ N/C to 19mm Ground Rod | TA 120mm SQ N/C Run to 120mm Flex in B140A Shim TAP | TA 240mm SQ Run x TAP | TA 120mm SQ Run to 70mm TAP Horizontal Tee | TA 70mm SQ Run to 120mm TAP Horizontal Tee | TA 70mm SQ Run x TAP
Weldmetal | #90 Plus | #150 Plus | #90 Plus | #250 plus | #115 Plus | #300 Plus | #200 Plus | #200Plus | #200 plus | #90 plus | #90 plus | #115 plus | #200 Plus | #150 Plus | #150 Plus | #250 plus | #115 plus | #200 Plus | #115 Plus | #200 Plus | #250 plus | #250 Plus | #240 Plus | #200 Plus | #200 Plus | #300 Plus | #115 Plus | #115 Plus | #115 Plus
Cable size | 50mm to 16mm Earth Rod
50mm to 50mm Tee
50mm to 50mm Cross
185mm to 185mm Tee
185mm to 120mm Tee
185mm to 120mm Cross
185mm to 185mm Cross
185mm to 50mm to 50mm Cross
50mm to 70mm Tee
50mm to 50mm flex Tee
70mm to 50mm flex tee
185mm to 185mm flex tee
120mm to 16mm Earth Rod
185mm to 185mm inline join
185mm to 70mm cross
240mm to 120mm Tee
70mm to 70mm Tee
120mm to 70mm Tee
70mm to 120mm Tee