## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | ITR-CL-1-125 Cone and Thread Tubing Installation |  |  |  |  | Yes | ITR-CL-1-125 Cone and Thread Tubing Installation | 00ce8ebc-6b8e-4be1-888f-25f2efb5ad08
checkpoint-no-status |  |  | checkpoint | General Data
text | 7141cf95-5dea-5b0f-8d8c-81f196d5a59d |  | textbox | Location:
text | 255cbc42-9802-516c-a136-c042f69c7857 |  | textbox | Duty:
text | 6887b83d-bc70-53e8-b553-80544ea43fe2 |  | textbox | Reference Drawings/Hook-up drawing:
text | f71a1a13-44f7-556b-996b-2b1398f630d8 |  | textbox | Related instrument tag no:
text | 3b8c7d90-5404-50c9-9cb5-ff74c7cc5ca7 |  | textbox | Tube diameter and wall thickness:
checkpoint-status |  |  | checkpoint | Cone and Thread installation - Stainless fittings
button | d43e5bc0-c8bb-5532-b2df-b69f7cceeaed |  | button | Correct thread compatibility and engagement | Yes,N/A
button | 39be5582-98e9-5b64-bf35-b56df54e22ac |  | button | Check fitting collar prior to connection - 1 to 2 threads visible at cone | Yes,N/A
button | 11c86109-300b-5d46-bd80-5b4e8b2204b7 |  | button | Tube installation follows the client specification. (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables) | Yes,N/A
button | 6b9ea312-508f-5804-ace3-ed7b548bba4b |  | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
button | 920b9894-e0d8-5af6-80e5-a90c1b5d34f1 |  | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
checkpoint-status |  |  | checkpoint | Cone machined face. No defects, lines, bumps etc. (MANDATORY PHOTO)
label | 2f419ae7-c5f8-5b75-9102-aadd65f3b4ee |  | note | Attach photo of cone and thread.
checkpoint-status |  |  | checkpoint | Thread cleanly cut, de-burred and cleaned. (MANDATORY PHOTO)
label | 6b9e5d58-35a2-5767-8ee8-64320309ab65 |  | note | Attach photo of collar.
button | 33b6b064-7fb6-5c17-a57d-ab015a8f638f |  | button | Lubricate collar, cone and gland thread at assembly to prevent galling as required | Yes,N/A
button | 675acade-cf00-58b2-be9e-8c885504bf48 |  | button | Correct Tube nut used for the right sized tube | Yes,N/A
label | 6390f66d-ee7b-532c-a0cc-ae3ab696094e |  | note | Ensure No thread tape or sealant are used on tube nuts | Yes,N/A
button | 7bcc3afc-9160-54a2-9b81-be483b83d27a |  | button | Tube fitting hex torqued to ensure correct tightness, marked with pen | Yes,N/A
button | f354ef76-4789-5085-ad39-925286a57219 |  | button | Ensure Weep hole is unobstructed and clean | Yes,N/A
button | dfb2e174-954a-5a61-b637-6609eb938380 |  | button | In service leak test performed and passed | Yes,N/A
button | 1126d282-7850-5605-aa0d-367ec4066b64 |  | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-sectioned |  |  | checklist | MSDS |  |  |  |  | Yes | MSDS | 04fa8306-4590-489a-ae2b-9fc9f178f2e9
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Please Upload MSDS Sheets
checklist-flat |  |  | checklist | ITR-CL-1-121 Instrument Installation |  |  |  |  | Yes | ITR-CL-1-121 Instrument Installation | 0cc3ea88-445e-485f-bca3-95a81194646f
checkpoint-status |  |  | checkpoint | Instrument Installation (Mandatory Photo)
button | 1012254a-4972-5fdc-8d71-df31d7dadfa9 |  | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
button | 0c741fc8-02f3-53e1-ab33-06f15918df18 |  | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
button | 54a6e2ff-164b-58bf-8867-c6cb5e7af121 |  | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
button | 8a3d1bdb-9159-5dbd-aea9-7619d3191e3a |  | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
button | 60d133f8-3ef0-50a2-9179-acecbf0cbeb6 |  | button | Vent lines are directed into a safe area. | Yes,N/A
button | d050cc4f-30ba-5466-b4b8-df2714d53a47 |  | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
button | 7f312423-2e54-5722-97cc-15062feec468 |  | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
button | daaa6797-cafb-5a0f-85ad-b402e355489f |  | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
button | d21240e8-c68e-5dae-bad1-45031304c583 |  | button | Instrument earthed in accordance with project specification. | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-101B Cable Supports Above Ground |  |  |  |  | Yes | ITR-CL-1-101B Cable Supports Above Ground | 135f4eec-4a78-4115-a754-bbd07ee0c11b
checkpoint-status |  |  | checkpoint | Cable Supports Above Ground
button | 545ba4b9-3ca9-53bf-a8c1-33531ac2922f |  | button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
button | 08f6bbce-68f2-5214-8e82-3c09cc89da33 |  | button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
button | 9de24e4f-cfa4-5a4b-8afd-73762a459057 |  | button | All covers fitted if applicable. | Yes,N/A
button | ee6eb51c-4cb0-5ff4-9fa1-fd6a361665c8 |  | button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
button | 49004d30-ee0f-51e2-a510-d838e09c10af |  | button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
button | 2c5500c2-0096-57dc-a19a-400a00138f91 |  | button | Splice plates, barriers, earthing system secure. | Yes,N/A
button | d9b9bf78-2d3f-5724-9afc-22cf8925fff5 |  | button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
button | 9e40b1d4-5f40-562f-9287-d94c46168b0f |  | button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
button | 63a588ab-dc2c-5420-985d-41d2e43f6907 |  | button | Cables have adequate mechanical protection as and where required. | Yes,N/A
button | 18d95617-e1a5-5897-8fc6-86d92bd4e5cb |  | button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
button | 94fbde4f-136d-5a56-bfde-952c6a4e7848 |  | button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
button | 2f2f2852-6611-5582-bbe2-bd5b29ac5e2a |  | button | Tray bonded to structure at correct locations. | Yes,N/A
button | cda96ee6-f7a6-59c5-b81f-8011bd5bec87 |  | button | Earth bonding continuity tested – record result: | Yes,N/A
checklist-flat |  |  | checklist | ITR-CL-1-100 General Electrical Equipment |  |  |  |  | Yes | ITR-CL-1-100 General Electrical Equipment | 14193213-b5e0-490f-a909-27e7755074d1
checkpoint-status |  |  | checkpoint | General Electrical Equipment
button | cb2b4f97-7bb6-5cdf-b568-f35972d86f61 |  | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | 60cf451e-2147-50f0-878e-d1d58401ec15 |  | button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | ff7f4f22-5a01-5101-8163-c5d80786d1b0 |  | button | Installation is clean and tidy | Yes,N/A
button | 2a27440d-8e2b-56e8-981f-798dd378e5f3 |  | button | Mounting arrangement correct | Yes,N/A
button | 39d43819-935f-5663-bd11-12aa8755583f |  | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
button | e1c8e2c4-6fdd-52ac-b0b3-1dcd9dc10b14 |  | button | External cabling is correctly installed and labelled. | Yes,N/A
button | 3f4f40a8-a7c7-52ba-88eb-0ed6855575f0 |  | button | Check that Equipment is correctly earthed. | Yes,N/A
button | af3cd66c-f354-5542-9f6d-342aeecff850 |  | button | Check gland, plate, frame & door earth continuity | Yes,N/A
button | 1659b601-6c2b-50b6-9175-44f9de00b359 |  | button | All spare entries blanked off with correct plugs. | Yes,N/A
button | aaf24b8e-ed4c-50b7-a7e2-48d43fa4947d |  | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
button | 37da6b30-7a6e-5253-b41a-d9a2a5a1b4a8 |  | button | Conforms to Specifications and Drawings. | Yes,N/A
button | af731ba5-7686-5fc4-a623-04a38d5c3ff6 |  | button | As-builts complete. | Yes,N/A
checkpoint-status |  |  | checkpoint | Electrical Checks
text | a9832c0e-7740-56da-a183-cf3080831d45 |  | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  | MegaOhms
holdpoint |  |  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-107 Heat Tracing Circuit |  |  |  |  | Yes | ITR-CL-1-107 Heat Tracing Circuit | 17fd04e1-8427-40d9-b33f-e88aaaf2d702
checkpoint-status |  |  | checkpoint | Heat Tracing Circuit
button | f0a55675-6e06-5319-931c-d84f849fe50b |  | button | Circuit installed, connected & identified according to design drawings. | Yes,N/A
button | 1dd2bd0a-28f6-52e7-924d-4b8c31c44e5b |  | button | End caps and connection kits correctly installed. | Yes,N/A
button | f0254351-98f8-5421-9a2c-2bd73c9d2a20 |  | button | All junction boxes properly supported, and all cables protected against sharp edges. | Yes,N/A
button | 997c8955-f08b-575e-8fdd-2e7ca677b1bb |  | button | Cable termination and glanding at all junction boxes correct. | Yes,N/A
button | b9630306-2879-57d0-bbd6-d4fc782eee4c |  | button | All spare entries blanked off correctly. | Yes,N/A
text | 7b96e0b9-f07a-5593-b29f-5ac940bbb33e |  | textbox | IR test: Phase - Earth, Phase - Neutral | Yes,N/A
button | f94780da-b851-5167-81f5-7b59c66cf3bf |  | button | Equipment certification meets the area classification requirements. | Yes,N/A
button | a0d2760e-0c76-5f68-89cf-85c50306a06c |  | button | Confirm warning labels are fixed on outside of pipe lagging | Yes,N/A
checkpoint-status |  |  | checkpoint | Electrical tests
text | 4f89bd2a-fca3-515b-a040-451bbb38e09e |  | textbox | Insulation Resistance: Phase - Earth
text | 5962cbe2-2039-58a0-a14c-ef598aba88c5 |  | textbox | Insulation Resistance: Phase - Neutral
holdpoint |  |  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-106 - Junction Box |  |  |  |  | Yes | ITR-CL-1-106 - Junction Box | 1bb9b0d9-43cd-498e-aaf0-910e249fcfc4
checkpoint-status |  |  | checkpoint | Junction Box
button | 245cf2c2-93e7-55f4-8b8f-084910184ab1 |  | button | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule | Yes,N/A
button | e3722cc5-e37c-5219-9ad3-e6af0c0e3bdc |  | button | Check mechanical damage | Yes,N/A
button | 8d4f6c79-ed60-5205-9480-609b73d9bea3 |  | button | Earthing installed correctly and as per drawing | Yes,N/A
button | 8cfd38ca-9728-5203-8826-00aa47888d5f |  | button | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable) | Yes,N/A
button | 216f195f-1635-5eb8-ae32-8039ae13c07a |  | button | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating | Yes,N/A
button | 1ee44d58-4ef0-524c-9c0b-6cf1d43db717 |  | button | Check all Cables & Cores are correctly identified | Yes,N/A
button | 5319ace1-7c03-56db-a539-1b75be9081de |  | button | Check internals for cleanliness | Yes,N/A
button | 68ff54a5-b7c5-5162-aa43-cc806b8cf101 |  | button | Check manual operation of selector switch, MCB, push button, etc | Yes,N/A
button | bee4f161-e6b7-54db-b47d-7cb9ac72ffbc |  | button | Check MCB/Fuse ratings (If applicable) | Yes,N/A
text | 72788ef3-35a9-597e-aa86-40956951b878 |  | textbox | Record earth bar resistance to earth bond
checklist-flat |  |  | checklist | ITR-CL-1-127 Telecommunications Equipment Panel |  |  |  |  | Yes | ITR-CL-1-127 Telecommunications Equipment Panel | 1ce40f69-e19b-42ab-ac97-9984bdce9de8
checkpoint-status |  |  | checkpoint | Telecommunications Equipment Panel
button | 484f6359-9b8f-514e-ba92-38eb94aff49f |  | button | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings: | Yes,N/A
button | 19e9f9b1-d7c3-5daf-b1f0-fb51ee88b1b4 |  | button | Check tag number is in accordance with Telecommunications Equipment List. | Yes,N/A
button | 12f8ffc5-c8e6-55f5-9522-76a209bd3e60 |  | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
button | 936ffdf6-019d-527d-99ec-4e8a7ea64003 |  | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
button | 012a506c-b61a-55c4-8ea9-fa509bbb8ecf |  | button | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified. | Yes,N/A
button | 849f4624-9b10-50af-b750-6f5365a1266e |  | button | Check panel air vents are clean and free of dust and dirt. | Yes,N/A
button | 27341d97-8db3-512a-8b5e-bfa4629b0fc5 |  | button | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | 512848cc-59c8-57dd-9043-e46615bf02fa |  | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
button | 8c99f84b-0bbb-5acc-bb39-35d6e62b3517 |  | button | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
button | ceb55166-fde4-5dbd-97cf-f2ddde176c60 |  | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | 27bd8155-5aaf-5348-b08b-d3d172ebdbcd |  | button | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel. | Yes,N/A
button | 9e4c60d9-10b1-5af2-8aaf-48920f19ce54 |  | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
button | def6d813-ea1c-5313-b111-fc49eecac804 |  | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
checklist-flat |  |  | checklist | Cadwelds |  |  |  |  | Yes | Cadwelds | 22357ef9-3286-45e8-b48e-b1ef6305960a
checkpoint-status |  |  | checkpoint | Mold type, #, and cable size identified
select | 40a98fe5-15bc-5b62-9405-849c2ef315bb |  | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee, PC 240mm SQ N/C Run to 120mm SQ TAP, TA 250mm SQ N/C Run to 240mm SQ Flex B140A Shim TAP * GAP Cable 3mm *, GT 120mm SQ N/C to 19mm Ground Rod, TA 120mm SQ N/C Run to 120mm Flex in B140A Shim TAP, TA 240mm SQ Run x TAP, TA 120mm SQ Run to 70mm TAP Horizontal Tee, TA 70mm SQ Run to 120mm TAP Horizontal Tee
select | ae92e117-f81d-5c93-9033-e70a5ac2c5ac |  | dropdown | Select mold # | GTC-312C, XBQ-2C2C, TAC-2C2C, ZC-11159Z, TAC-3D2C, XAC-3D3D, ZC-11160Z, TAC-3D2V, TAC-3D3D, TAC.3Q3Q, ZC.11170Z, GTC.182V, ZC.1174Z, PCC.3Q2V, TAC.2V2G, TAC.2G2V
select | 45b392c8-2f90-53e9-8837-a0a0439583d9 |  | dropdown | Select cable size | 50mm to 16mm Earth Rod, 50mm to 50mm Tee, 50mm to 50mm Cross, 185mm to 185mm Tee, 185mm to 120mm Tee, 185mm to 120mm Cross, 185mm to 185mm Cross, 185mm to 50mm to 50mm Cross, 50mm to 70mm, 50mm to 50mm flex Tee, 240mm to 240mm Tee, 240mm to 120mm Tee, 70mm to 70mm Tee, 70mm to 120mm Tee, 120mm to 70mm Tee,
checkpoint-status |  |  | checkpoint | Cadweld Visual test
label | 59be31a2-a63b-588c-a157-54fcb1f30061 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld Ductor test
text | ef019124-db6d-565b-aad7-7114c8ec0c8e |  | textbox | Result :
label | da34ba6a-d319-56c4-9f23-11f515aaad6c |  | note | Pass if <50 micro ohms
label | 9b3d3c3e-1783-56c7-a717-1dbc6605fe42 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld wrapped in 3M SCOTCH 23 RUBBER, 3M TEMFLEX 1500 GREEN TAPE
label | 8239a98c-09c8-5018-90f7-2eedd28c9648 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | GPS coordinates taken
text | 8b4f2217-7918-5ab5-908e-5e698ff03bb2 |  | textbox | Notes:
checklist-flat |  |  | checklist | Certificate of compliance (COC) |  |  |  |  | Yes | Certificate of compliance (COC) | 24ce6696-f439-40e7-8bb2-9270022a8517
checkpoint-status |  |  | checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-flat |  |  | checklist | Record of Inspection (ROI) |  |  |  |  | Yes | Record of Inspection (ROI) | 28bd5556-61ec-4802-a838-dff089b564b7
checkpoint-status |  |  | checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist-flat |  |  | checklist | ITR-CL-1-116 Fire and Gas Detection Alarms |  |  |  |  | Yes | ITR-CL-1-116 Fire and Gas Detection Alarms | 292d8202-ecb8-4b67-8e73-e1a08a78f61b
checkpoint-status |  |  | checkpoint | Fire and Gas detection alarms
text | 91f7b1d3-927a-5fc1-9922-bc889c00505c |  | textbox | Make and Model
text | f74503eb-f8b8-5f8e-b15b-bc3a87d9ea8a |  | textbox | Type
button | 5e850025-09cc-5119-915a-620b56b44ce0 |  | button | Location correct as per drawings | Yes,N/A
button | 8b274b91-c78c-587a-b0e8-39b43622205c |  | button | Component & Type / Model correct per equipment schedule | Yes,N/A
button | d7a2ddc7-5046-5fa7-8d29-7be80745b4dd |  | button | Cable connection & termination correct | Yes,N/A
button | 8db5056c-243d-5516-a00c-13058274d2c3 |  | button | Installation free of mechanical damage and clean | Yes,N/A
button | 0ce5a0e7-0835-5d7d-997b-7463dc6ec51e |  | button | Glanding correct and spare entries plugged with correctly rated plug | Yes,N/A
button | ad343b60-f41d-54d7-a669-217ebad820be |  | button | E.O.L Installation | Yes,N/A
button | 10a1d75d-7f45-549f-ae11-b119f9100343 |  | button | Test tubing installation | Yes,N/A
button | 16a9ac87-3d01-5ae4-b987-e759bbbf1289 |  | button | Detection Path Clear | Yes,N/A
checkpoint-status |  |  | checkpoint | Inspection
text | 90a3b868-54d7-5ada-b1b3-d1cf777ceca2 |  | textbox | Tag No.
text | 748cea45-9cca-57af-8ec8-1452e3e9e996 |  | textbox | RX Tag No:
button | bdc38525-5b3f-5bef-9b2a-6d376212e844 |  | button | Area Classification correct | Yes,N/A
text | 96e54638-45c0-57d7-bc02-07452460aa8b |  | textbox | Hazardous Area Certificate:
text | d4d1741e-bff6-5186-b897-df18213d20a0 |  | textbox | Detector Type:
text | a8e6f72e-0e9d-5a3a-8251-8461ff0dadb2 |  | textbox | Gas Type:
text | dc36ed29-eb76-5be6-82d8-6065c51d4cc2 |  | textbox | Supply Voltage:
text | 6489be0d-16ce-5477-b392-be1e7b98d1c2 |  | textbox | Output Signal:
checkpoint-status |  |  | checkpoint | Functional Check
button | 94fbb7c7-03dc-5b8c-b852-90e5415b1f35 |  | button | Self Test | Yes,N/A
button | 103afaec-87cc-596d-b875-68318384ef65 |  | button | Alarm Operation | Yes,N/A
button | eefdd49b-785e-5e37-b0c0-50283fdb91f5 |  | button | Fault Relay Operation | Yes,N/A
text | 18957424-83c6-5d83-9bbe-1169bdce9e22 |  | textbox | Measured output (clear path)
text | 1b23ccee-71d3-56c0-9249-3592d9153ad6 |  | textbox | Measured output (blocked path)
text | 0ad6eb12-6904-568e-b578-63d2ce00b169 |  | textbox | Measured output (filter in place)
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-110 Generator Package (LV) |  |  |  |  | Yes | ITR-CL-1-110 Generator Package (LV) | 361649cb-faf0-4ee1-ba92-fc011acccdbe
checkpoint-status |  |  | checkpoint | Generator Package (LV)
button | e6fbe5d1-989b-5a7e-b072-80dc518b5d7e |  | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | e9c3bab9-6b0a-50d1-9266-6b9eff330218 |  | button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | ac81d7b6-fbb0-55a6-9705-74febf2117b2 |  | button | Check terminal boxes and glanding correct. | Yes,N/A
button | 43aaa178-860c-5c80-9eb2-b1fedb98d454 |  | button | Instruments correctly installed. | Yes,N/A
button | 3f2812c3-0080-5af8-b515-1c8bbb556654 |  | button | Heaters correctly installed. | Yes,N/A
button | c0e1f9e1-d4ae-5cc6-9d5e-1670fb4f81d7 |  | button | Check unit for cleanliness. | Yes,N/A
button | c04fb45e-b6a6-5b3f-be27-d7d74e800f98 |  | button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
button | 8f2c4e75-2f9e-54ec-b5fc-f2eb0b40183e |  | button | External cabling correctly installed. | Yes,N/A
button | d349a7dc-022f-5b37-b638-395c086a5f48 |  | button | Protection of live parts adequate. | Yes,N/A
button | ab32df2f-ff8b-59a0-910c-73386532b64c |  | button | Main terminal box complete and terminations correct torque. | Yes,N/A
button | 3302ba7c-ca89-506d-b543-2d6436452c85 |  | button | Ensure direction of rotation is clearly marked. | Yes,N/A
button | f809155e-fd49-55cd-b27d-40689fb303cc |  | button | Check gasket and seals are not damaged. | Yes,N/A
button | c7f299c2-ab94-5e6b-893a-f06d46279e6d |  | button | Unused cable entries are correctly sealed. | Yes,N/A
checkpoint-status |  |  | checkpoint | Electrical Checks
text | 1a8692e3-b3a0-55c9-8688-c459a400bd8b |  | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
text | 0b143cde-a7c2-5c3e-82b7-a93cb5550b3f |  | textbox | Heater circuit insulation resistance:
holdpoint |  |  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-130 Pressure Instrument Installation |  |  |  |  | Yes | ITR-CL-1-130 Pressure Instrument Installation | 3cf0276d-2fba-4cc9-b588-eb474a05a621
checkpoint-status |  |  | checkpoint | Pressure Instrument Installation
button | 3551c246-6b6b-5e9e-b168-09e9da476d8c |  | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
button | 9bac761e-4fd1-59f5-a25c-77efd674b87a |  | button | Pressure Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
button | 1a2f2ebd-21bf-59d5-93f8-de0becef9f63 |  | button | Instrument mounted as per hook-up drawings | Yes,N/A
button | 0207d236-be36-57d4-a64d-492b83b4ce92 |  | button | Air line/Impulse line are correct material to site specifications | Yes,N/A
button | ed2879d7-7bdc-55ba-88c1-b177386890a1 |  | button | Air line/Impulse line are routed tidily and as per hook-up drawings | Yes,N/A
button | 6ce27fe2-de24-57b7-b477-4fd4ddbb6236 |  | button | Correct bolt size and material/grade used | Yes,N/A
button | 87d4819e-9699-57b5-a505-c6ba0a9c6515 |  | button | Local indicator is mounted and easy to read, easy access for technicians | Yes,N/A
button | 95901383-a398-57fe-917c-498e0f9b050f |  | button | Instrument and tubing are adequately supported as per drawings | Yes,N/A
button | 32276249-0f52-5741-863f-5d512f6e0457 |  | button | Isolation valve installed | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-124 Commissioning Instruments |  |  |  |  | Yes | ITR-CL-1-124 Commissioning Instruments | 3e290253-a02e-4231-99db-f4ef9ff733a8
checkpoint-status |  |  | checkpoint | Required Data
text | 7d782c52-bbaa-504f-a90d-8788404f7508 |  | textbox | Instrument range:
button | 759396e7-a65e-5b5d-bfde-afdd21fdd322 |  | button | Installation complete | Yes,N/A
button | 32fdef0f-346b-52b6-b9dd-bcc8b2ea83d9 |  | button | Point-to-point | Yes,N/A
button | 1d10c968-6216-5936-8f24-5d70acc19c2b |  | button | Haz. Inspected | Yes,N/A
button | ddb0305c-1859-54dc-99f4-287a62ae8a8a |  | button | Tag correct | Yes,N/A
button | 2b8bbdd7-9ffc-5fad-809f-29d35a4b5514 |  | button | Hook-up correct | Yes,N/A
checkpoint-status |  |  | checkpoint | Alarms & Set points
checkpoint-no-status |  |  | checkpoint | Alarm Lo
text | 39ed4655-2862-588c-a3b1-153d512e527e |  | textbox | Activated:
checkpoint-no-status |  |  | checkpoint | Alarm Lo-Lo
text | 651f931f-b1a4-5b08-a49d-c2cb17ce66f5 |  | textbox | Activated:
checkpoint-no-status |  |  | checkpoint | Alarm Hi
text | 74d6c4a9-b6b2-5e02-b52c-839395a706c7 |  | textbox | Activated:
checkpoint-no-status |  |  | checkpoint | Alarm Hi-Hi
text | be9d0b2e-14c9-5375-8f6a-e84a29a6505d |  | textbox | Activated:
checkpoint-no-status |  |  | checkpoint | Set Point 1
text | be81ac26-8dcc-5ac5-8b01-d8277febae29 |  | textbox | Activated:
checkpoint-no-status |  |  | checkpoint | Set Point 2
text | cd52fb7d-5e3b-5a43-b82c-5acecbdba150 |  | textbox | Activated:
checkpoint-no-status |  |  | checkpoint | Set Point 3
text | 20dcee58-d50d-5e32-b540-749665832549 |  | textbox | Activated:
checkpoint-no-status |  |  | checkpoint | Set Point 4
text | 957a2329-e4e4-5280-b20f-203083a54a14 |  | textbox | Activated:
checkpoint-status |  |  | checkpoint | Calibration settings
text | 408edc55-83c2-5e4f-82e9-1175ffc54db0 |  | textbox | Zero
text | 56d1d0ef-0eab-5bdf-bba7-5a3960989452 |  | textbox | Range
text | e0e4a04e-ff82-5a4a-a5bd-6b458db51718 |  | textbox | Other (Specify)
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-131 Level Instrument Installation |  |  |  |  | Yes | ITR-CL-1-131 Level Instrument Installation | 3e790364-1af4-431b-b7fa-0943e10f712f
checkpoint-status |  |  | checkpoint | Level Instrument Installation
button | cb30df0e-b480-5026-8139-809f2feb861e |  | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
button | a3c4b616-52ed-524a-a54c-5a33cf1c7e6d |  | button | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
button | be629b31-5e80-55b1-8d2e-e063834710b6 |  | button | Level instrument mounting equipment is adequately sturdy and correct materials used | Yes,N/A
button | 5e6da57c-3caf-50b2-9afd-49e3456a6a9a |  | button | Bolts and studs are to site specification | Yes,N/A
button | 9af8105c-9d64-58c2-ae6f-c6aa3c928578 |  | button | Ensure location and tapping point is verified per relevant drawings | Yes,N/A
button | 0363c507-fc6b-5a10-9f56-544a45013556 |  | button | Ensure gasket and studs are used as per specifications | Yes,N/A
button | 8b14497a-acf8-579b-b824-7b51bb902980 |  | button | Verify contact type sensor probes are installed without any resistance | Yes,N/A
button | a760aff2-422b-5236-81f7-a9621af1693e |  | button | Verify antenna/source are installed correctly | Yes,N/A
button | 734d1561-7cff-5d9e-add6-f610b703003e |  | button | Ensure display is easily readable by operations and access is easy for technicians | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-122 Instrument Calibration |  |  |  |  | Yes | ITR-CL-1-122 Instrument Calibration | 4966f07b-27cb-42ce-8980-e4f069c956f5
checkpoint-no-status |  |  | checkpoint | Required Data
text | 41757319-167a-5cd8-aa07-c7199b9ba8d1 |  | textbox | Type and Size:
text | 42e7d429-c339-5e32-90b0-dff5c5fa554d |  | textbox | Make and Model:
text | 9525ed89-0474-5d44-8ff0-3f1f965963c5 |  | textbox | Serial No:
text | 5f6e8c41-a08b-5394-94f3-dfaee7420291 |  | textbox | Instrument Type:
text | ef6e8d81-b952-543e-b989-618e5fc54fce |  | textbox | Instrument designation/equipment no
text | 013ed506-2f7b-5333-b447-51c85cc51039 |  | textbox | Calibration interval
text | b514c3b3-3339-571b-bb05-9d42ed54d281 |  | textbox | Calibration method
text | 92652948-f8e5-5c46-aac9-dc8673169287 |  | textbox | Calibrated at
checkpoint-status |  |  | checkpoint | Instrument Power Supply
select | e3a84c82-da34-5d47-8dd7-17426f6e7f45 |  | dropdown | Supply type | VAC, 2 Wire DC, Other, None
text | 487fbee1-964d-5c75-8eaa-c3d60db995b2 |  | textbox | Supply value:
button | 8d9f507d-31de-553a-8602-8f512697a4b5 |  | button | Calibration sheet completed and attached below | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-114 UPS Installation |  |  |  |  | Yes | ITR-CL-1-114 UPS Installation | 5a227d54-ee2b-4a72-957c-b14c075e97ee
checkpoint-status |  |  | checkpoint | UPS Installation (Mandatory Photo)
button | 655d03c8-7681-5332-9444-21a0283d5354 |  | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
button | ed9c1d95-9a89-57cc-8d03-1f0d8b36ff8a |  | button | Check for mechanical damage. | Yes,N/A
button | aea841e9-31ab-539f-872a-1044ac154d25 |  | button | Panel IP rating is correct. | Yes,N/A
button | 397fc40c-7a69-5ef2-b67d-09213ffe7cd1 |  | button | Holding down arrangement and seat alignment correct. | Yes,N/A
button | 262740ab-cdd3-5090-9149-ba920db5d195 |  | button | Panels aligned correctly. | Yes,N/A
button | 1c9ce2cf-65ed-5c1a-b678-dd6e6b26c32d |  | button | External bonding correct | Yes,N/A
button | b3e5c818-c5cc-5e49-8587-92d32e461ac7 |  | button | Phase identification correct. | Yes,N/A
button | e5ac5a6a-a284-5786-b72e-f99a363362e6 |  | button | Instrument, indication lamps & interlocks correct. | Yes,N/A
button | 227fdf0c-9120-58b7-a162-b64a01cabd0c |  | button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
button | 64594450-bd12-5ca3-b334-388aedfe47eb |  | button | Check Main Isolator and Bypass switch operation | Yes,N/A
button | de0d11ea-7945-52d1-a887-d18d09663978 |  | button | COM Interface & Mod Link. | Yes,N/A
button | e828b151-e799-55a6-8ca1-70b7061ef18c |  | button | Padlocking facilities correct. | Yes,N/A
button | 3fdce359-213a-5841-8809-e3ad8cf1f943 |  | button | Check internals for cleanliness. | Yes,N/A
button | 1c2b202d-3598-524f-8900-035008717f05 |  | button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
button | 4b09e7bb-403c-50e2-9f20-7893df9d86c5 |  | button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
button | 37d878a1-cbae-520f-8189-62138a287e44 |  | button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
button | 0bf69a78-986b-51cb-8425-f587f1c40d47 |  | button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
checkpoint-status |  |  | checkpoint | Test results
text | c7229fd8-3143-5995-ac3a-94e91ae24239 |  | textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
checklist-flat |  |  | checklist | ITR-CL-1-101C Cable Transits |  |  |  |  | Yes | ITR-CL-1-101C Cable Transits | 667bc55a-9926-4208-be86-a713f81a2462
checkpoint-status |  |  | checkpoint | Cable Transits
button | 51b8c413-f37a-5297-b0b4-21d5691f4593 |  | button | Transit frame installed as per drawings. | Yes,N/A
button | 96467c01-a9ec-5277-bc40-fd9e3023e7a6 |  | button | Transit frame identification marked correctly and visible. | Yes,N/A
button | 21c75966-42d8-5280-a54d-21e841a37bbb |  | button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
button | 2f69ee43-4b4f-592f-a137-d72a6e2e14f5 |  | button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
button | 8a5cd616-5189-5ed3-aed7-bdeae1ecace4 |  | button | Rated insulation installed to transit (where required.) | Yes,N/A
button | f7647de3-9241-5a92-b7f5-717e39d07ab8 |  | button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
button | 48ddf984-809a-5360-8ed9-1ba660247247 |  | button | Cables pass through frames without strain on blocks. | Yes,N/A
button | 4b79551f-3b55-583c-9900-01559e09ee55 |  | button | All cables identified on both sides of transit and visible. | Yes,N/A
checklist-sectioned |  |  | checklist | Entec Daily Report |  |  |  |  | Yes | Entec Daily Report | 6824792f-7509-472f-a313-9a59df9ee507
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Daily Report
date | 56c74d02-2feb-5793-b9b6-1d52c994a8f6 |  | date | Date:
text | 857a0e69-b296-5371-b5fb-4fa741ad2ea6 |  | textbox | Site:
text | 658fedb9-dfce-5a7f-97b3-e07cfd381bea |  | textbox | Work completed:
text | b275ad11-385a-5887-957c-c661c3c5901e |  | textbox | Issues:
text | 19fbd79d-4e0d-57e8-ad1d-75d6c069af21 |  | textbox | Weather:
text | d7a1c016-ea44-5de1-96dc-5603c9a96894 |  | textbox | Labour:
text | 70900bee-f8a7-56e8-8315-77529c7db7df |  | textbox | Plant & Equipment used:
holdpoint |  |  | signoff | Signed/Approved:
checklist-flat |  |  | checklist | ITR-CL-1-111 Electrical earthing |  |  |  |  | Yes | ITR-CL-1-111 Electrical earthing | 77ef43d3-6664-4ec0-a1ec-26f7e4f325f5
checkpoint-status |  |  | checkpoint | Electrical earthing system installation
button | ed5cbec0-bbd9-5717-afa2-bbabadab2ad8 |  | button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
button | e9879619-f120-55be-8d65-9857f7539397 |  | button | Ensure that all metal work is earthed as required. | Yes,N/A
button | 40b4f2a2-bc56-50bb-b7e4-4311ee8e416d |  | button | Check welding of earth bosses and associated surface finish. | Yes,N/A
button | 012de3bc-21f3-555d-94c1-169b7f7d57af |  | button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
button | 30fbe546-1267-58a8-8b54-ec3ee26c26f8 |  | button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
button | 2e0a11fa-cb2b-5e15-9e21-8f7d322eb8df |  | button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
button | 7795a8c6-9b99-560e-8c3e-4a1637f7e9bf |  | button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
button | 03714326-861f-5bc9-9980-6d59b15a4973 |  | button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
button | eedc87cc-fe78-5415-af66-eb35afa8d051 |  | button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
button | 27a7a44b-94e5-5483-91c5-3d5da631d8aa |  | button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
button | ac7a48ae-b931-5d99-80eb-aaf2424ab844 |  | button | Ensure that earth cable identification markings are in place. | Yes,N/A
button | 673bd3b5-a328-596b-ba6e-9f804e3743d7 |  | button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
button | 8ae72d1d-24bb-55b5-b953-9000650101a0 |  | button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
checkpoint-status |  |  | checkpoint | Test Results
text | 9fb6c93b-c93d-5301-8726-b7b7ba5927a7 |  | textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
text | e0acc7d5-ee0d-557f-a05b-651fb56d3458 |  | textbox | 3-Wire earth test results (If applicable).
text | 930891ae-e43d-5ca6-86d5-adf9a95d195c |  | textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
checklist-flat |  |  | checklist | ITR-CL-1-102 Entec - Distribution Board Installation |  |  |  |  | Yes | ITR-CL-1-102 Entec - Distribution Board Installation | 7e93daa2-824a-4620-aca5-71634695e990
checkpoint-status |  |  | checkpoint | Distribution Board Installation (Mandatory Photo)
button | dd10045f-7c02-5b32-ba7d-bb204fc01509 |  | button | Inspect for mechanical damage from freight and handling | Yes,N/A
button | 36b5b6df-dbf1-54ba-8e0b-10de26e2b947 |  | button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
button | 60623dbb-82b8-5d8e-a013-e2c297e0caed |  | button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
button | e41011e6-c5d0-5d9d-bb0f-5df48dc6e223 |  | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
button | 0fdd7ef1-fea1-566e-b9f8-11dc9089b254 |  | button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
button | be177262-355d-5f6f-a945-678a725568c9 |  | button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | d46d2cc9-6446-596d-8fa6-c45c72ec9df2 |  | button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
button | 274fc4ae-0c46-5b8c-ad55-393f1c953843 |  | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | 5fad4a36-6295-5402-89f8-c583977a29e9 |  | button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
button | 232f2992-9a08-58cc-9ab7-49d9bbb97d1b |  | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
checkpoint-status |  |  | checkpoint | Test Results
text | 2845f34a-33d7-5508-8ec2-13c4edd2f9e1 |  | textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  | MegaOhms
text | 35dd8359-22f7-53ce-a056-50f64edb0e79 |  | textbox | Earth Continuity |  |  | Ohms
text | 3fa14140-bdf5-566b-904a-595c31dfe6d2 |  | textbox | Earth Bond |  |  | Ohms
text | 5d57d622-bdb7-59eb-bd68-fd952363ad21 |  | textbox | Fault Loop Impedance, PSSC.
text | dc872782-c03d-5f2f-ab18-f61d35777b0e |  | textbox | RCD Test results (1/2x I, 1x I, 5x I)
text | e7372391-e24a-5c79-a513-67117cff418c |  | textbox | Voltage and Phase Rotation
holdpoint |  |  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-113 Motor Control |  |  |  |  | Yes | ITR-CL-1-113 Motor Control | 81f3a0bf-587d-4ad3-ab4d-1f80a3027a72
checkpoint-status |  |  | checkpoint | General Motor Control
button | 271889a3-0b99-5efa-8b30-3c840a309d4b |  | button | Check all labelling and warning signs are correctly installed and visible | Yes,N/A
button | 42dd4760-41a4-512b-a9ab-c89d144ec924 |  | button | Check control equipment is clean and free from dust, debris and tools, no mechanical damage | Yes,N/A
button | 3ec738bc-3381-576b-ab5d-b8dd559f3a94 |  | button | Check preservation and transit items are removed | Yes,N/A
button | 7ae9798c-f24b-5c71-9791-d6fa6e08594d |  | button | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor | Yes,N/A
button | 2252f925-b80a-52dc-aa9a-30b89e0a442c |  | button | Check all cabling to control gear and motor is undamaged, supported and tidy | Yes,N/A
button | b37a4cd2-8560-56fa-ba6b-3ef8f07e645d |  | button | Check earthing bar and connections are correct and tight | Yes,N/A
button | 423e5baa-bfdd-5581-bece-8cab5fee68f0 |  | button | Check incoming and outgoing power cables are terminated and glanded correctly | Yes,N/A
button | 97ad2b41-4cff-562c-897a-79017543f3f1 |  | button | Check phase identification on power cables is correct and visible | Yes,N/A
button | bc55e934-6184-5205-818f-f531f2da50d9 |  | button | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque | Yes,N/A
button | 7de845f5-1cc1-5751-98f9-953a1e450f1f |  | button | Check all other nuts and bolts are tight | Yes,N/A
button | c4b35821-b001-577e-981b-0ed6f1fb942a |  | button | Check spare gland entries are plugged with correct rated plugs | Yes,N/A
button | dee4f953-7134-5cc7-b78d-d26f30a10744 |  | button | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected | Yes,N/A
checkpoint-status |  |  | checkpoint | Variable Speed Drives (VSD)
label | 41614d56-a8af-5092-9cb0-75a07864792f |  | note | Record VSD Details
text | 3e1612e5-3dc5-5ffb-8b8c-a9c5a0994c9e |  | textbox | Volts (Input) |  |  | V
text | bbffba4a-45ee-5161-95ad-eb804bcc9014 |  | textbox | Amps (Input) |  |  | A
text | fdeeec23-31f5-5b22-8981-4c3cc478e235 |  | textbox | Amps (Output) |  |  | A
button | ad6bba94-8c05-5051-afb0-fdb46e1f73fe |  | button | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input) | Yes,N/A
button | 3ba30a88-6699-5648-9dc6-3850dcbd81c3 |  | button | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used. | Yes,N/A
button | 8edb13bc-60e2-5deb-b03d-0e1248cf12c7 |  | button | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged | Yes,N/A
button | ee2d6df1-da80-53e7-9211-f7067bc8f4df |  | button | Check control signal cables use twisted pairs | Yes,N/A
button | a909a109-960c-5031-99e4-3d7bd42f0822 |  | button | Check control signal and profibus cables shield is earthed at one end | Yes,N/A
button | 62401cee-bc7c-5620-8e17-9c0b097e0f37 |  | button | Check analogue and digital signals are run in separate cables | Yes,N/A
checkpoint-status |  |  | checkpoint | Voltage segregation
button | 8ad4c2f8-6471-5e41-8427-26fdd46c4ac2 |  | button | Distance between input power and motor cable >300mm | Yes,N/A
button | 8d4b68cd-8844-5208-b74e-25cb470a457d |  | button | Distance between input power and control signal cable >200mm | Yes,N/A
button | 39727ef1-4ef6-56e4-bec7-abaaafa7ddec |  | button | Distance between motor cable and control signal cable >500mm | Yes,N/A
button | e2516a13-edf5-528a-a49c-36ea963a218a |  | button | Check there are no power factor compensation capacitors installed on the outgoing power cables | Yes,N/A
button | e0c0a718-f04e-522d-9bf2-3957e675e456 |  | button | Check gland plates with single core power cables are non-magnetic at VSD and LIS | Yes,N/A
button | c279141b-58af-5282-a021-59e7112de91f |  | button | Check mains voltage cannot be applied to the VSD output by means of a bypass connection | Yes,N/A
button | d1321e44-ff12-59d4-aa8a-0df8e46c8a8d |  | button | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC | Yes,N/A
button | dc639f77-ddbc-59a0-a1ff-43b2a1403aee |  | button | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position) | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | Cable Pre-installation |  |  |  |  | Yes | Cable Pre-installation | 863057a0-bf0a-4f39-bfcd-24a2cf5ee4eb
checkpoint-status |  |  | checkpoint | Cable Pre-Installation
boolean | 0d5f1045-5283-5dfd-8105-8869d67828e3 |  | tickbox | Check cable details are correct and in accordance with cable schedule.
boolean | 48d36003-edd0-5ece-a827-339f875f2022 |  | tickbox | Cable has been tested for insulation resistance and is safe to install
boolean | a599a58b-36b0-5966-bcbe-a6aa53d0cd9e |  | tickbox | Sufficient rollers in place to prevent excessive cable rubbing, (if applicable).
boolean | 45a024bd-2b61-5146-92d0-313fa71bd506 |  | tickbox | If using winch - ensure it is being used in accordance with Entec Winch SOP 2023-03
boolean | 89be9bb2-122d-5fda-9ac5-0428dbec34e0 |  | tickbox | In all cases, ensure the cable minimum bending radius is not exceeded.
boolean | 8525f444-70e5-5e40-9a9e-595927e8fc93 |  | tickbox | Check cable installed undamaged & cable ends are sealed to prevent the ingress of moisture.
boolean | 19c7b108-8217-5e39-9f1c-71ba617d6f35 |  | tickbox | Cable ties, clamps, cleats etc. are of suitable type and spacing as per the requirements.
boolean | d52aa36e-70c2-5f6c-a17a-610d4b1cee8a |  | tickbox | Segregation from other electrical systems, pipes or structures has been by separation, barriers, or distance (a minimum of 300mm).
checklist-sectioned |  |  | checklist | JHA - Job Step |  |  |  |  | Yes | JHA - Job Step | 8b9ea2c9-d957-47e8-ace3-e7590e7e78e0
checkpoint-group |  |  | section | Task Step - add task step for each individual task
checkpoint-no-status |  |  | checkpoint | Task Step - add task step for each individual task
date | 26e2895e-46dc-55d8-91aa-d34462d3219f |  | date | Date:
text | edc2c497-a45f-5063-8c12-87586ccbfeb2 |  | textbox | Task step number (eg. Step 1, Step 2 etc):
text | a12b90eb-71dc-5936-b414-a3b4762a0526 |  | textbox | Task details:
text | 90373697-09a2-52da-9093-db43db06e3e5 |  | textbox | Hazards:
select | f9753613-aa62-5d16-ba34-191186a9832b |  | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
text | 578f357f-fae0-515e-99b1-60042e5723d9 |  | textbox | Potential consequence:
text | be7dc2f6-39bf-5087-a981-031a48ffe06d |  | textbox | Controls:
text | d61174a1-6a04-5f2c-90e9-2d589f32cacf |  | textbox | Recovery steps:
select | 38bcca95-c251-5bb8-8ce5-ce18bef184a7 |  | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist-flat |  |  | checklist | ITR-CL-1-115 Lightning Protection |  |  |  |  | Yes | ITR-CL-1-115 Lightning Protection | 8cefef7d-7d77-41cc-8894-2d3316acebc9
checkpoint-status |  |  | checkpoint | Lightning Protection Earthing system (Mandatory Photo)
button | 962dc00a-bf7b-5e05-acf2-d5645b2eb507 |  | button | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007 | Yes,N/A
button | 3fd75246-24af-5c69-959d-532d34b705ac |  | button | Lightning conductor is 2 metres or more above the entire protected area | Yes,N/A
button | 0fb071fe-8243-5ed6-9685-eb139ed94ee5 |  | button | Check the materials and equipment used for the down conductors are suitable | Yes,N/A
button | 298085f4-2d0f-5af7-8443-080df6513427 |  | button | Check the down conductors are routed, located and electrically bonded as required | Yes,N/A
button | c6f282a1-b08f-519d-ba1d-89ebf825c0b3 |  | button | Check all installed components are firmly secured | Yes,N/A
button | 61e068f0-3e1d-5b6a-a39c-5b705e475cec |  | button | Check the method of protection against electric shock, including the measurement of distances | Yes,N/A
button | 67727910-4ffa-5a66-a264-005150daf9e9 |  | button | Check earth termination systems are interconnected | Yes,N/A
button | 12880d6b-3ef4-5d2c-82ae-fd9fd56afbd6 |  | button | Check isolating and switching devices correctly located | Yes,N/A
button | ca1a8f84-153c-54c8-a30f-ae68fac9c2a5 |  | button | Check warning signs and diagrams are installed | Yes,N/A
button | 665900b8-513e-5425-b6b9-1b80f47d7d52 |  | button | Check accessibility for operation and maintenance | Yes,N/A
checkpoint-status |  |  | checkpoint | Test Results
text | 157ca8be-2ef6-5e87-ba6f-f102e88400c7 |  | textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  | Ohm
text | ddcc6e90-3827-5bad-a39e-b99ee4d7280f |  | textbox | Earth termination system resistance is correct and record value |  |  | Ohm
text | b1d32614-dcb6-5954-938b-7724481d8f46 |  | textbox | Record the insulation resistance of the electrical installation |  |  | MegaOhm
text | a5a93179-92e2-52e2-8be0-00cabc3894c7 |  | textbox | Continuity of the main and supplementary equipotential bonding: |  |  | Ohm
checklist-flat |  |  | checklist | ITR-CL-1-129 Flow Meter Installation |  |  |  |  | Yes | ITR-CL-1-129 Flow Meter Installation | 8e1e0926-8711-4a76-a887-5a91e39a484f
checkpoint-status |  |  | checkpoint | Flow Meter Installation
button | 79d399e8-6bf1-5cf5-8726-622bba11e82f |  | button | Check instrument nameplate details are correct in accordance with the instrument index | Yes,N/A
button | cda7b0d1-4555-5c62-b89f-a442ee69f159 |  | button | Flow meter calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
button | ff13f8b1-514d-5390-8877-9a74428cc7b7 |  | button | Ensure location and tapping point is verified as per P&ID & location drawings | Yes,N/A
button | 6235fc3d-b0ef-5cc5-b169-4aef086a088a |  | button | Ensure direction of flow is correct with respect to flow meter | Yes,N/A
button | 6ac08eff-e464-5c4f-b8ad-bcbcac0b0234 |  | button | Check mechanical clearance is adequate for installation of flow meter | Yes,N/A
button | a3eb006e-3fed-5fd6-a7bd-7667a3be5301 |  | button | Verify type and size of gasket is correct between process line and measuring unit flange | Yes,N/A
button | d1c16033-5856-5923-b04f-9286452fea9b |  | button | Ensure correct nut and bolt grade and material for connecting unit to process line | Yes,N/A
button | d9e10f5b-05b1-52b1-a51e-e01317f8a08b |  | button | Verify display/cover is oriented for ease of use for operators and access for technicians | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-104 - Low Voltage Cable |  |  |  |  | Yes | ITR-CL-1-104 - Low Voltage Cable | 91f5de3f-6421-4881-8a1b-8b6c2e056983
checkpoint-status |  |  | checkpoint | Low Voltage Cable
button | af28edc1-96a0-5a5f-bd7d-81afda15fcbf |  | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
button | e46a9aa7-5f6d-5842-bc61-cfb5182e4911 |  | button | Check dressing / cleating, cable undamaged | Yes,N/A
button | 5c2861ad-6315-5bc7-bae4-059e0a0eaefa |  | button | Check cable cores correctly identified and labelled. | Yes,N/A
button | 22f0c09d-6de4-5561-a994-c02bcf20db5f |  | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
button | 77d6ecc1-fdb5-5479-8bb1-91e113d59070 |  | button | Check Armour / Screen correctly made off. | Yes,N/A
button | fb923de7-835f-5346-9267-0c1d13b74f2c |  | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
button | 054e931d-90ae-5f38-bb32-dc7a88eacd10 |  | button | Glanding / Locknuts correctly installed. | Yes,N/A
text | 352202bf-aae8-5e4e-9735-7d1feb3c873b |  | textbox | Gland type - from: |  | Haz. Area Rating
text | d7c958cc-8da0-56eb-844d-cc4554705410 |  | textbox | Haz. Area Cert Details.
text | 40c0b575-5d7a-5779-9b72-185f2b33d28a |  | textbox | Gland type - to: |  | Haz. Area Rating
text | 823ab698-3882-53fd-b7c4-a046de87be21 |  | textbox | Haz. Area Cert Details.
checkpoint-status |  |  | checkpoint | Electrical Checks
text | 17074137-45f3-563a-9f62-a5192912d54d |  | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
holdpoint |  |  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-101A Conduit/Ducting Below Ground |  |  |  |  | Yes | ITR-CL-1-101A Conduit/Ducting Below Ground | 9273ce44-05e6-436b-ba32-57caf1b033bb
checkpoint-status |  |  | checkpoint | Conduit/Ducting Installation Below Ground
button | 408a7d94-31bc-56a4-9a3f-c4846c80162c |  | button | Check equipment details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | d7f3657d-5f2f-55ea-bd1d-49025ee6f55a |  | button | Check conduit cable enclosure installation is as-per design, layout drawings and specifications. | Yes,N/A
button | 83053eed-e03e-57a3-b4dd-37d0d23f1a27 |  | button | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed. | Yes,N/A
button | e7d1e47f-c7b6-54a2-8cce-b288322b4e14 |  | button | Confirm that there are no obstructions, and that the installation will be accessible for maintenance. | Yes,N/A
button | b64c2bff-cd7c-5ad4-b6b3-c1a3961ed5cb |  | button | Check all fixings are tight and secure. | Yes,N/A
button | 14356867-98fd-55f9-8a02-dbaf14dd2fa7 |  | button | Check bends do not exceed the maximum cable bend radius. | Yes,N/A
checklist-flat |  |  | checklist | Earth Pegs |  |  |  |  | Yes | Earth Pegs | 9922fb81-d2c3-4a3d-8b9a-327270c5bd2f
checkpoint-status |  |  | checkpoint | Mold type identified
select | 8d2a1b0a-b8f1-5a0b-92f8-c0daec33c794 |  | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee
checkpoint-status |  |  | checkpoint | Cadweld Visual test
label | 9ae17236-0bd9-5bc0-96c6-72e9587a7dfe |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld Ductor test
text | 642b96df-9734-5ef4-9531-417d49c3a50a |  | textbox | Result:
label | ed808718-9484-59f7-add4-506485bf45ae |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Continuity test [Peg to Earth Bar]
text | 401dacd4-633d-5769-9b12-62217ab63f5d |  | textbox | Result:
checkpoint-status |  |  | checkpoint | 3 Wire Earth test
text | b9baa9b0-974d-593f-aa66-43f8886f0563 |  | textbox | Result:
label | 803b2e55-3d8f-55f2-a311-076921ef9cd6 |  | note | Pass if <1 ohm
checklist-flat |  |  | checklist | ITR-CL-1-126 Cone and Thread Pressure Testing |  |  |  |  | Yes | ITR-CL-1-126 Cone and Thread Pressure Testing | a13e7dc3-f98d-42c8-a922-b4d52c89ae7a
checkpoint-no-status |  |  | checkpoint | General Data
text | 9bdca364-c6e4-5032-9956-643da41dda63 |  | textbox | Location:
text | 96a72ebf-1e66-59ad-b053-72910f7c9442 |  | textbox | Duty:
text | cbf08a12-f724-5e20-8708-9376e9c32c97 |  | textbox | Reference Drawings:
text | 3ffd6b5a-1297-55c2-a17b-d946fdedbca2 |  | textbox | Hook-up drawing:
text | 41943411-c78c-5e38-929d-e23a499f8658 |  | textbox | Related instrument tag no:
text | b53090f0-055e-57a8-bd2f-8e79b7d37312 |  | textbox | Tube diameter and wall thickness:
checkpoint-status |  |  | checkpoint | Checklist items
button | 4cddb07c-c76a-539b-baf0-14863ebb25b4 |  | button | Tubing orientation as per hook up drawing. | Yes,N/A
button | 623dbe2f-d69c-5ccb-93e7-44635f6c4d19 |  | button | Checked with a Torque Wrench and marked and tagged | Yes,N/A
button | fb1b199d-5938-5a8b-a26f-b0107005353d |  | button | Ensure Area is barricaded off to restrict unauthorized entry to personnel | Yes,N/A
button | f23cd556-ae2c-55d3-abac-643c35a70465 |  | button | Tube as per specification and hook up drawings. | Yes,N/A
text | 76a67493-fab4-57c4-9a27-a6abb7748fc3 |  | textbox | Max design pressure:
text | 6cc939ae-1c2d-5e20-b4e3-1b666eb3cda5 |  | textbox | Test medium used:
text | 1c71bf2f-6b10-5fb9-aa9b-c87225790e6f |  | textbox | Record Testing pressure:
text | 3661e20b-d462-54c0-9f7e-9f01d240b545 |  | textbox | Test pressure duration: |  |  | Minutes
text | df8aaede-7e79-54e6-9f6e-53339dd0db91 |  | textbox | Test leak rate: |  |  | Litres/minute
button | b50cedcc-0f97-5536-b30e-e74667a73118 |  | button | Chart recorder used and attached (where applicable). | Yes,N/A
button | 7ad8258c-4c5a-5f9f-b969-c11763f0a080 |  | button | Confirm all Tubing lines have been pigged / cleaned. | Yes,N/A
button | b4354c34-3058-51b6-bf55-9a43cc123035 |  | button | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions. | Yes,N/A
button | 2a69bb8b-cafe-5fb6-a250-a5c95445879f |  | button | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-sectioned |  |  | checklist | ITP-I05B ENTEC - Instrument Loop Check |  |  |  |  | Yes | ITP-I05B ENTEC - Instrument Loop Check | a1f4c03a-ad2d-4e25-8b9a-91677d7019b0
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Please upload ITP here when complete
checklist-flat |  |  | checklist | ITR-CL-1-118 Instrument Pressure/Leak Test |  |  |  |  | Yes | ITR-CL-1-118 Instrument Pressure/Leak Test | a260049e-1c70-4b17-873d-276b46940572
checkpoint-status |  |  | checkpoint | Checklist items
button | 312025e1-3aa4-5c7d-aa52-585ee212bd62 |  | button | Tube identification correct | Yes,N/A
button | 03343d53-ec9d-5c39-8c6b-fa6ca5dfaf29 |  | button | Mechanical damage visual check | Yes,N/A
button | c939ebae-325e-5129-8cc3-5fbc505398b6 |  | button | Flow direction and instrument orientation correct | Yes,N/A
button | 6913b8c4-d27f-5fc4-8dd5-eb1b6002100f |  | button | Tubing size and installation correct | Yes,N/A
checkpoint-status |  |  | checkpoint | Testing
label | 6ea556cb-8c60-580f-a306-65fdc03cf287 |  | note | Verify test pressure and medium is correct per project and manufacture specification prior to test
text | 9dde934f-af34-5214-b0a2-800a3990188a |  | textbox | Test fluid:
text | da7acc81-9ae5-5c3f-b054-5acf2799e4a1 |  | textbox | Test pressure:
text | a1bea254-af4e-50f2-ae2d-92369cf7ecf3 |  | textbox | Max design pressure:
select | f64592ff-f819-56bc-a234-d2a209e0f199 |  | dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
text | d3fd68d6-32f5-5f43-8ac3-f077f5b1e763 |  | textbox | Duration: |  |  | Minutes
button | 8e886e08-9f34-51e4-b3ce-a7a66cde1937 |  | button | Confirm all impulse lines have been drained and cleaned | Yes,N/A
button | 09e66fd4-b7db-5f5e-a369-00651bd26e51 |  | button | Confirm any temporary test connections, valve etc. are rated for the intended test. | Yes,N/A
button | f940703f-8ef3-52f1-adc2-1efb474c5b33 |  | button | Confirm pneumatic, test gas and aspirator lines have been blown clear. | Yes,N/A
button | cc603aa1-7bc7-5247-bb26-b44d6904a9f6 |  | button | Check hydraulic lines flushed to project specification. | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-sectioned |  |  | checklist | Safe/Unsafe Observation Card |  |  |  |  | Yes | Safe/Unsafe Observation Card | af9b74d2-e6dc-4e1a-8602-115abf4ef084
checkpoint-group |  |  | section | Basic Details
checkpoint-status |  |  | checkpoint | Basic Details
button | d602e59a-1a81-5f60-a7d6-2f827da33a73 |  | button | Safe or Unsafe observation? | SAFE,UNSAFE
date | cb033385-3086-53a0-bbac-3c20e33d057c |  | date | Date:
text | f49370b9-a829-5df1-9111-809ae08fe247 |  | textbox | Observers Name
text | d28cfffc-ddd4-5179-bcd9-5f78155c4826 |  | textbox | Site
text | 96f36722-055e-5270-ad2d-69c7d78c54b4 |  | textbox | Task Observed
checkpoint-group |  |  | section | Hazard Observation (select all that apply)
checkpoint-status |  |  | checkpoint | Hazard Observation (select all that apply)
button | 17092683-2b10-5c80-8089-05b8947b07a7 |  | button | Mobile Equipment | YES,NO
button | 7b7871e6-df54-557f-b017-58f42a9916cc |  | button | Hoisting & Lifting | YES,NO
button | fbdfbd64-b065-50c3-b73a-51c15673e56a |  | button | Dropped Objects | YES,NO
button | ae96e44c-d7d4-53ac-80bd-478435f9a4ce |  | button | PPE & Process | YES,NO
button | 293008da-b8f7-5abd-be58-679497580893 |  | button | Pressurised equipment | YES,NO
button | 057c83c4-04b1-554d-94b6-2faa2f064aa5 |  | button | Machinery & Tools | YES,NO
button | a4de9a3f-f26c-5ecd-9ef2-a0656e7698d4 |  | button | Electrical equipment | YES,NO
button | 9e38850d-3fe1-571d-8d97-1c621613565c |  | button | Housekeeping | YES,NO
button | 080c4ecc-937a-56fb-a4e0-3520ca024a33 |  | button | Person fall risk | YES,NO
button | 75d1356e-4970-503d-8356-7e0ec8c43b6a |  | button | Manual handling | YES,NO
button | 0c091747-fc77-5b1c-82c2-7840e1a97f4a |  | button | Exposure to process temperatures. | YES,NO
button | c2d1aff2-59c0-586f-bb05-7b9b11611ec1 |  | button | Confined space | YES,NO
text | 48b40157-a891-5948-b3eb-9475aa0b0d1d |  | textbox | What I saw
text | 45961bcc-530a-5d8f-919f-4a526f17c0fa |  | textbox | What I did
button | 69046fb6-7bd8-5821-98a7-34e0bee56b6d |  | button | Is further action required? | YES,NO
checkpoint-status |  |  | checkpoint | Observation reported?
text | 9e09ffc8-baf0-5b76-bf83-57ad64ebda26 |  | textbox | Reported to:
text | 0e65806f-84ca-5b46-af40-22bafee761af |  | textbox | Other comments
checklist-flat |  |  | checklist | ITR-CL-1-103 Schedule of Test Results DB |  |  |  |  | Yes | ITR-CL-1-103 Schedule of Test Results DB | afc973bc-2c21-49fc-a4b9-7c4550d496a7
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-flat |  |  | checklist | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation) |  |  |  |  | Yes | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation) | bdfa0aaf-9816-4da1-90bc-aeaf6e566be9
checkpoint-status |  |  | checkpoint | Equipment
button | 517f5143-2410-513c-8d7d-2f49f3d447d4 |  | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
button | e22f1dcd-0f91-56a9-b6cb-a657c721443f |  | button | Equipment checked for additional items as applicable | Yes,N/A
checkpoint-status |  |  | checkpoint | Valve
text | 9c92b41f-7204-5212-aed6-3257e9f1b7cc |  | textbox | Valve Size:
text | 7d24d3e9-9f5b-5d1c-a74f-957af5d4b1f3 |  | textbox | Flange type:
button | 0a702e8c-08c2-5464-b2d8-fd941f8a3d01 |  | button | Material certification correct | Yes,N/A
button | 92bb5ec1-ca60-5b8f-b9cc-d35f849c577a |  | button | Trim material correct | Yes,N/A
text | b7a66705-312c-5a37-9753-203ae866d715 |  | textbox | Rating:
text | 5c677dbd-6c51-56ca-b12d-e43861762262 |  | textbox | Service:
button | e53a853d-d881-565d-b124-03e1435e4930 |  | button | Body material correct | Yes,N/A
text | 4d94fca5-e1ce-5478-bf38-7f1643e91e5b |  | textbox | Leakage class:
checkpoint-status |  |  | checkpoint | Actuator
text | 9b7a3aed-3141-5b36-9b2e-2f29c818b119 |  | textbox | Input range: |  |  | kPa
button | e668a569-7003-53d4-8b08-8e4c92694a20 |  | button | Failure action | Yes,N/A
button | 2cc0eae6-ebc3-52de-9a88-26880a470426 |  | button | Hand wheel operation correct | Yes,N/A
checkpoint-status |  |  | checkpoint | Positioner
text | b353380f-c770-5581-9f3c-7bc0f3062240 |  | textbox | Signal range
text | 692a4b53-6dd2-5d34-b8ee-c78765cbf08d |  | textbox | Output range
checkpoint-status |  |  | checkpoint | I/P Converter
text | 23899687-e4b5-5875-ab6e-0b992899d669 |  | textbox | Signal range
text | d9e416c5-a93e-555c-bcef-34fe261bf1ab |  | textbox | Output range
checkpoint-status |  |  | checkpoint | Filter/Regulator
text | 133eac93-481f-5f9c-a0fd-083ac3e95430 |  | textbox | Range |  |  | kPa
text | afb87505-cc8c-590d-a8ab-f4fbe6467c95 |  | textbox | Pressure setting |  |  | kPa
checkpoint-status |  |  | checkpoint | Fail Action
select | ec04e265-647e-56b6-8b48-479e5b1f7d91 |  | dropdown | Electrical Fail Action | FO, FC, FL
select | 1f215402-4968-5151-b202-9151944b4fa6 |  | dropdown | Motive Force | FO, FC, FL
checkpoint-status |  |  | checkpoint | Proximity Detectors
button | a6571574-2216-51c5-87cc-f29592cd916a |  | button | Open switch set, correct mode setting | Yes,N/A
button | a5c32505-2c84-5fb2-883c-dc82759dd51e |  | button | Closed switch set, correct mode setting | Yes,N/A
button | 66d0472f-bc64-5a28-bdb5-47499a2c6fa0 |  | button | Electrical connections and certification correct | Yes,N/A
checkpoint-status |  |  | checkpoint | Solenoid Valve
button | 477ffd2c-7a55-5882-b145-66e2e665aa61 |  | button | Operation correct | Yes,N/A
button | 5e5836a0-2ecc-5161-83ad-45659d110dd2 |  | button | Electrical connections correct | Yes,N/A
button | 1ed1de9a-41c6-55d5-9c48-622ffc409103 |  | button | Electrical certification correct | Yes,N/A
text | 3689c809-ad49-5bd0-99c2-7966adc57484 |  | textbox | Voltage: |  |  | V
button | a9b111b0-2063-56fc-b003-48e1eab4f337 |  | button | Pneumatic connections correct | Yes,N/A
text | a48a85ea-943d-5624-90ad-a23cfcdbae12 |  | textbox | Pneumatic pressure |  |  | kPa
checkpoint-status |  |  | checkpoint | Pilot Valve
button | f7ba09ab-1e8a-52b3-ae21-6066c26d4698 |  | button | Pneumatic connections correct | Yes,N/A
button | 9e3f4bdd-0d8a-54fe-a5bd-b25a21d04ff5 |  | button | Operation correct | Yes,N/A
button | e739200f-9bd6-5986-9259-34611ad5a919 |  | button | Action/Lockup | Yes,N/A
checkpoint-status |  |  | checkpoint | Hydraulic Actuator
text | 3e3f1287-83ab-5697-a097-d3fb85193daf |  | textbox | Working pressure
text | ce6ad7ab-df42-5863-9dc3-92275dbbab72 |  | textbox | Manifold pressure
text | 47db2c3b-2c8e-5791-92b3-a2f611270808 |  | textbox | Fluid type
button | 00b85d2f-e7eb-54fe-8746-2b6cd1a8e3de |  | button | Hydraulic connections correct | Yes,N/A
text | cfea285c-20c6-5066-afe1-e5ea2b77b970 |  | textbox | Regulator pressure setting
button | 81455763-1465-59ed-9c39-72ef5c753235 |  | button | Pilot operation correct | Yes,N/A
checkpoint-status |  |  | checkpoint | Accumulator
button | 5fe56fca-7110-5ccf-8f3a-2b4f73566419 |  | button | N2 Charge required | Yes,N/A
text | 28b774b6-e360-5287-ae20-275ef49ca2fb |  | textbox | N2 Pre-charge pressure
text | 60cc1dcc-44df-567a-b2ab-1eabd920de9a |  | textbox | Pressure switch setting
text | c4bb92f6-e099-50ca-b2b0-829d0328b7d4 |  | textbox | Working pressure
text | de143b9b-52d2-54e5-9891-144af16a37d1 |  | textbox | Output range
button | d81fa3fa-09ec-5bfa-8162-7b63a087e6fa |  | button | Volume tank & check valve installed correctly | Yes,N/A
checkpoint-status |  |  | checkpoint | Electric Actuator
text | d2e1d6f4-25f5-5405-80f3-5b2f510618d2 |  | textbox | Voltage:
button | 56ea04ca-b789-5764-ae95-c2a9a5e23027 |  | button | Electrical certification correct | Yes,N/A
button | 82255a42-1ddb-53fb-a6a3-d64f51011a20 |  | button | Electrical connections correct | Yes,N/A
button | babce00a-1db7-5a22-b91a-4a9c1e9df755 |  | button | Remote operation correct | Yes,N/A
button | 65f0b7d2-9988-5b1c-926a-12f183b4121d |  | button | Local hand operation correct | Yes,N/A
button | a27675c1-7419-56b3-a584-16fe4381ca7e |  | button | Torque switches and travel stops set | Yes,N/A
checkpoint-status |  |  | checkpoint | Miscellaneous Equipment
text | b2608af8-33a2-5723-b44f-13b93084cf30 |  | textbox | Description
text | f037109f-9268-5948-bf2c-6432b6d71b72 |  | textbox | Manufacturer
text | f217159e-30b0-5085-b0f1-0d648c1f56cd |  | textbox | Model No:
text | 7aa41820-86e2-5bde-a60c-fcbbe8f5f391 |  | textbox | Serial No:
text | 2e603b63-0a65-5ca2-8ae9-d1d1e046e97f |  | textbox | Range:
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-sectioned |  |  | checklist | JHA - Job Hazard Analysis |  |  |  |  | Yes | JHA - Job Hazard Analysis | bf8cc7f5-8d61-4ab6-8cab-9dbd4c88ee12
checkpoint-group |  |  | section | Job details
checkpoint-no-status |  |  | checkpoint | Job details
date | 9121b653-9465-5c94-8e98-616d3720b083 |  | date | Date:
text | 2296b6cd-d4f1-5691-8da3-a529becb34bf |  | textbox | Permit No.
text | 8c3c490d-c825-5522-bdbc-0b806270bda3 |  | textbox | Job No.
text | b79ea938-c5ce-52f8-af36-c62c2f65c8e3 |  | textbox | Site
text | e10cb77a-6c27-5a76-995b-93e170d648e0 |  | textbox | Activity Location
text | 72676fca-63ab-5aef-bc4e-64505c74da15 |  | textbox | Asset:
text | 2f2b1683-9a8b-5c8a-84d5-4dade0dd5aa0 |  | textbox | Work Details:
checkpoint-group |  |  | section | Prompts for Hazards - Mark all that apply.
checkpoint-no-status |  |  | checkpoint | Prompts for Hazards - Mark all that apply.
boolean | e2e74f39-287a-52bd-8eca-eb140dc9cf2a |  | tickbox | Sparks/Open flame
boolean | 2acfc571-e5a6-505c-ac2b-eba8970a62d4 |  | tickbox | Disabled safety device(s)
boolean | 65f6238a-90cd-56f6-ad6b-0554edd0bd36 |  | tickbox | Uneven surfaces
boolean | f9e713ed-53fd-5dc5-929f-d6ff97eeecf0 |  | tickbox | Fatigue, over-exertion
boolean | 24e995ec-3dd7-569e-b330-0578c5373bae |  | tickbox | Crane movements
boolean | 01452f54-e4bd-5c7e-8ec0-ffa875e8501a |  | tickbox | Moving/Rotating parts
boolean | 1f7273b3-8cb8-5054-9bbf-90013ef12dfc |  | tickbox | Remote area, working alone
boolean | 1e00237e-3a56-527c-95bd-1af4f5c47fa6 |  | tickbox | Conflicting work/SIMOPS
boolean | 48550d8d-c109-5c4c-9a7d-ed410eba740f |  | tickbox | Electrical arc flash
boolean | d3c0a2b4-04b7-5bc6-aef3-4ca1c2480940 |  | tickbox | Sharp objects/materials
boolean | f9d836e2-dc1e-51ae-a045-3e021201afe1 |  | tickbox | Restricted/Difficult Entry/Exit
boolean | f0c52d3f-bfd4-53c0-92dd-c40489c22c79 |  | tickbox | Overhead obstacles
boolean | 7c761f22-d173-52dc-8223-bd1285cc4716 |  | tickbox | Ignition sources (other)
boolean | 3272747d-9450-5da3-a2ac-faa787d2363f |  | tickbox | Access/Egress
boolean | 866f2e8c-c205-5d58-8086-23ecb0668fb0 |  | tickbox | Water body
boolean | d3e0555a-b9f4-5c0c-b061-e01105e6b7d3 |  | tickbox | Live equipment
boolean | 24ac8cbf-ef66-53d5-a5ce-8bcbf39c061d |  | tickbox | Slippery surfaces
boolean | a3b30d7b-ec59-58ca-9313-26d2c562f387 |  | tickbox | Suspended loads
boolean | 98b1bf54-a699-528e-821a-322c9c2430da |  | tickbox | Hazardous substances (chemicals)
boolean | 22f019ba-6ada-5889-82f6-57f72a23a014 |  | tickbox | Use of non-intrinsically safe equipment
boolean | e3dc92c4-6d8c-5806-9d79-ba9d7375189c |  | tickbox | Weather extremes
boolean | 317ef129-b4f2-5978-a01b-dd9b3f7ee83c |  | tickbox | Moving vehicles
boolean | 789348a6-324b-5e45-98b9-5df2ad640f56 |  | tickbox | Task related noise
boolean | d4e3a79f-63f6-53ac-a71f-8f3f6f7034a1 |  | tickbox | Engulfment
boolean | f77e1ae9-20bd-5d76-b6fe-db40018c1738 |  | tickbox | General waste
boolean | bfa762a9-8535-532c-9647-bd72e4369d72 |  | tickbox | Hazardous waste
boolean | 3f775ada-8d29-5732-8d34-4393bf241882 |  | tickbox | Hazardous/toxic substance, fumes, gas
boolean | 6d0bf608-f379-595e-bf82-0b824ac63501 |  | tickbox | Flammable materials - Gas, liquids, solids
boolean | 34bd77ea-7899-5601-b0fd-d9b499ba4ac3 |  | tickbox | Reduced visibility, lighting
boolean | fb4bb6db-ab81-5c66-b884-cb3f83b3f055 |  | tickbox | Electricity
boolean | 3c73deb5-614d-59df-aa2a-6bc6c5952c80 |  | tickbox | Static electricity
boolean | 337fec5f-a0d8-5f8b-bec4-6af9d689ac55 |  | tickbox | Work at height
boolean | 317be1f2-c61e-5d51-9f28-b1926070f1fa |  | tickbox | Underground services
boolean | 14ec678d-6ee2-5bda-a8e5-9a125d230adf |  | tickbox | O2 Deficiency/Excess
boolean | 8303cc09-1e9a-5772-836c-820f27c974f5 |  | tickbox | Temperature extremes
boolean | 82a98376-7688-5830-87bd-11ec437ec37c |  | tickbox | Heavy objects
boolean | 39972442-f325-5a1d-93e7-200899637b63 |  | tickbox | Radiation
boolean | 4f4b68b1-b454-55a0-a219-1a2333da1520 |  | tickbox | Potential energy - Tension/Compression
boolean | ff1407f6-56d7-5d5f-b604-0a466c33788b |  | tickbox | Flying particles/Dust/Objects
boolean | 35a7f122-ad6a-5594-9946-aba2eb678cba |  | tickbox | Vehicle entry
boolean | 5c89e163-bce5-5049-b6a2-5e1ebad30bfb |  | tickbox | Exposure to process temperatures.
checkpoint-group |  |  | section | Prompts for Initial Consequences - Mark all that apply
checkpoint-no-status |  |  | checkpoint | Prompts for Initial Consequences - Mark all that apply
boolean | 00f19fe5-1ad2-53fd-8229-8c082a6bd8bc |  | tickbox | Falling/Dropped objects
boolean | c7c51e4d-394e-5bb3-9043-2690d397d2d1 |  | tickbox | Fall from height
boolean | 5fc58abf-df57-5cdf-b4fc-b936b095b1b1 |  | tickbox | Trip/Slip/Fall
boolean | 963fbd82-7281-5cb7-b204-586311d1a02c |  | tickbox | Gas release
boolean | 35caaac2-10b3-53bb-9464-4f613176c840 |  | tickbox | Pressure release
boolean | a8380d82-74a4-5f0f-8446-51917018e112 |  | tickbox | Struck by object
boolean | 8b925c2b-16c6-5bff-a427-8a4f2cce1558 |  | tickbox | Exceeding tool limits
boolean | 855f5e64-7af0-51fe-8436-0fda03120d74 |  | tickbox | Overloading people
boolean | 51b43355-9c5f-57c3-8d84-1d991669a3d4 |  | tickbox | Unplanned shutdown
boolean | 1c3f2082-961c-5c6d-b286-218a65f1a12d |  | tickbox | Exposure to O2 deficiency/excess
boolean | 742ffc11-e2e1-556f-9da6-d85cdf6ab0c9 |  | tickbox | Exposure to hazardous substance
boolean | 3c76c8a8-0ec2-58d3-b890-4b9f9c07f07c |  | tickbox | Entanglement
boolean | 17cab252-ff5d-5afc-8c9f-0291ff00b395 |  | tickbox | Flying objects
boolean | 545a0a83-f1ae-53ae-a51d-3559eee6d18e |  | tickbox | Loss of control
boolean | 7c4c484c-cef0-50f7-9fdc-d2c237b59e35 |  | tickbox | Loss of containment
boolean | 38e73858-15e2-530f-b6cb-687a3a5228b5 |  | tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
boolean | a479994e-91eb-527b-8b30-780190b19085 |  | tickbox | Loss of structural integrity
boolean | 07de0b49-6421-52ef-8c3e-90e955f5e47b |  | tickbox | Equipment failure
boolean | e42f97da-349e-5e21-a5f3-f9b5b4e59e24 |  | tickbox | Uncontrolled ignition source
boolean | 3d7150c4-b075-5b3b-a8a5-2b2b91b8d6a9 |  | tickbox | Collision
boolean | b7287a6e-9b8a-5347-bfc7-686ff353c681 |  | tickbox | Ignition/Fire
boolean | c1e99fe1-fa68-5556-bb36-7462c665d8b8 |  | tickbox | Back strain/Injury
boolean | febb8172-fed9-5553-9762-1ed383864782 |  | tickbox | Burns
boolean | 65f86853-2b43-501a-81fa-10802d729290 |  | tickbox | Heat exhaustion
checkpoint-group |  |  | section | Initial controls - Mark all that apply.
checkpoint-no-status |  |  | checkpoint | Initial controls - Mark all that apply.
label | 0531576a-0e0d-5e0a-9822-c90127d2c91f |  | note | People controls
boolean | cdb87cd9-aa83-552e-9f27-192ad19e29f1 |  | tickbox | Safety/Fire watch person
boolean | c7ce9b43-64e2-5a9c-8866-82a154afcba6 |  | tickbox | Barriers/Flagging
boolean | dcf6bb7e-a5f9-52f0-a099-4bfb78439724 |  | tickbox | Warning signs
label | bc6fc587-4cd7-57aa-8aac-b1885ff5d667 |  | note | Equipment controls
boolean | 92675b30-30a9-58e0-af6a-1b04a7c62402 |  | tickbox | Master tags and locks
boolean | 5ae218e2-4b86-5e4c-a9cc-6344228e94da |  | tickbox | Scaffolding for access
boolean | d3d8dc3e-2571-5fed-b558-c2a29d1d7824 |  | tickbox | Radio communication
label | 56c8c170-dbe5-5304-a387-0e1d58901816 |  | note | Environmental controls
boolean | d74792dd-5e8d-54f1-8718-88bf002c7d28 |  | tickbox | Ventilation
boolean | 08c2a88f-3143-553f-ba43-3884c222ed1c |  | tickbox | Lighting
boolean | 15c09d2b-546f-5b76-a853-2b27f4dcf21a |  | tickbox | Gas Testing
label | 24f619a7-6d34-5444-b150-524826812edb |  | note | High risk controls
boolean | 17426f23-9ba6-535d-a26c-8d86191f6e73 |  | tickbox | WSCS Work permit
boolean | 00147651-933a-5dad-83fd-9df182bf01de |  | tickbox | WSCS Certificates
boolean | b26db9bb-a7f2-55cd-9f17-ca969ff48d9b |  | tickbox | Critical lift/Fall protection plan
boolean | 8d1fd861-b1cb-5271-acd4-f4cfd50bb495 |  | tickbox | Specialised PPE
boolean | 2142844c-3e51-58fa-a1a1-06005b55fd4f |  | tickbox | Spill kit
boolean | 35ee2540-5d3d-5bc6-abb6-1a93433e919f |  | tickbox | Fire extinguisher
checkpoint-group |  |  | section | Signatures
checkpoint-no-status |  |  | checkpoint | Signatures
holdpoint |  |  | signoff | Applicant signature
checklist-flat |  |  | checklist | Cable Test Record |  |  |  |  | Yes | Cable Test Record | c2e493b2-3553-4c3d-97ed-0eb6e4414cd6
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-flat |  |  | checklist | ITR-CL-1-123 Instrument Pre-Commissioning |  |  |  |  | Yes | ITR-CL-1-123 Instrument Pre-Commissioning | c58f2264-59cc-43d6-ba94-e51143055468
checkpoint-status |  |  | checkpoint | Checklist items
button | 897e9c39-89a6-5075-b9aa-fde697807612 |  | button | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface | Yes,N/A
button | 47f1318b-307e-5a97-a5fe-c77d0c3a625d |  | button | Relevant individual control system/ESD loops have been checked and test sheets completed | Yes,N/A
checkpoint-status |  |  | checkpoint | Analogue Input:
checkpoint-no-status |  |  | checkpoint | Analogue Input:
text | 378a8d55-eb5f-5b57-b324-9108a86e2635 |  | textbox | Input range & units:
text | 62d06d33-8cad-5af8-ae02-814d936f92c9 |  | textbox | Indication range & units:
checkpoint-no-status |  |  | checkpoint | 0% Rising
text | 6c3091b6-dc01-598f-a533-d3e2ab0b9468 |  | textbox | Input Signal:
text | ac589bf5-4f15-5503-aa6d-71bab343ea42 |  | textbox | Control Interface Indication:
checkpoint-no-status |  |  | checkpoint | 25% Rising
text | e8415b3f-3ac1-50f6-914c-a30b2c89be64 |  | textbox | Input Signal:
text | 7af91f29-8b47-5538-877f-01c0ce9d0f7b |  | textbox | Control Interface Indication:
checkpoint-no-status |  |  | checkpoint | 50% Rising
text | b3dfbaad-7d56-5932-8ccf-19733cf462cd |  | textbox | Input Signal:
text | 235fb3ca-b4c1-571b-8dab-a2b4ef0dcafc |  | textbox | Control Interface Indication:
checkpoint-no-status |  |  | checkpoint | 75% Rising
text | abc5d65e-8e20-5c2e-b704-d6bc0a5f2e67 |  | textbox | Input Signal:
text | a230595e-ee97-53ee-8ac5-45f9654d7297 |  | textbox | Control Interface Indication:
checkpoint-no-status |  |  | checkpoint | 100% Peak
text | e961078d-a3f4-5808-bd61-5427a76bb78b |  | textbox | Input Signal:
text | 6c5546a6-4215-59b3-a07e-f36021f29bcb |  | textbox | Control Interface Indication:
checkpoint-no-status |  |  | checkpoint | 75% Falling
text | b3deb643-40c6-5199-9484-e024b9980ae4 |  | textbox | Input Signal:
text | 4863c711-1488-5deb-a5b3-2c60e9183372 |  | textbox | Control Interface Indication:
checkpoint-no-status |  |  | checkpoint | 50% Falling
text | 98a2b6df-5603-5b93-9a8a-48c41df189b2 |  | textbox | Input Signal:
text | fc09dfe3-c9a3-523c-89ac-a6e00319a87d |  | textbox | Control Interface Indication:
checkpoint-no-status |  |  | checkpoint | 25% Falling
text | 014656fd-4bef-53ad-ade6-bf4f401a9cbf |  | textbox | Input Signal:
text | b65a9234-d2a4-5ce8-96bc-3cd215943c6a |  | textbox | Control Interface Indication:
checkpoint-no-status |  |  | checkpoint | 0% Falling
text | a99fedbf-ba52-53a7-b23b-51f8c31c2f5b |  | textbox | Input Signal:
text | 9df90556-69b2-53bc-b89c-6537f4f59540 |  | textbox | Control Interface Indication:
checkpoint-status |  |  | checkpoint | Digital Input/Analogue Alarm Trip Points
checkpoint-no-status |  |  | checkpoint | Alarm Lo:
text | 962425e6-dcc3-5b54-9225-40b97d1fc357 |  | textbox | Alarm setting
text | 08f42cc8-e309-5ef5-9e0f-82d963771251 |  | textbox | Measured Alarm Point
text | aebb232e-e92e-5ca4-b6ec-b9f513b43530 |  | textbox | Filter/Time Delay
text | 52d9be6f-a683-52ed-a0ec-d858870ce05f |  | textbox | Result
checkpoint-no-status |  |  | checkpoint | Alarm Lo-Lo:
text | a1abf795-19f3-5a51-8298-ac0238d21741 |  | textbox | Alarm setting
text | fd85b330-89f1-55eb-860d-701a06f98bd2 |  | textbox | Measured Alarm Point
text | a118d913-ab14-5f51-96db-e8d2833c9ee3 |  | textbox | Filter/Time Delay
text | 1ab1dc99-d556-555b-b45b-e3abd75ff08f |  | textbox | Result
checkpoint-no-status |  |  | checkpoint | Alarm Hi:
text | d85a7b2b-4c84-5a58-aeac-f60b7a795eae |  | textbox | Alarm setting
text | 84a67f05-f22e-5bca-8d4d-91fb178fdc1d |  | textbox | Measured Alarm Point
text | 60d46a44-257f-5dac-9985-54bb773aae1f |  | textbox | Filter/Time Delay
text | c9fd08ad-30c3-5610-8e1b-2cb691acee86 |  | textbox | Result
checkpoint-no-status |  |  | checkpoint | Alarm Hi-Hi:
text | 8698d97d-6c93-53e2-a922-f98558c5c64b |  | textbox | Alarm setting
text | 27d38d77-62a4-5bcd-a195-02d0467b1ce4 |  | textbox | Measured Alarm Point
text | 20462948-5499-5de0-b84e-83595ed54bf2 |  | textbox | Filter/Time Delay
text | 36f57217-6430-5d43-884a-41842a0a23e9 |  | textbox | Result
checkpoint-no-status |  |  | checkpoint | Control loop set points correct:
text | 2a301152-a39d-59d5-becf-713d8ab86590 |  | textbox | Set Point 1:
text | 5602cd0c-76fd-54b1-8d63-7518b1e2cfa4 |  | textbox | Set Point 2:
text | 82912c49-655e-5895-9ec0-1823330525b3 |  | textbox | Set Point 3:
text | 936ef3ac-8cea-5e81-a069-e7683e2e71f0 |  | textbox | Set Point 4:
checkpoint-status |  |  | checkpoint | Startup, Shutdown and Override functions
button | 140999e7-21db-5d8f-8c3e-64acb045e0a7 |  | button | Control system graphic display | Yes,N/A
button | f92b149f-fe16-55fc-8508-4cedcd34d717 |  | button | Control system point display | Yes,N/A
button | 51d22c96-e685-5d6f-a000-240b788b14d0 |  | button | ESD graphic display | Yes,N/A
button | c2dccac6-6065-55ee-821e-cfe8f4cda715 |  | button | Alarm Recording and Text | Yes,N/A
checkpoint-status |  |  | checkpoint | Additional checks
button | 7b1d1578-812d-51d2-8657-7f08d153646e |  | button | Control system display and alarms are correct as per control functions | Yes,N/A
button | a813ba46-f34e-5288-80be-4b607bb1c24b |  | button | Transmitter fail direction and burnout are to spec (Upscale/Downscale) | Yes,N/A
button | ec7ef43b-b63a-51cb-8c64-8940affd60dd |  | button | Switch action verified, including power loss | Yes,N/A
button | 895842f3-ac96-5241-b3ef-bb893805d6df |  | button | Drawings, documents and As-Builts scanned and attached | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-105 Control Panel |  |  |  |  | Yes | ITR-CL-1-105 Control Panel | c875822b-78ca-4f91-b278-d4c46264c657
checkpoint-status |  |  | checkpoint | Control Panel
button | b32d8822-1353-5faf-8885-16285f555a51 |  | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | 97775b31-6c59-5c38-97e7-faa0f79c54d3 |  | button | Check holding down/mounting arrangement is correct. | Yes,N/A
button | c6564c61-370c-5dfd-af7b-ac634022aa9b |  | button | Check for mechanical damage. | Yes,N/A
button | 5a0b37f2-3c66-512a-913f-25fdd58a12c6 |  | button | Check tightness of circuit connections. | Yes,N/A
button | 2d9e2ffc-ce5f-5879-a79b-95b7019e6c0b |  | button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
button | 6e4c2e2c-19a6-54d0-a92a-78e0458a07de |  | button | Ammeter scale and current transformer correct. | Yes,N/A
button | 4d78ad12-1e63-5aab-8cba-8f294bbe7547 |  | button | Check internals for cleanliness. | Yes,N/A
button | 6672607f-dbe1-50f6-a535-09eebcfc9c58 |  | button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
button | c3cac6f6-ff46-57cd-a687-2e0c862a7aea |  | button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
button | 28cd137b-01c6-5f66-8d4e-68584f0083ff |  | button | Heaters correctly installed. | Yes,N/A
button | ffd04a09-51f4-5631-8a62-72a2c8d36942 |  | button | Fuse rating correct. | Yes,N/A
checkpoint-status |  |  | checkpoint | Electrical Checks
text | 48527285-cf10-596b-b759-6eecee08cb68 |  | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
holdpoint |  |  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation) |  |  |  |  | Yes | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation) | cb6e5c5f-8ee3-474c-8cb6-a81ff740e4da
checkpoint-status |  |  | checkpoint | Equipment
button | c7902cfb-91a8-5221-ace4-52220adfc729 |  | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
button | 71885bce-d253-55aa-aad6-1f6e8b3f00ae |  | button | Equipment checked for additional items as applicable | Yes,N/A
checkpoint-status |  |  | checkpoint | Valve
text | 973b94f3-475e-5c09-ac58-26f45d41ebe1 |  | textbox | Valve Size:
text | f20d9d4d-85b2-5a40-8dd0-eed2475e8bbc |  | textbox | Flange type:
button | 46178969-5f15-5787-967e-863a89227d55 |  | button | Material certification correct | Yes,N/A
button | dfd1b5de-f2c2-5283-bcd2-dd64538b2fbf |  | button | Trim material correct | Yes,N/A
text | 1456995c-c9c8-515f-8646-65968398415c |  | textbox | Rating:
text | d9937dd5-b397-5c5a-b005-517fdf84e468 |  | textbox | Service:
button | 6d28f2af-9daf-56df-9677-24b936328a25 |  | button | Body material correct | Yes,N/A
text | 5d3f0c67-e22a-5d31-94c0-5dcde54f30fb |  | textbox | Leakage class:
checkpoint-status |  |  | checkpoint | Actuator
text | ea7a4302-e31b-5d16-9163-9b69fbc71306 |  | textbox | Input range: |  |  | kPa
button | 4b4228e1-3a1a-58d9-b97c-6fefb9148e4f |  | button | Failure action | Yes,N/A
button | ab7fed77-7f58-547c-a589-3dcc6d39745a |  | button | Hand wheel operation correct | Yes,N/A
checkpoint-status |  |  | checkpoint | Positioner
text | 9f9f468f-b7eb-5cb2-bee2-4a391dc38bba |  | textbox | Signal range
text | 28a5795d-b6dc-5958-87ef-423101e4c7b3 |  | textbox | Output range
checkpoint-status |  |  | checkpoint | I/P Converter
text | c28cfeb1-1625-5399-94a5-8b013f789ddd |  | textbox | Signal range
text | f6dda411-d9ab-5ecf-b26e-9962402b51f9 |  | textbox | Output range
checkpoint-status |  |  | checkpoint | Filter/Regulator/On-Off Valve
text | d39e7391-c9dc-5e77-b9d2-4a7d9c6e01eb |  | textbox | Range |  |  | kPa
text | 3b3b07a2-f274-5b91-ac1e-4326125d8d3c |  | textbox | Pressure setting |  |  | kPa
button | 28d8afca-429e-5a36-ba0d-b32abd7deac8 |  | button | Stroke Time correct | Yes,N/A
text | 7a3a8aa0-b4a0-5d29-acec-8e10a7739541 |  | textbox | Open |  |  | sec
text | eddc7056-f6b2-51ad-b7a6-b766b2ed6c50 |  | textbox | Close |  |  | sec
button | ffc3d9f6-1adc-59c1-af3b-bfa1ef97e584 |  | button | Open/Close times conform to commissioning specifications | Yes,N/A
checkpoint-status |  |  | checkpoint | Fail Action
select | ec614ba9-235a-594e-a1c7-197827b5dc88 |  | dropdown | Electrical Fail Action | FO, FC, FL
select | 1e269914-91f1-58b1-9190-82ba3aa37633 |  | dropdown | Motive Force | FO, FC, FL
checkpoint-status |  |  | checkpoint | Valve Field Calibration and Hysteresis Check
boolean | ec856f7d-5948-5501-a248-63d28d70d62e |  | tickbox | Confirm test equipment is within calibration period prior to testing
label | 4ecce144-7b92-5376-a8fe-9d25739a69ab |  | note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
button | fc906e42-ff91-5aed-8b52-b7a39f44db3a |  | button | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100% | Yes,N/A
checkpoint-status |  |  | checkpoint | Proximity Detectors
button | 04cb349a-1c6f-5eea-ab26-85787735f476 |  | button | Open switch set, correct mode setting | Yes,N/A
button | 8cc87a8e-f8b5-56dc-b10a-dfe5e65a97d8 |  | button | Closed switch set, correct mode setting | Yes,N/A
button | 6b496ae2-8a2a-5e38-8e80-fa765b80c4f4 |  | button | Electrical connections and certification correct | Yes,N/A
checkpoint-status |  |  | checkpoint | Solenoid Valve
button | 636044cd-24db-507f-a623-010ac1276448 |  | button | Operation correct | Yes,N/A
button | 825a6f2e-3bfd-5f04-9627-c8e72439318d |  | button | Electrical connections correct | Yes,N/A
button | a5a070ca-4531-58e6-9b16-c2a979213aee |  | button | Electrical certification correct | Yes,N/A
text | 8c15cfd9-ce6b-59f0-9944-7b5c80044bec |  | textbox | Voltage: |  |  | V
button | 624b2e20-bee3-5885-bc05-3f03ebefc6ae |  | button | Pneumatic connections correct | Yes,N/A
text | c6f14b9f-450f-5187-af0b-1e63d1affbc1 |  | textbox | Pneumatic pressure |  |  | kPa
checkpoint-status |  |  | checkpoint | Pilot Valve
button | 3a1d4e7b-6274-5ca2-bf6a-cd2e64e24abd |  | button | Pneumatic connections correct | Yes,N/A
button | 0ff1938e-c0ce-5503-ac50-7b00f7a334e6 |  | button | Operation correct | Yes,N/A
button | 68617ca0-7a10-5bf7-9d34-ff60b33b6661 |  | button | Action/Lockup | Yes,N/A
checkpoint-status |  |  | checkpoint | Hydraulic Actuator
text | 036099cb-3bb7-5f84-85a2-37263c265a39 |  | textbox | Working pressure
text | a8d86c7d-51e2-5730-a39f-eb731ad29d79 |  | textbox | Manifold pressure
text | 2e2a6b4d-e0c9-5d86-999a-8d648dc9e31a |  | textbox | Fluid type
button | 1f5173af-7b7f-5d87-8ed3-256ac6b591e2 |  | button | Hydraulic connections correct | Yes,N/A
text | f72452df-ab6f-5271-a347-de98a3718a92 |  | textbox | Regulator pressure setting
button | a62b06dc-d632-5faa-a886-7f19368bb4f7 |  | button | Pilot operation correct | Yes,N/A
checkpoint-status |  |  | checkpoint | Accumulator
button | 3bf6099a-5f6d-5d4e-bd7a-16979f529e99 |  | button | N2 Charge required | Yes,N/A
text | 4c5449a4-0ec8-5004-87f1-08930390d5ef |  | textbox | N2 Pre-charge pressure
text | ff4e652b-ceca-516c-b404-3ed4ad5368c2 |  | textbox | Pressure switch setting
text | 5567df27-7709-520a-ab43-37b13f72b8d8 |  | textbox | Working pressure
text | c0522002-1dae-5fed-a3f7-c043c09a2efe |  | textbox | Output range
button | 196ad47c-8082-5bb5-9add-53d69ea5257a |  | button | Volume tank & check valve installed correctly | Yes,N/A
checkpoint-status |  |  | checkpoint | Electric Actuator
text | 84e375bd-edcf-5a31-b959-00c66a045863 |  | textbox | Voltage:
button | 2b8a5344-b4fc-58ce-8c3e-d5327a046dae |  | button | Electrical certification correct | Yes,N/A
button | 3003da78-38ff-5327-93e1-7add060dee85 |  | button | Electrical connections correct | Yes,N/A
button | 9fa4f9d0-7ae5-50e4-a995-52c4ab144116 |  | button | Remote operation correct | Yes,N/A
button | 96f775c8-715b-5289-a875-4ac20e781985 |  | button | Local hand operation correct | Yes,N/A
button | 1e2878e8-d699-5703-ac7e-4b52dd229efc |  | button | Torque switches and travel stops set | Yes,N/A
checkpoint-status |  |  | checkpoint | Miscellaneous Equipment
text | dd2193cf-450f-522e-9330-aaf0e6a2d7ff |  | textbox | Description
text | 05d4c2dc-1e67-5653-986b-0445b024b51e |  | textbox | Manufacturer
text | a3940dc7-1266-583e-ac24-f1d0978f7aff |  | textbox | Model No:
text | 334edf41-6e51-5019-999d-03dd0b9909d1 |  | textbox | Serial No:
text | e3ddc484-f2ad-5601-8d8a-4881522e51e1 |  | textbox | Range:
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-117 Instrument Tubing Installation |  |  |  |  | Yes | ITR-CL-1-117 Instrument Tubing Installation | d813f88f-26c7-4ad3-8d07-9ff23921029e
checkpoint-status |  |  | checkpoint | Checks Pre-Installation
button | 2e7fc366-26f6-5021-8aeb-271a33e5282f |  | button | Tubing connection to and from equipment as per drawings. | Yes,N/A
button | 9ca1d4f5-95e2-5a47-8b4e-73e78d1f79e5 |  | button | Tube material type, size, gauge and standard confirmed and available | Yes,N/A
button | 843f4816-9c4b-55d5-9da9-9c719e8bcddf |  | button | Tube fitting size and type confirmed and available | Yes,N/A
checkpoint-status |  |  | checkpoint | Checks During and Post-Installation
button | 4968da8e-676b-5ef3-bdba-b430d7ad1d52 |  | button | Correct thread compatibility and engagement | Yes,N/A
button | 84be2f7d-f244-5d87-a8ed-adff19279816 |  | button | Correct thread tape and sealant used on fittings | Yes,N/A
button | 0cfcae7a-f9b5-57e1-8fc7-32ebcede9857 |  | button | Check fitting ferrule orientation and confirm prior to connection | Yes,N/A
button | 49722970-578c-56ae-b877-09e9203c11e5 |  | button | Tube installation is in compliance with the client specification. (Supports, bracketry, slope, expansion, vibration, access, cables) | Yes,N/A
button | 70763579-d4d8-56c6-a6ec-bb4ba1a5c649 |  | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
button | c2e51bd9-35f8-50e0-9389-00c99de63ea7 |  | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
button | 52ca6a4f-fe50-5c4d-8cb9-16bdeacfc70c |  | button | Depth insertion tool used; witness mark visible at all stages of process | Yes,N/A
button | 66858c37-fbb2-578d-811b-66e29a58aff3 |  | button | Tube fitting hexes marked to ensure correct swage tightness | Yes,N/A
button | e8c5a865-c141-5574-97df-4ce185ce3988 |  | button | Random check with No-Go gap gauge | Yes,N/A
button | 6306f1ee-a88c-5e02-b5d3-513693e4dbfe |  | button | In service leak test performed and passed (ITR-CL-1-118) | Yes,N/A
button | b77b2185-19d4-575a-996e-f93077065e0d |  | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
label | 8312427c-3f1e-5a34-a83f-13a43b12be7b |  | note | Refer to Swagelok book for tube/thread size pressure ratings
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-sectioned |  |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | dda5a4e5-cc60-4243-9795-36ca923cc72a
checkpoint-group |  |  | section | Toolbox meeting
checkpoint-no-status |  |  | checkpoint | Toolbox meeting
date | da98d349-009c-5dbb-aded-33660590f394 |  | date | Date:
text | b0c2f5f3-8c74-5db3-ae82-57d532528533 |  | textbox | Meeting location:
text | 1571e769-db4c-5060-be7a-4bdfe3bdaa39 |  | textbox | Meeting conducted by:
text | f08798a0-bb3a-5f99-bcdb-0c1b059e3de6 |  | textbox | Meeting attendees:
text | 10be6db0-65fb-5ac7-a41d-09e750c341e4 |  | textbox | Today's work scope/Hazards
text | 620957ff-5c29-5c5b-89f5-3b1f659122ee |  | textbox | Hazard controls:
holdpoint |  |  | signoff | PICWS Signoff
checklist-flat |  |  | checklist | Test Equipment Details: |  |  |  |  | Yes | Test Equipment Details: | decb1300-9c78-4713-8884-70b7555d749c
checkpoint-no-status |  |  | checkpoint | Details
text | 4a866a34-da33-5783-8eda-0803536fed2f |  | textbox | Make
text | d22df50f-1070-5906-b3c0-7c4dc5fe5ce4 |  | textbox | Model
text | ba416c92-406b-57d4-b40f-fbb09fe6ac82 |  | textbox | Serial No
text | 6aecfb6a-a654-5cc3-8de7-e0850f9c3fd4 |  | textbox | Calibration Expiry Date
checklist-flat |  |  | checklist | ITR-CL-1-128 Temperature Instrument Installation |  |  |  |  | Yes | ITR-CL-1-128 Temperature Instrument Installation | e3cc43e1-7536-4c6d-81c5-2d5fb3f1933b
checkpoint-status |  |  | checkpoint | Temperature Instrument Installation
button | 40121701-d5a4-5d7b-8ca5-f5bcf7e868c1 |  | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
button | 435b3ada-fb4a-5318-b7d8-e7f8b08d1b33 |  | button | Temperature instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
select | 1191fafb-f55a-5e82-a46c-1a722f57b6c7 |  | dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
button | bf1a36c6-83ba-51b3-b211-e2e6b22ce900 |  | button | Thermowell details including flange size are correct in accordance with the specifications | Yes,N/A
button | 804640f3-5ffc-5ca7-b188-b5a50885a2e0 |  | button | Internal depth of thermowell checked and recorded | Yes,N/A
text | 7763a5c3-ed16-5a59-85c6-62931a0298ae |  | textbox | Depth:
button | f4cf64b4-ecb3-598b-aa05-16a76c52e56e |  | button | Bar material and tag number stamped on thermowell flange/exposed surface | Yes,N/A
button | 94922c1b-4642-512e-bc43-8cbae749d22c |  | button | Thermowell CE marked | YES,NO
button | 726fe10c-739c-5d4b-a353-c91634bbd281 |  | button | EOL resistor fitted and correctly rated where applicable | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-CL-1-132 - Instrument/Control Cables |  |  |  |  | Yes | ITR-CL-1-132 - Instrument/Control Cables | f0cab57a-8677-4248-98ee-aa4a268df183
checkpoint-status |  |  | checkpoint | Instrument Cable
boolean | 4b586dea-8524-57e2-bd82-fb498b11e8de |  | tickbox | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
boolean | 1015a2e0-7024-5955-9cb7-bf3b859d7de1 |  | tickbox | Check dressing / cleating, cable undamaged
boolean | 2434bd05-bb7d-5af2-9c93-409566b9154c |  | tickbox | Cable mechanically protected
boolean | 0dd1efb9-fae9-5160-85fa-66773beb780c |  | tickbox | Cable terminated with correct lugs and crimped with the correct die.
boolean | aa6a4488-6bbc-57e2-b238-8431f5ffa129 |  | tickbox | Screen correctly made off
boolean | 04133039-5e75-5b4e-a24e-41ce66f52b1a |  | tickbox | Glanding / Locknuts correctly installed.
text | ea63889e-fa37-57d1-a654-b6ce558197f8 |  | textbox | Gland type - from: |  | Haz. Area Rating
text | 24270c61-7851-5fb5-b525-602cac73aa55 |  | textbox | Haz. Area Cert Details.
text | c96cb602-9d18-5941-84fe-1aa2103d121f |  | textbox | Gland type - to: |  | Haz. Area Rating
text | e2af27cf-b385-579f-bf76-3fede25e79e3 |  | textbox | Haz. Area Cert Details.
boolean | 1d3748a8-aa40-5286-909a-ccffadd9a097 |  | tickbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
checkpoint-status |  |  | checkpoint | Electrical Checks
text | 53aa764e-a12d-5622-aeba-2590e8356ffe |  | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
checklist-flat |  |  | checklist | ITR-CL-1-108 Electrical Switch Rooms |  |  |  |  | Yes | ITR-CL-1-108 Electrical Switch Rooms | f2e0dc3e-8c24-4c3f-9167-723e7a65b28b
checkpoint-status |  |  | checkpoint | Electrical Switchroom (Mandatory Photo)
button | c35c8c3b-6e5f-5852-8138-e12183b47e82 |  | button | Ensure all equipment is installed in accordance with layout drawings and equipment schedule. | Yes,N/A
button | 9cb19cf9-3094-5dd8-b75f-c9e71c4da266 |  | button | Ensure all equipment is installed as per manufacturers instructions. | Yes,N/A
button | 6a9f984c-8d46-531e-ae34-602a384296e1 |  | button | Ensure there is no visible damage to installed equipment. | Yes,N/A
button | 38133667-8af5-5f22-9190-904b05cc6b48 |  | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
button | 1bb30d2e-808b-5e4f-b3d6-1a59666c3f13 |  | button | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified. | Yes,N/A
button | 39b51e08-1787-5c74-8ef1-2f12f5dc619c |  | button | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar. | Yes,N/A
button | 506a4e85-a11e-50cd-b2ae-3f34b9aaffe8 |  | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
button | 194f3185-12e2-5655-aa25-e24355f795e8 |  | button | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
button | 513c5db0-c432-5a6b-8e94-d5956b35794f |  | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
button | 987ea7a8-ff94-5ca8-b9b2-f4ceda30a358 |  | button | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel. | Yes,N/A
button | c2c4ff65-2e25-515c-98e2-46b89ca72d6a |  | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
button | 8251fa54-2619-5f08-a5cc-8bc7e06dfb45 |  | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
button | 8782e416-2329-5221-98d9-08b14c73962c |  | button | Equipment IP, Ex ratings correct. Check tightness for all circuit connections | Yes,N/A
button | cac4a24a-fec9-53cf-8a0d-394f91f9eda7 |  | button | All internal cables and wiring is correctly numbered, colour coded and terminated | Yes,N/A
button | d9a8e4db-3fc8-58f7-a3cd-6245104a996e |  | button | Check internals for cleanliness | Yes,N/A
button | 95d95cd8-dd26-5176-8d7c-f8dd08d99591 |  | button | Relays Metering and Protection ratings are correct as per design | Yes,N/A
button | 3ad5afe7-96ec-5205-9dad-f7e3848b1c62 |  | button | As-builts complete | Yes,N/A
checklist-sectioned |  |  | checklist | As-Built Drawings |  |  |  |  | Yes | As-Built Drawings | f31ce4cc-3a42-4793-a35e-47c300c460f7
checkpoint-group |  |  | section | As-Built Drawings - attach scanned documents
checkpoint-no-status |  |  | checkpoint | As-Built Drawings - attach scanned documents
text | 97c91d10-8a66-5e83-90c0-ef3afede49b8 |  | textbox | Drawing no.
checklist-flat |  |  | checklist | ITR-CL-1-112 Motors |  |  |  |  | Yes | ITR-CL-1-112 Motors | f63b6973-ff3f-49b2-bd81-3501be3ddbc2
checkpoint-status |  |  | checkpoint | Motors installation
boolean | 481f033e-46c8-5430-b530-6f504e55bdbb |  | tickbox | Tag number, area classification, IP rating correct as per drawings and equipment schedule
button | 88c4988e-d18e-5e59-8c4b-6484dfd5c17f |  | button | Space heater | Yes,N/A
text | 47f7463d-fb36-563e-89c8-501bad7c1569 |  | textbox | Space heater specification (Power (Watts) and Voltage:)
checkpoint-status |  |  | checkpoint | Nameplate details correct and in accordance with the data sheet (Mandatory Photo)
label | 73a15ef7-a7ab-543b-88d7-1ca840163365 |  | note | Upload clear photo of nameplate
checkpoint-status |  |  | checkpoint | Checklist items
button | d173609e-3e03-5d51-965a-5b0e1db325ec |  | button | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets | Yes,N/A
button | d78a2bae-0d71-5dd3-a29c-8bdd83d3cfed |  | button | Identification Tag and Rotation Plate correctly fitted | Yes,N/A
button | 6c5ab35a-a8bf-536c-8c9d-a833e064cd07 |  | button | Motor electrical coupling (Delta/Star) is correct. | Yes,N/A
button | 55c44db7-a0fe-53b4-9b37-a0039b77be66 |  | button | Check for mechanical condition, air ducts and fan free of debris | Yes,N/A
button | 92238dca-2d29-5bed-80f2-44e4db9408dc |  | button | Correct glanding for area classification. | Yes,N/A
button | 75e0a3c4-6588-50e6-8a4b-918df7a2f881 |  | button | Holding down bolts fitted correctly. | Yes,N/A
button | 7866c60e-e106-5a1e-aad5-30fb8248593a |  | button | Check bearing lubrication, free rotation with shaft uncoupled | Yes,N/A
button | 890fb388-d930-5723-a4c5-a6ac805f468d |  | button | Cable(s) correctly terminated, labelled and colour identification | Yes,N/A
button | 774fc876-b113-5771-bb52-817081b294bc |  | button | Terminations/connections torqued correctly to data sheets. | Yes,N/A
checkpoint-status |  |  | checkpoint | Motor Installation Testing
text | 16f8af62-d6d0-51ab-b8a7-f880c9595eb9 |  | textbox | LV Motor winding insulation resistance with supply cables disconnected; 1 minute test
label | 87efb043-7852-5434-b74f-5895c1d22b39 |  | note | Insulation resistance U, V, W
text | c9db8775-ca52-5fec-a144-234e961e5c9c |  | textbox | LV Motor winding insulation resistance with supply cables disconnected; 10 minute test
label | a7ca9aef-9cb7-5178-bc50-97f58c58ecb6 |  | note | Insulation resistance U, V, W
text | e440f398-1b1f-595e-8d57-d7738c1f20d1 |  | textbox | Motor continuity between windings
label | c33dab3b-e5d0-5e71-a1e9-fcb65f2c5561 |  | note | Continuity U1-U2, V1-V2, W1-W2.
text | 5692b944-3d62-5378-96d9-2d08640ed6ef |  | textbox | Space heater continuity & resistance check
label | 832cb8eb-373f-53a3-8db7-0431fb43e82d |  | note | Continuity & Insulation resistance results:
text | 696c7508-4ab7-535d-b554-cc4f03324fe1 |  | textbox | Thermostat or RTD wiring resistance check
label | 3cbbd2db-5840-594a-81c1-779596aabf45 |  | note | Resistance:
text | c45f3e5a-11d5-5281-b95e-25a319732177 |  | textbox | Check motor is earthed correctly and record motor earth bond:
checkpoint-status |  |  | checkpoint | Additional checks
boolean | 9b10d71f-3358-507d-8a4a-20893d8d6f74 |  | tickbox | Winding temperature detector
boolean | 1609bd00-806f-5fcc-849c-5d4e4e07be9e |  | tickbox | Air temp detectors
boolean | 5474f5ca-d6b1-5888-a4bb-ad0f40e3eb48 |  | tickbox | Bearing temp indicators
boolean | 76cb80fc-a5da-55c6-ba74-6904835b8bd0 |  | tickbox | Vibration Monitors
boolean | 700fd2bc-8cce-59c0-b270-ba655c37ff4f |  | tickbox | Condensation detector
button | ad7a159c-e128-5124-b632-ab7f525a6695 |  | button | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable) | Yes,N/A
button | 3080b9a2-d7b9-5fab-9678-883bf29f3898 |  | button | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable) | Yes,N/A
button | 45e0c59b-ebdc-5bf7-83fd-6aa3efd96f3a |  | button | Installation conforms to specification and drawings | Yes,N/A
button | 4c6f4151-1a21-5825-9277-5c1539c7db16 |  | button | As-Builts complete | Yes,N/A
holdpoint |  |  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
checklist-flat |  |  | checklist | ITR-I-44A Fibre Optic Cable |  |  |  |  | Yes | ITR-I-44A Fibre Optic Cable | f76c9783-b2fd-4cd2-b55a-0dbbb950230e
checkpoint-status |  |  | checkpoint | Fibre Optic Cable
boolean | f8967535-d5a8-52a8-a7a1-a55b3561d3f1 |  | tickbox | Verify cable type, size, colour code and tag is in accordance with the Cable Schedule.
boolean | f4c44eb3-41e9-56f1-b936-d386aadda08d |  | tickbox | Check cable optical fibre loss and record data in the attached report.
boolean | 2c077374-8e9e-51fc-a03e-99a7495df09c |  | tickbox | Check fibres correctly identified and labelled.
boolean | ec513bd3-3461-57f1-ad84-05b090eb3b97 |  | tickbox | Check fibres correctly terminated and secure.
boolean | 1d38d5f7-7e87-54e9-8cad-a38ac9b7c212 |  | tickbox | Upload Contractor OTDR report
checklist-flat |  |  | checklist | ITR-CL-1-109 Electrical Equipment Package |  |  |  |  | Yes | ITR-CL-1-109 Electrical Equipment Package | fae573fc-30df-421b-9218-c5516980b784
checkpoint-status |  |  | checkpoint | Electrical Equipment Package
button | de1a4929-51d8-5010-bb5a-8acbeaef7579 |  | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
button | 72770694-ba7a-53a3-8049-ada9f0bd30b5 |  | button | Check equipment is correctly rated for the area. | Yes,N/A
button | 46e6b0ba-1237-5410-8e55-8782af342125 |  | button | Check if package is complete with all accessories. | Yes,N/A
button | 0e7ade92-ffba-519f-99b4-c1ace5282e56 |  | button | No mechanical damage and paintwork in good condition. | Yes,N/A
button | 054459c2-a788-5880-b639-bad34d3ef7ab |  | button | All transportation supports, stops and fastenings removed. | Yes,N/A
button | 91359383-e280-5b6e-92b6-97eb0e6046b6 |  | button | Package fixing down bolts/shims/washers installed and tensioned. | Yes,N/A
button | b6048e1f-0a8d-5bd7-a133-d4dede4e475e |  | button | Check package is installed on a level plane. | Yes,N/A
button | eb88b8e2-3dd1-5fee-a01f-8a04c9481d2d |  | button | External cabling (if required) correctly installed. | Yes,N/A
button | f0753463-a336-5ecd-b492-08f4dd0684ec |  | button | Internal equipment installed and all tests complete and accepted. | Yes,N/A
button | 7c187dfb-945b-5f5d-b74c-ec1330baa79b |  | button | Verify package using vendor and/or project P&IDs. | Yes,N/A
button | 9fdec3f6-3e46-5769-9cad-68cd22178037 |  | button | Check that equipment is correctly earthed. | Yes,N/A
text | 576774d6-4e9c-5045-b609-1f8c9697a62e |  | textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  | Ohm