## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0398-ITP-014 Electrical Conduit Installation Rev 1 | itp |  |  |  |  | INF-HSEQ CC0398-ITP-014 Electrical Conduit Installation Rev 1
section | 1.0 Pre-start activities
checkpoint | 1.1 - Set out
label | Ref docs - Composite Drawings
label | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
label | ○ IFC and latest available revision used?
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
checkpoint | 1.2 - IFC Submission & Approval
label | Ref docs - Composite Drawings
label | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Permits
label | Ref docs - Symal Safety Procedure
label | Acceptance criteria - Have the below permits been created.
label | – GPP
label | – Working at Heights
label | – Hot Works
label | – Confined Space
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
checkpoint | 1.4 - Determine Lot Size
label | Acceptance criteria - Has the lot size been determined?
button | Frequency | Yes,No,N/A
label | Key - S
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | LOT map
checkpoint | 1.5 - Delivered materials
label | Acceptance criteria - Has a material inspection checklist been completed?
label | ○ Have the materials and tag numbers/heat numbers been verified?
button | Frequency | Yes,No,N/A
label | Key - W
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Inspection Checklist
checkpoint | 1.6 - Electrical and Earthing Pre- Qualification
label | Ref docs - 235929- MG1668-CV- 003-SUBC-000181
label | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Welding Qualifications
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.7 - Backfill Materials Approval
label | Ref docs - 235929- MG1668-CV-
label | Acceptance criteria - Has bedding and backfill materials been approved for use?
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | Approval number:
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Excavation and Placement
checkpoint | 2.1 - Service Location
label | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
label | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - S
checkpoint | 2.2 - Excavation
label | Ref docs - 235929-000- CV-SP- 00006 UG PIPE FAB and INSTALL Section 12.1.12
label | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.
label | ○ Trench width to provide 50mm from edge of trench to conduit walls at minimum.
label | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
button | Frequency | Yes,No,N/A
label | Key - W
label | MDR/VIVA - S
checkpoint | 2.3 - Conduit materials and size
label | Ref docs - 235929- MG1668-CV-003-SUBC-000112 (Shop Drawings)
label | ○ 235929-MG1668-CV-003-SUBC-000009 (UG Services AMS)
label | ○ 235929-154-CV-08-92002-080001 (Rev1) & 080002 (Rev1) & 080005 (Rev2)
label | Acceptance criteria - Are the HDPE conduits approved for use?
label | ○ Have the conduits been installed using approved couplers?
label | ○ Has the installation of the couplers been reviewed by the client?
label | ○ Has the bend radii been checked and adheres to the drawing?
button | Frequency | Yes,No,N/A
label | Key - W
label | MDR/VIVA - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.4 - Conduit placement
label | Ref docs - 235929-154- CV-08- 92002-080001 (Rev1) & 080002 (Rev1) & 080005 (Rev2)
label | Acceptance criteria - Have the Conduits have been placed as per drawings and specifications and inspected by a VIVA representative?
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.5 - Backfill placement & Marker Tape & Rope
label | Ref docs - 235929-000- CV-SP- 00002
label | Acceptance criteria -
button | ○ Have all trenching works been recorded for as- built and digital data prior to backfilling? | Yes,No
button | ○ Has bedding material/sand been placed for the full width of the trench over the conduits for a minimum cover depth of 200mm? | Yes,No
button | ○ Has marker tape been placed in-line and above the conduits on the surface of the sand layer? | Yes,No
button | ○ Has draw rope been installed through the conduit? | Yes,No
button | Frequency | Yes,No,N/A
label | Key - W
label | MDR/VIVA - R
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Photos
section | 3.0 Finishing
checkpoint | 3.1 - Clean-up of site
button | Acceptance criteria - Have the areas affected by the works been restored to a condition similar to that which existed prior to the commencement of the work? | Yes,No
button | Frequency | Yes,No,N/A
label | Key - S
label | MDR/VIVA - S
checkpoint | 3.2 - Identification and recording
button | Acceptance criteria - Have the actual installed location and depth of the conduits, and location of pits, been accurately recorded on an as-built? | Yes,No
button | Frequency | Yes,No,N/A
label | Key - S
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | As-built
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Work is complete and complies with design plans / drawings / specs
label | Acceptance criteria - Redline mark-ups As-Built Survey: Conduits to conform to the required depths and locations.
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | As-built
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Certificate of electrical safety
label | Acceptance criteria - Electrician to supply Certificate of electrical safety for conduit installation witnessed
button | Frequency | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Certificate of electrical safety
holdpoint | AUTHORITY HOLDPOINT