## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 1717b3dd-adb1-40bb-956d-280abc0f23df |  | checklist | ITP No. 7 - Structured Cabling Rough In |  |  |  |  | Yes | ITP No. 7 - Structured Cabling Rough In | 0fb27be3-074b-4e19-af9f-a2e5eb5fb066
label | 10ac250a-a5ce-4456-974a-a5cdac67f654 | Data not allowed on checklist-flat. | note | Refer approved drawings and specification.
checkpoint-status | edfaec3d-c028-4f4a-a3d8-27da8a2d7d45 |  | checkpoint | Install cable support or conduit where required.
checkpoint-status | d866d67f-048d-4bd4-b3e1-5ff031120835 |  | checkpoint | Verify correct cable type.
checkpoint-status | 957b606c-98e0-43a3-b505-52f62e712279 |  | checkpoint | Refer to approved drawings for cable numbering sequence relevant to final fit off sequence & record
checkpoint-status | c4aacdb5-acdb-42ea-82fe-a122b9402a9f |  | checkpoint | Install cable within or on cable support systems maintaining min segregations, ensure velcro cable ties are used as per specification
checkpoint-status | 8e60552e-447d-486a-9e9a-e7d1e6c39420 |  | checkpoint | Form cables into relevant fit-off groups at the cabinet end.
checklist-flat | aa27e7c6-3a4d-47f9-9070-3158ebf402d9 |  | checklist | ITP No. 9 - STRUCTURED CABLING TESTING CERTIFIED SYSTEM |  |  |  |  | Yes | ITP No. 9 - Structured Cabling Testing Certified System | 0fc52370-41e2-4faa-a815-6e0050b763f5
checkpoint-status | b1a9e525-b290-4912-9179-de61c83ccbb6 |  | checkpoint | Refer to installed drawings
checkpoint-status | c1733812-2f1c-48e0-8d5b-ee3dcab2790c |  | checkpoint | Test terminations using copper structured cabling tester and log results
checkpoint-status | 64b89b32-c7be-45b1-a95d-bb35eacc6419 |  | checkpoint | Rectify any failed results, re-test and log
checkpoint-status | 8f64be17-fb94-4f4c-87ef-416339b4836d |  | checkpoint | Label frames and patch panels
checkpoint-status | 1c06cc8f-21ae-4191-b61f-f7a25a2e60b4 |  | checkpoint | Complete patch panel schedule
checkpoint-status | 0c0dfe23-c7ff-4a34-8de1-413323a2aebd |  | checkpoint | Download results from tester to project folder
checklist-flat | 4578429c-4272-4d6d-adf2-c02b60ea7fff |  | checklist | ITR No. 33C - Installing Underground Services (Comms) |  |  |  |  | Yes | ITR No. 33C - Installing Underground Services (Comms) | 2d4c901a-af74-4fac-9b62-78b982189cc8
checkpoint-status | 95ab6e3e-9067-4409-87a5-b228da8cb6c2 |  | checkpoint | Inspect conduit material to check that it meets material specifications
checkpoint-status | 3cc07a1f-25af-4ae3-84b5-15cf861b736c |  | checkpoint | Check conduit alignment as per plans
checkpoint-status | 3a731c29-0312-429f-9389-ca590e430f0d |  | checkpoint | Set out marked, and all services located
checkpoint-status | 748fa309-dbc3-4219-8cba-36069455e710 |  | checkpoint | Erect pedestrian barricading as per plan
checkpoint-status | e1d19080-c3fd-4112-a55f-92c9f10c7970 |  | checkpoint | Check excavation depth against proposed road level
checkpoint-status | 66176f84-59ec-497e-9d15-64bf0c3f3a32 |  | checkpoint | Excavate to the trench as per plan
checkpoint-status | 425d9923-7af4-4421-8932-849a12ff3c27 |  | checkpoint | Place specified bedding material in trench
checkpoint-status | b128d2cd-7307-475f-8f54-913f83761db1 |  | checkpoint | Placement of conduit of specified size in accordance with specifications/drawings
checkpoint-status | a9360902-d3ba-47cf-bac7-530288a48cff |  | checkpoint | Backfill over conduit to 450mm
checkpoint-status | cb4a4f41-f288-4c94-8e93-c7a990e36a89 |  | checkpoint | Install cover slabs over conduit (if necessary)
checklist-flat | 9ec185b8-932e-447c-a54b-c3513bb67191 |  | checklist | ITR No. 34 - Installing Light Pole Footings/Cages |  |  |  |  | Yes | ITR No. 34 - Installing Light Pole Footings/Cages | 38f9b280-e649-484b-9a93-be6c8423c7df
checkpoint-status | 607be333-a8c9-4a01-9a73-d451f02655fc |  | checkpoint | Inspect cages for any damage prior to installation
checkpoint-status | 8709b2b5-605a-4280-9ce9-3208058e2f2c |  | checkpoint | Set out light pole location, alignment and state height as specified
checkpoint-status | 819b7d37-2a4c-4e5e-a11f-c2d4ca67b51d |  | checkpoint | Erect pedestrian barricading as per plan around work area
checkpoint-status | 4a40602c-625c-412a-bbb7-09d23802e2b1 |  | checkpoint | Excavate as per plan, placing specified bedding material as per requirement
checkpoint-status | 3d486f90-52d2-4289-ad30-45f4af8f9881 |  | checkpoint | Install light pole cages and conduits as required
checkpoint-status | 2c75b540-86ac-4c75-b6ce-76b407d1fb35 |  | checkpoint | Recheck finshed height as per civil drawings
checkpoint-status | 3d1a1549-08dd-4070-b3f6-ec00e4dea229 |  | checkpoint | Pour concrete footing with specified mpa
checkpoint-status | f4df20bc-19d0-4163-a4ec-a0ce3f5db58b |  | checkpoint | Clean up and barricade work area
checklist-flat | 8e45ecd9-af42-4c38-b02c-b3bfcdf489c7 |  | checklist | Pre-Start Meeting |  |  |  |  | Yes | Pre-Start Meeting | 3eb961c7-53b6-4c40-8092-1891ba253021
checkpoint-status | de7e192d-f554-4ca3-a9f1-7bd40808e56c |  | checkpoint | Attach any relevant photos or documents
text | a7f32f25-b6f9-5681-8b0a-f11f963a4d56 |  | textbox | Area:
text | ecd6a2bd-04ef-52b0-8f7c-3009aaa78a29 |  | textbox | Conducted By:
text | d620a280-ddf6-58db-861f-7550fb5661f7 |  | textbox | Task/s:
text | 4953927d-09fc-527d-9ab4-31c3549e5aa1 |  | textbox | SWMS
checkpoint-status | 8b96f90e-c8d4-4cc8-92db-4eb929693b20 |  | checkpoint | Have any hazards been identified?
text | 49621d45-1a58-5255-9e49-97b277ac5c9b |  | textbox | Newly identified hazards are
text | bdd1ed25-036a-5589-88ab-44c211cc6a09 |  | textbox | Control measures are
text | 1b7d708f-72b0-5123-a452-950db40bab58 |  | textbox | Responsible person
checkpoint-status | 59159761-e973-47bf-b612-2622b5672df4 |  | checkpoint | Scope of work for the week was discussed and understood
checkpoint-status | 3ac9a681-9afa-4b6d-88b9-731acef2c341 |  | checkpoint | Relevant SWMS were reviewed, understood and signed by all workers
checkpoint-status | 72b08b52-313b-4a0e-9104-bb773911c593 |  | checkpoint | Tools and equipment are in good working order
checkpoint-status | 549a9c2e-c962-4ab8-8ee5-b09e34880bec |  | checkpoint | All electrical equipment displays current test tags
checkpoint-status | fc6d7576-f105-44fd-a9f5-97edfd671b87 |  | checkpoint | Appropriate PPE for tasks is understood and available
checkpoint-status | e2d5dfcd-d390-4434-a12f-1acfc9331893 |  | checkpoint | Housekeeping and clean-up has been discussed and is understood
checkpoint-status | 15e869f6-a6b8-45e4-9df5-77c3fb6d93e7 |  | checkpoint | Attendees - Attach name and signature
text | e2074df0-b05c-5ce6-89cf-38139e9d1bdd |  | textbox | Type Names
checklist-flat | 213c4994-41c8-493e-bb0a-5ca0d7fc3ee6 |  | checklist | ITR No. 14 - Mains and Sub Mains Installation |  |  |  |  | Yes | ITR No. 14 - Mains and Sub Mains Installation | 4c9dac9f-b349-41be-b12c-180fd825424a
checkpoint-status | 723c3be8-be45-455f-8c30-d6f5a77b3e34 |  | checkpoint | Measure cable runs with appropriate accurate measuring instrument eg: tape measure, wheel, rope in conduit
checkpoint-status | 732f90f1-b708-4d06-8ce9-3c56b8708311 |  | checkpoint | Confirm length of cable
checkpoint-status | 15355ed7-c606-4a43-aafa-42c3832e8cf6 |  | checkpoint | Install cable in applicable method eg: cable stands, electric winch, pulleys etc
label | 8d753246-fd9f-5c79-a57c-55409aa7d87b |  | note | Any cable not terminated immediately must have the end taped covering the bare copper
checkpoint-status | 6c4f83aa-08e8-4c1e-bd9f-47ae6b8b093d |  | checkpoint | Trefoil (refer to details on back for all options) cables and tie cables to support system
checkpoint-status | 8c454ac3-f13c-48c1-8044-120b48cbdbe5 |  | checkpoint | Check cable requirements for cable identification and install
checklist-flat | b075bb4c-7783-4e38-aa01-c1069f08a09a |  | checklist | ITR No. 35 - Installation of Underground Pits |  |  |  |  | Yes | ITR No. 35 - Installation of Underground Pits | 51b64a16-c68c-4d38-990a-0a6590b9ea19
checkpoint-status | 2d8e141b-4463-41ea-82ad-6a8e01d4ae46 |  | checkpoint | Inspect pits for any damage prior to installation
checkpoint-status | ebf1071f-316e-4f14-a8ff-d60a42342785 |  | checkpoint | Set out pit location, alignment and height as specified
checkpoint-status | 56eebd71-164e-4e6c-ac59-b80a52493444 |  | checkpoint | Erect pedestrian barricading as per plan
checkpoint-status | e8665302-9e62-4fb4-b4b4-35790a0439ed |  | checkpoint | Excavate as per plan
checkpoint-status | b68963ec-8a83-4555-af7e-8cef3fe4330f |  | checkpoint | Place specified bedding material as per requirement
checkpoint-status | 42231295-b0d3-4c32-b1d9-4021edc01354 |  | checkpoint | Install pit and conduits as required
checkpoint-status | f4b0b20d-f8f3-4df6-9e39-b7dda2eb4a13 |  | checkpoint | Recheck finshed height as per civil drawings
checkpoint-status | 0359884f-ed01-430b-9a98-a9c81cdc6ae4 |  | checkpoint | Backfill and reinstate ground as required
checklist-flat | 8f2b9d40-f1a2-4828-82ea-91e7ca7d92ee |  | checklist | ITR No. 16 - Switchboard Installation and Terminate Sub Mains |  |  |  |  | Yes | ITR No. 16 - Switchboard Installation and Terminate Sub Mains | 62c60010-e1de-4618-a9e1-362ef0fcfe69
checkpoint-status | ffcbe851-0036-4461-a445-2266eebe58b8 |  | checkpoint | Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
checkpoint-status | b01af7fa-337b-4e26-8075-c2ef12fade79 |  | checkpoint | Locate & fix into position
checkpoint-status | 238e4d95-71fa-489a-b751-b30ee7808624 |  | checkpoint | Install sub mains cabling as appropriate eg. glands, tray, duct
checkpoint-status | a6947b8f-33db-4b10-b4ce-5e1852844212 |  | checkpoint | Install lugs and terminate
checkpoint-status | 87dcdfcb-54b9-471b-8e1c-c09d64cb162c |  | checkpoint | Any cables not terminated prior to energisation must be removed from cubicle at origin and have ends covered in heat shrink. at destination cables must be covered in heat shrink and be contained in a junction box
checkpoint-status | e4e5f6ff-1cd7-4326-b7de-c68c30c497f0 |  | checkpoint | Clean & vacuum
checkpoint-status | 24d1583f-1d3e-478e-969d-3348fa084f25 |  | checkpoint | Organise inspection by inspector. lodge prescribed / non prescribed (as applicable) certificate of electrical safety (if required).
checkpoint-status | 68d4c717-28c2-4a96-a6fd-96b9ce08ce70 |  | checkpoint | Clearly identify services
checkpoint-status | 4e38595c-ad86-44c4-aee9-5d9cc273b22f |  | checkpoint | When ready to energise proceed in accordance with energisation procedure
checkpoint-status | 25cc7444-702e-4e99-a064-d663d6f6bdfe |  | checkpoint | Energize & record results
checkpoint-status | 0222ffd0-1f31-474a-9b49-8d539461e984 |  | checkpoint | Check switchboard as installed matches shop drawing. if necessary modify shop drawing to match installed & return to office
checkpoint-status | d0f3c1f6-eb82-4855-9ffb-9ab19938180a |  | checkpoint | Clean switchboard cupboard
checkpoint-status | 92331dc9-318a-456b-9a18-3dd1b837d638 |  | checkpoint | Install sub circuit cabling in accordance with db schedule and terminate. if circuit not complete at the other end, it must not be terminated but placed in a junction box at field end and in connectors at distribution board end.
checkpoint-status | eef1c1bd-a1c5-47ee-9ba6-3d849ab89224 |  | checkpoint | Clean & vacuum
checkpoint-status | 098d70dc-f0c4-4d7b-93cb-4edf5e19fcce |  | checkpoint | Record relevant information and any changes on db schedule. and return to administrator/office for commissioning team
checklist-flat | 26d594bc-522c-494a-ad3e-295853638d1d |  | checklist | ITR No. 33 - Installing Underground Services (Electrical) |  |  |  |  | Yes | ITR No. 33 - Installing Underground Services (Electrical) | 779454a1-dc81-442e-9975-66787ab76eec
checkpoint-status | 8d6a2304-2882-4657-b6db-c1c07d766445 |  | checkpoint | Inspect conduit material to check that it meets material specifications
checkpoint-status | 356c9845-936a-4963-9dc8-9f1fb1251910 |  | checkpoint | Check conduit alignment as per plans
checkpoint-status | 5cab24fa-21fc-492c-a57b-eb1902d078c4 |  | checkpoint | Set out marked, and all services located
checkpoint-status | e7003b46-4277-4dfe-b5ab-0ed10433604a |  | checkpoint | Erect pedestrian barricading as per plan
checkpoint-status | 676680d1-07c5-4e88-9427-0a191c307ee7 |  | checkpoint | Check excavation depth against proposed road level
checkpoint-status | 397bc42b-5f0e-4c94-aaca-49496a311636 |  | checkpoint | Excavate to the trench as per plan
checkpoint-status | 5a521754-90ff-4b35-aa72-6c4236e69ce2 |  | checkpoint | Place specified bedding material in trench
checkpoint-status | b50e7761-3cc7-4ced-bc14-6b945d50dec6 |  | checkpoint | Placement of conduit of specified size in accordance with specifications/drawings
checkpoint-status | 44b5ba86-6ad6-46a7-9650-23690cde73b0 |  | checkpoint | Backfill over conduit to 600mm
checkpoint-status | 8050eb9a-bb13-4e01-8331-949de7703986 |  | checkpoint | Install cover slabs over conduit (if necessary)
checklist-flat | d24af3ab-3e21-4520-b0c0-9b21c9772593 |  | checklist | ITR No.12 - Switchboard Commissioning |  |  |  |  | Yes | ITR No. 12 - Switchboard Commissioning | 9cec2e95-939d-4c07-a903-640ebff60eb0
checkpoint-status | b8767eef-2293-4d4c-a526-f0b905afe35e |  | checkpoint | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure And All Steps Undertaken To Ensure Compliance With This Procedure
checkpoint-status | 708f5541-98ed-41ba-851f-d2cc5af579a9 |  | checkpoint | Refer To As Installed Drawings
checkpoint-status | 4908900a-6bdc-4c70-bf43-f69314918ba9 |  | checkpoint | Obtain Copy Of Switchboard Schedule And Schematic Drawings
checkpoint-status | 7b767f2d-4769-4828-aae1-e7e28e4ea8a2 |  | checkpoint | Mark Up Any Additions Or Deletions Found Whilst Commissioning
checkpoint-status | 3e8a7645-c5c1-4839-b6fb-242535542c7a |  | checkpoint | Complete Visual Checks
checkpoint-status | ed218816-873a-4d03-89a2-07334ba05b06 |  | checkpoint | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below
checkpoint-status | fa7ef7a8-7db3-4c8e-859b-98d59f9c83f0 |  | checkpoint | Complete Mandatory Tests Using Metrel Tester, Save And Log Results On Tester
checkpoint-status | 5112d84a-85ea-4213-8d20-eb848090c1ca |  | checkpoint | Any Failed Results To Be Rectified Saved And Logged On Tester
checkpoint-status | faefa2c0-22ea-46bc-9cca-233a2152b3ae |  | checkpoint | Ensure Correct Operation Of All Control/Equipment Installed In Switchboard
checkpoint-status | 73684c12-86df-4f60-b267-18da58737eee |  | checkpoint | Ensure Vast Witness Test Has Been Completed
checkpoint-status | aa871bf8-3c91-4efd-8bf3-0a2b5600da18 |  | checkpoint | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated
checkpoint-status | 53d07b18-5dc8-4829-97b8-334a58fb6dc0 |  | checkpoint | Ensure No Access To Live Parts
checkpoint-status | 5649ec35-37fd-4e6b-a1c4-55b362b66a32 |  | checkpoint | Complete Switchboard Schedules On Vast Template, Install And Fix To Allocated Position In Switchboard
checkpoint-status | c998d0b7-a497-415c-bb7e-9899dabe9bc7 |  | checkpoint | Download Test Results From Metrel Tester And Save To Project Folder
checkpoint-status | efc154cd-ea5f-4050-8b2a-681da8bcdff4 |  | checkpoint | Complete Certificate Of Electrical Safety And Save To Project Folder
checklist-flat | 0f62d89e-57a0-4260-831a-65fe04aeeb47 |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | dbd424ea-077b-42bf-aef9-39d8ea598213
checkpoint-status | decd8a96-685e-4f28-8e50-47e2bd93d09d |  | checkpoint | Details
text | acd446e9-425e-519b-992d-37c653e93b3a |  | textbox | Location
text | 584c8b07-1952-52fb-96b1-d33f22ebebe2 |  | textbox | Supervisor
text | f2df7993-08bd-55a7-b963-f6a24029d7ac |  | textbox | Date
text | 86bf3f4c-4b87-5460-95df-79f833b3d475 |  | textbox | Time
text | aada1ba2-e42e-522a-ae83-93188c9d606e |  | textbox | Persons present
label | 2edb7a82-9792-5c51-b090-590b130131a1 |  | note | Topics discussed
boolean | 8620ec71-f1d1-5bde-a218-01579e56052b |  | tickbox | - Injuries, near misses and incidents
boolean | dcd8d09c-2b0c-5491-af13-836000890d20 |  | tickbox | - Management of major hazards
boolean | eb62f661-8372-533c-a886-19ced59e43bd |  | tickbox | - Compliance with our Vast SWMS
boolean | 109aba20-cfdb-59df-8651-ead89987567b |  | tickbox | - Safety - E.g., Apply LOTO processes when applicable. When Megger testing ensure that no person is working at the other end of cable being tested.
boolean | f3c0de5c-d953-5538-b42c-851b5412762b |  | tickbox | - Housekeeping
text | a8f4766f-f8aa-5b17-80ae-f20aa19b7cdc |  | textbox | Comments from the floor
checklist-flat | 6c5897b6-c7ba-41e7-aadd-e1191dc3f79b |  | checklist | ITP No. 8 - STRUCTURED CABLING FIT OFF |  |  |  |  | Yes | ITP No. 8 - Structured Cabling Fit Off | f5c252a7-e4df-4e22-8845-8f823c8eb9cb
checkpoint-status | 65374739-97ca-430c-a6e2-0af60b5eed3e |  | checkpoint | Visual check ensuring cable to be fitted off in correct position.
checkpoint-status | 16fa7839-370f-4bac-bcb7-9fbf8549bcae |  | checkpoint | Selection of correct tool to be used for termination type.
checkpoint-status | eef2f771-c931-4c18-886b-d37ff6ef4ad4 |  | checkpoint | Ensure cables are stripped no more than the specified distance. check terminations at completion for colour code and sequence.
checkpoint-status | 9ba83dc7-8bf9-4066-88c8-ad61860619fd |  | checkpoint | Attach wrap around label to cable no more than 60mm from the jack. ensuring correct number sequence.
checkpoint-status | e930b2cd-6ca4-413b-bf19-c5a57771d3f6 |  | checkpoint | Dress cables to final location. ensure velcro straps for cat 6 cabling
checkpoint-status | eb987ea8-8afd-493f-bf70-36afa7102257 |  | checkpoint | Install jack into workstation or wall outlet.
checkpoint-status | 9b98d9f6-fb3a-40d8-a42b-d28785e920dc |  | checkpoint | Install patch panel into cabinet loom cables to the back of the patch panel. tie into position using velcro strip and/or cable ties supplied.
checkpoint-status | c09cfadb-c438-4ee9-85d7-7866bdbb6db9 |  | checkpoint | Patch outlets to hardware devices where applicable and check for correct operation.
checkpoint-status | a9fb2524-0946-49b8-9720-14626d9ef274 |  | checkpoint | Label outlet ensuring correct number sequence
checkpoint-status | 8f95e12a-18db-49bf-943e-2a681d78a91a |  | checkpoint | Complete certification as required
checklist-flat | 7d84d548-55e7-4805-aadc-1795d9e81533 |  | checklist | ITP No. # - Installation of Gatic Style Pit Lids |  |  |  |  | Yes | ITP No. # - Installation of Gatic Style Pit Lids | ffbdf20f-a684-4057-816b-ee2c2b76bb90
checkpoint-status | 15ce8478-4159-4693-a212-3d2058390e6f |  | checkpoint | Inspect all lids upon delivered for any damage and correct part
checkpoint-status | 44a30be0-c842-48b4-bc61-d117bf582718 |  | checkpoint | Set out and form border around pit to be concreted, using manufactures insallation requirements as a guide
checkpoint-status | b4d2b400-3f5e-455c-bffa-04864c8ce104 |  | checkpoint | Place gatic lid on top of pit, make lid level/match finished floor level
checkpoint-status | e078518a-d42b-4318-849c-34ac6770e458 |  | checkpoint | Block any and all necessary gaps/holes as required
checkpoint-status | 7f25528d-c6f1-48f9-b4f7-7e44c66a8ced |  | checkpoint | Pour concrete (or applicable material) around border and infill pit lid, finish appropriatly
checkpoint-status | 10f95da4-070e-4f85-a0f3-fc90a38d0d13 |  | checkpoint | Barricade finished works, erect signage as needed
checkpoint-status | 440d2ac4-4ca3-4baa-8176-41d76f29cefb |  | checkpoint | Clean up work area