## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 813d9cf3-1a2d-4c73-a028-0d2c72643554 |  | checklist | ITR 18. Installing Underground Services |  |  |  |  | Yes | ITR No.18 Dan Murphy's Light and Power fit off | 015ad7d0-e605-40ca-b921-3d660b3504d9
checkpoint-group | 2d48b7ff-de59-465f-9d16-4a41778771c7 |  | section | Bakelite and Power
checkpoint-status | 9f03106a-393e-4b04-a16a-d20713deb898 |  | checkpoint | Check drawings for quantity, brand type and colour
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | a70046b3-b34e-4d88-a9e5-1706b6d3a417 |  | checkpoint | Location/compliance wet areas, hazards etc. mounting heights,
checkpoint-status | eae85d77-41a7-4afc-ab50-86e5f29448de |  | checkpoint | fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. each circuit must be fitted off completely
checkpoint-status | 350bcd52-7f78-4d06-b536-ac33880af5b8 |  | checkpoint | Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use a shroud. each circuit must be fitted off completely
checkpoint-status | cd4a3df0-cddc-4389-b4ca-821b3680e0a0 |  | checkpoint | Fit off final appliances
checkpoint-status | 9853a159-0fd3-4504-81ff-8c44d9fd7d70 |  | checkpoint | Cover plates (if required)
checkpoint-status | 18f1c384-a716-445a-9604-bbd39c8fc6e4 |  | checkpoint | Install label (if a specified requirement)
checkpoint-group | 632890fa-7062-4a1c-9968-86f6a35f393f |  | section | Light Fittings
checkpoint-status | 9ed1a546-dfee-4e11-823f-bdef5dd0b845 |  | checkpoint | Delivery check for damage and correct quantities
checkpoint-status | 5cf808b7-6419-48a9-a1f0-138d5f978350 |  | checkpoint | Locations coordinate with other services
checkpoint-status | 5239070c-358e-47dc-86f5-55e0c968cccc |  | checkpoint | Marking out if required - refer to reflected ceiling plan for set out
checkpoint-status | 5ffbf7e1-5f92-49e7-941a-41f768f22c67 |  | checkpoint | Plug in or fit off light / plug base
checkpoint-status | cc3cf09d-a5cd-47a1-a89d-631bd93a62ed |  | checkpoint | Install light fitting
checkpoint-status | d8888f4b-ef2b-4b3c-b591-51781f680bed |  | checkpoint | Install lamps and diffuser
checkpoint-status | b09dbfd4-43d7-4e4b-98f4-9de1cc6ae068 |  | checkpoint | Clean fitting, lamp diffuser
checklist-sectioned | 216f7afb-82e4-457a-8795-8bc5185c8f39 |  | checklist | ITR No.09 Dan Murphy's In Slab Conduits |  |  |  |  | Yes | ITR No.09 Dan Murphy's In Slab Conduits | 021d383d-4613-4bad-9012-b4f2bb290963
checkpoint-group | 8741c542-9162-48f1-a1a4-8300420cb255 |  | section | Preparation
checkpoint-status | ea9e13db-58a3-4c90-a88e-64bf04c9d490 |  | checkpoint | Determine origin and destination
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | 4158935e-6f96-4f02-805b-d5f2ae0620f1 |  | checkpoint | Check clear of other services, penetrations etc
checkpoint-status | bd5f5ddd-948f-4273-a60f-6fc03a7322de |  | checkpoint | Check cable size to verify conduit size
checkpoint-status | 83df71fe-e746-4873-8977-4538e5a8f957 |  | checkpoint | Check if expansion joints are required
checkpoint-group | b1ce6b78-e68c-418f-b28f-3e04fc65a5cc |  | section | Installation
checkpoint-status | 60e7eb48-9507-45ea-8392-3fba46736b40 |  | checkpoint | Mark out positions of junction boxes and penetrations where necessary
checkpoint-status | fd9e37e5-a31f-415f-bc49-2c72a8646bda |  | checkpoint | Install bar chairs where necessary
checkpoint-status | 0e7ec852-4135-4b16-a188-38d4f7c55845 |  | checkpoint | Install junction boxes and conduits and glue
checkpoint-status | fb970534-8b00-416d-8dc9-c76e3b717e9e |  | checkpoint | Tie conduits securely at all joints and midpoints
checkpoint-status | c87ff2a2-8346-4b3d-b3a2-06d44a48d08f |  | checkpoint | Ensure all conduits are 50mm above deck
checkpoint-status | b9e64eb3-cc44-49f6-b997-259f32802ec1 |  | checkpoint | Mark up drawing of conduit runs (if required)
checkpoint-status | 2baed040-f2c0-4903-a82b-fcfb4f7adb27 |  | checkpoint | Observe conduits when concrete is being poured
checklist-sectioned | a3a0c7f6-43db-45c9-b2c3-d2f31bf75973 |  | checklist | ITR No.09 Woolworths In Slab Conduits |  |  |  |  | Yes | ITR No.09 Woolworths In Slab Conduits | 16aacc72-ae36-4846-b91a-e50c580b3d92
checkpoint-group | 0623a205-bba4-4c6d-b6b5-f707e7bd8086 |  | section | Preparation
checkpoint-status | abb7c196-1423-4180-88f5-c17924dcc086 |  | checkpoint | Determine origin and destination
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | caf4a293-6962-47fb-af17-3d97aad3480b |  | checkpoint | Check clear of other services, penetrations etc
checkpoint-status | 8c6595b8-adb5-4d89-95b9-9ba83217734d |  | checkpoint | Check cable size to verify conduit size
checkpoint-status | 2c484626-5057-4b64-a66e-0c351fd42fc3 |  | checkpoint | Check if expansion joints are required
checkpoint-group | 9793b014-6d2d-460e-b373-0bc0ff43e5eb |  | section | Installation
checkpoint-status | 79c130dd-f430-419e-882a-fda1da38b16d |  | checkpoint | Mark out positions of junction boxes and penetrations where necessary
checkpoint-status | f3cba0d1-0969-4349-9c2c-ccfae34b205a |  | checkpoint | Install bar chairs where necessary
checkpoint-status | 2c8eff0a-90f4-4d98-b944-501d19550646 |  | checkpoint | Install junction boxes and conduits and glue
checkpoint-status | 203c6695-40c3-4432-af4b-de95b5b48794 |  | checkpoint | Tie conduits securely at all joints and midpoints
checkpoint-status | a01f1209-4035-4e5c-b58d-d77a2132ec11 |  | checkpoint | Ensure all conduits are 50mm above deck
checkpoint-status | 096ecbf8-1379-48c2-a6e9-5b5c46bf452b |  | checkpoint | Mark up drawing of conduit runs (if required)
checkpoint-status | e2755688-a566-41ef-a378-12390c701e6c |  | checkpoint | Observe conduits when concrete is being poured
checklist-flat | fd97f411-345d-414b-8bcb-f731df305f31 |  | checklist | ITR No.16 Basement Switchboard Installation and Terminate Sub Mains |  |  |  |  | Yes | ITR No.16 Basement Switchboard Installation and Terminate Sub Mains | 174022f6-efab-49dd-9d36-fcbacc365af1
checkpoint-status | ee1b3b99-2dc3-4a8a-929d-bca648e18bd1 |  | checkpoint | Area clear, tidy and accessible
checkpoint-status | 3af48510-8285-4eef-96da-92405bbc9a6c |  | checkpoint | Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
checkpoint-no-status | 2cc33f0d-51bd-4fc8-bbce-54c27318b91a |  | checkpoint | Drawing Rev No.
text | 5117b332-4d50-5626-9e1c-3e4f60124977 |  | textbox | Drawing Rev No.
checkpoint-status | ea2c0d18-1eda-4286-b9c3-6593597c1637 |  | checkpoint | Locate & fix into position
checkpoint-status | 697df402-f957-4150-b24e-4807b6773c28 |  | checkpoint | Install sub mains cabling as appropriate eg. glands, tray, duct
checkpoint-status | f6f7d166-a008-47f5-a5a9-6a7e7f2be0ad |  | checkpoint | Install lugs and terminate
label | d58cd6c6-19b7-54d1-b5ea-505b15f77adf |  | note | Any cables not terminated prior to energisation must be removed from the cubicle at origin and have ends covered in heatshrink at destination cables must be covered in heat shrink and be contained in a junction box
checkpoint-status | 3f571c75-7312-4351-a65c-16351e7db9b8 |  | checkpoint | Clean & vacuum
checkpoint-status | 493513c8-8ef9-4b35-a643-e8395cb1c2f1 |  | checkpoint | Organise inspection by inspector, lodge prescribed / non prescribed (as applicable) certificate of electrical safety (if required).
checkpoint-status | 626be9fc-eb7e-4ac8-a1c1-76fbd4d400fb |  | checkpoint | Clearly identify services
label | 5ade8e5e-ddde-51e2-84af-ec5bc7cd33ae |  | note | When ready to energise proceed in accordance with energisation procedure energize & record results on itp 116
checkpoint-status | 3a94e078-e165-425c-ab3e-65015d87589e |  | checkpoint | Check the switchboard as installed matches the shop drawing.
label | b9154b1a-3c24-56d7-a0d2-9e6cbdc85465 |  | note | If necessary modify shop drawing to match installed & return to office
checkpoint-status | 2c0ac714-c44c-44a9-9e55-642afa48cf15 |  | checkpoint | Clean switchboard cupboard
checkpoint-status | 7f735357-53c9-4258-8aa0-fd286130dc41 |  | checkpoint | Install sub circuit cabling in accordance with db schedule and terminate
label | de18f665-cf7e-569e-9aca-28f17a5d9776 |  | note | If the circuit not complete at the other end, it must not be terminated but placed in a junction box at field end and in connectors at distribution board end
checkpoint-status | 38855661-9dc3-4908-a398-dc7747a107f6 |  | checkpoint | Clean & vacuum
label | c57febdd-7be8-5b1b-a4b8-601c5956e1d9 |  | note | Record relevant information and any changes on db schedule and return to administrator/office for commissioning team
checklist-flat | 40c43e9e-9ccc-4744-8419-ddce9efdde52 |  | checklist | ITR No.7 Hallway - Fit Off Electrical (High Level & Walls) |  |  |  |  | Yes | ITR No.7 Hallway - Fit Off Electrical (High Level & Walls) | 18945191-85a1-4e33-a3d6-8c6fb36ab497
checkpoint-status | d8a06b29-baf8-4d58-9adc-c6fc694111e2 |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | 95b059d4-e9bd-42ed-80c4-2f466b8951d9 |  | checkpoint | Fit off all Lights
checkpoint-status | cf7cc6c8-996a-49fe-954b-0cc852ad86b6 |  | checkpoint | Fit off all Sensors and SET TIME TO MINIMUM
checkpoint-status | 0d203d3a-91ee-4cd0-a0c8-f3175450c22b |  | checkpoint | Fit off all EX/EMG’s
checkpoint-status | c0665856-8380-47bd-9b76-06cd37c95005 |  | checkpoint | Label all EX/EMG’s as per plan number
checkpoint-status | c3048d4c-529a-4fb5-a645-c48dfa5240df |  | checkpoint | Fit off all Cleaners GPOs
checkpoint-status | 380ed77b-107e-4168-bb43-84663ae08189 |  | checkpoint | Fit off all Comms Riser GPOs
checkpoint-status | 2a97cb64-19f2-4cd8-bfe1-58c60a83ab3a |  | checkpoint | Ensure area is left clean
checklist-sectioned | 110c709c-cb4a-4686-86d9-52558bac32c1 |  | checklist | ITR No.23 Retail Light and Power fit off |  |  |  |  | Yes | ITR No.23 Retail Light and Power fit off | 1b0f9f45-2442-4379-97b5-0ba41ca1c9c9
checkpoint-group | ee56e78c-1d43-4d06-8ac2-d25f2f26f24e |  | section | Bakelite and Power
checkpoint-status | 74a46941-fe4e-429d-ab4b-a02532008aff |  | checkpoint | Check drawings for quantity, brand type and colour
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | d2cb3213-e71d-4895-b610-f4f4bdd8ba19 |  | checkpoint | Location/compliance wet areas, hazards etc. mounting heights,
checkpoint-status | 1cd05fdd-fe89-4599-94c9-1f87f9ac8751 |  | checkpoint | fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. each circuit must be fitted off completely
checkpoint-status | c7d547b1-4c9a-41fe-931b-25a88a67a1c2 |  | checkpoint | Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use a shroud. each circuit must be fitted off completely
checkpoint-status | 4f08fe0e-c6a3-42aa-aa5c-f6ee3eed8f4d |  | checkpoint | Fit off final appliances
checkpoint-status | b3e98276-0e47-4c46-9e26-c1b1e8cb1a46 |  | checkpoint | Cover plates (if required)
checkpoint-status | b225d2f5-5bc3-4ee5-84ac-bab2e5661dac |  | checkpoint | Install label (if a specified requirement)
checkpoint-group | bf88a8c4-2a69-46b1-8a18-731709f5960c |  | section | Light Fittings
checkpoint-status | 5cc6fe7a-d5e9-44c9-8142-d4afb8ae5117 |  | checkpoint | Delivery check for damage and correct quantities
checkpoint-status | 55707981-08c2-49b6-98f5-a4c7a155acfc |  | checkpoint | Locations coordinate with other services
checkpoint-status | f9093a12-c686-40dc-9872-e9c788933680 |  | checkpoint | Marking out if required - refer to reflected ceiling plan for set out
checkpoint-status | fee70879-14c9-4d43-b682-910498c2237d |  | checkpoint | Plug in or fit off light / plug base
checkpoint-status | cb13e45f-d35f-474d-ac8a-c270e9d8b247 |  | checkpoint | Install light fitting
checkpoint-status | dda9bcf6-4a3c-4e4f-b007-11c4a2a31544 |  | checkpoint | Install lamps and diffuser
checkpoint-status | 2c4190b1-f364-4aff-ae3e-c998caa32804 |  | checkpoint | Clean fitting, lamp diffuser
checklist-sectioned | 469b9795-6022-4929-a521-af2d039f2f44 |  | checklist | ITR No.28 Woolworths Commissioning Distribution Boards and Light and Power |  |  |  |  | Yes | ITR No.28 Woolworths Commissioning Distribution Boards and Light and Power | 1fa8fd8e-919a-4ce9-822c-21957dfd5811
checkpoint-group | 329a06ec-0e5f-40c0-bf99-cd7d11d5ffc3 |  | section | Distribution Board
checkpoint-status | 091d9acf-f4b2-4113-a7c2-562281d4184b |  | checkpoint | Area clear, tidy and accessible
label | 7831382e-4534-5b8e-b57b-3a9c4f950cb8 |  | note | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
label | da9a062a-6078-5881-93b8-48d316ec45e8 |  | note | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
label | d2bc3b33-e8e4-5c3c-95b6-45a8a83d08ca |  | note | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
label | 8d5b0583-abec-5ab2-9e60-4ac299ae43b1 |  | note | Collect material from the office and have the correct db structure downloaded.
checkpoint-status | 66ca5b86-0a9e-4bad-8704-5b6a18e00736 |  | checkpoint | Commence commissioning
label | a3aac8d2-bdd7-5d9d-bb8f-4fb6d56b8405 |  | note | Update copies of distribution board schedule with any additions/deletions return db schedule to office for typing of switchboard schedule, leave copy in switchboard
label | c146d299-b642-5b20-a48a-da1919a4dd10 |  | note | Check typed schedule for accuracy and install in schedule holder
checkpoint-status | 17a9771a-5340-4868-a644-e88add8fa9ab |  | checkpoint | Clean switchboard cupboard
checkpoint-group | 979cfc7a-06f6-4081-ab2d-3d8701367331 |  | section | Light and Power
checkpoint-status | 82a03724-6cee-4eda-9904-099cb7c433b6 |  | checkpoint | Energisation permit completed prior to energisation
checkpoint-status | be208e22-00b1-4235-b878-7fb407941e99 |  | checkpoint | Visual Check all items
text | 683b5a90-a42b-57d4-bfcf-143a2044da11 |  | textbox | 1
text | 4ad739b0-4be6-57c3-a1af-39c2e384c27e |  | textbox | Live Test
text | 4356afa7-8274-5e06-99b8-173957e5857c |  | textbox | Record Metrel Results and log
checkpoint-status | 91e38b77-1ae1-4785-84f1-097c17a509fc |  | checkpoint | Test plug bases for switching
checkpoint-status | d375b615-98e7-488e-ba0b-a9e651aa767d |  | checkpoint | Check light switches/Sensors for correct switching functions
checkpoint-status | d13cc046-df04-4a94-8cf2-5ab484b8a5ce |  | checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
checkpoint-status | b41bcc36-d5d5-4fd0-9d07-b709e89da996 |  | checkpoint | Install switchboard cover / label (take photos)
checklist-sectioned | b39c9fc2-afce-4b23-85b3-2ce5c25a57cb |  | checklist | ITR No.09 Ground In Slab Conduits |  |  |  |  | Yes | ITR No.09 Ground In Slab Conduits | 264ce01f-cc48-42d9-9221-69f72922c8eb
checkpoint-group | 44d639c9-7efd-4fe5-97a9-f4b5bb484fb1 |  | section | Preparation
checkpoint-status | fb0a85b3-22b9-4570-ae3c-ef9a6665d4a9 |  | checkpoint | Determine origin and destination
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | dbe5671a-7c83-481d-a489-12317d5bb331 |  | checkpoint | Check clear of other services, penetrations etc
checkpoint-status | d62152bd-b0ef-4388-947e-71033a627830 |  | checkpoint | Check cable size to verify conduit size
checkpoint-status | d2f07376-8a34-44fe-8925-9e8b300d5258 |  | checkpoint | Check if expansion joints are required
checkpoint-group | 9ddea926-1c89-45c3-985f-49fc520a2373 |  | section | Installation
checkpoint-status | 5429edb9-a469-49e4-ba13-aeae0021a86c |  | checkpoint | Mark out positions of junction boxes and penetrations where necessary
checkpoint-status | 80148aea-365c-4b4b-ab47-252db8f6e6f5 |  | checkpoint | Install bar chairs where necessary
checkpoint-status | b7f10bf7-5db4-4b76-8f8b-f02926645bc1 |  | checkpoint | Install junction boxes and conduits and glue
checkpoint-status | c899d4dd-60b4-47ad-ac3f-5e3ed4330129 |  | checkpoint | Tie conduits securely at all joints and midpoints
checkpoint-status | b10c43c5-fa05-49bc-9d43-e50a4cfe7eb5 |  | checkpoint | Ensure all conduits are 50mm above deck
checkpoint-status | 15ed4058-c343-4fe1-84ee-c67ebb1c3d81 |  | checkpoint | Mark up drawing of conduit runs (if required)
checkpoint-status | ff3648f5-32bb-4f84-b05f-997edb61eb8b |  | checkpoint | Observe conduits when concrete is being poured
checklist-flat | 71137954-b6e2-47a4-9ff5-b9033144abdb |  | checklist | ITR No.21 Dan Murphy's Switchboard Installation and Terminate Sub Mains |  |  |  |  | Yes | ITR No.21 Dan Murphy's Switchboard Installation and Terminate Sub Mains | 276b4263-de4a-49f1-9cb6-7151d0f34a25
checkpoint-status | 4b799e8e-081f-4082-9c39-a976f86c5315 |  | checkpoint | Area clear, tidy and accessible
checkpoint-status | defd3150-1ee3-4afd-8f80-7eab3808cce9 |  | checkpoint | Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
checkpoint-no-status | ee96a320-63f5-4e5d-a00a-fcd97d92b960 |  | checkpoint | Drawing Rev No.
text | 6bbacf9e-e77e-5f3f-9156-80370782e8e7 |  | textbox | Drawing Rev No.
checkpoint-status | 967b968d-41e6-4953-b3bc-9ff4ce1d67cf |  | checkpoint | Locate & fix into position
checkpoint-status | 58a09ec2-2a78-438f-b791-be17a329b513 |  | checkpoint | Install sub mains cabling as appropriate eg. glands, tray, duct
checkpoint-status | 6ccf7757-97ee-4803-88b4-1640bb176fb0 |  | checkpoint | Install lugs and terminate
label | a4ce6dc1-15de-577a-ab57-7d7741385cb4 |  | note | Any cables not terminated prior to energisation must be removed from the cubicle at origin and have ends covered in heatshrink at destination cables must be covered in heat shrink and be contained in a junction box
checkpoint-status | 23a8a3b7-e6d3-4698-97e6-54f29978010f |  | checkpoint | Clean & vacuum
checkpoint-status | 36dbb187-a0a7-486e-845a-5144dd651590 |  | checkpoint | Organise inspection by inspector, lodge prescribed / non prescribed (as applicable) certificate of electrical safety (if required).
checkpoint-status | 1590c03d-ca66-4681-b496-3e85d209f552 |  | checkpoint | Clearly identify services
label | 4b9114e7-ff2e-58c6-b7a0-62582e79a4d8 |  | note | When ready to energise proceed in accordance with energisation procedure energize & record results on itp 116
checkpoint-status | 07bf572d-5706-443e-8b2a-77f4cd24d45a |  | checkpoint | Check the switchboard as installed matches the shop drawing.
label | 2cc5dddf-1c7d-5f6a-b385-ef2aef32cf2c |  | note | If necessary modify shop drawing to match installed & return to office
checkpoint-status | debbd18b-a356-476f-885c-3d16bd270cc4 |  | checkpoint | Clean switchboard cupboard
checkpoint-status | e7619d0e-308b-4e00-94fa-9ae93c0cb08b |  | checkpoint | Install sub circuit cabling in accordance with db schedule and terminate
label | b30167e5-fec4-5371-845c-d4c460717b9c |  | note | If the circuit not complete at the other end, it must not be terminated but placed in a junction box at field end and in connectors at distribution board end
checkpoint-status | 8e463f4f-d3e9-4b90-837b-e9535c0c3e50 |  | checkpoint | Clean & vacuum
label | 086e2736-9977-53f9-87b8-20b02a8e5e4a |  | note | Record relevant information and any changes on db schedule and return to administrator/office for commissioning team
checklist-flat | be3c8a78-78ff-494f-a85c-fa592621a42c |  | checklist | Toolbox Meeting |  |  |  |  | Yes | zSYS - Toolbox Meeting | 2c6f15b5-b453-4f23-b4c3-f8d3fc94b548
checkpoint-status | 2423995f-a882-45cd-a675-8048cce9d7c4 |  | checkpoint | VAST toolbox meeting completed
text | c20c023d-2f6c-57a4-bf1b-88aa31f5848f |  | textbox | Supervisor
text | 58cc085c-4400-5969-90e4-2ed2c4f2fa16 |  | textbox | Persons present
boolean | ad2e4221-07b8-5b7d-bb39-e9fcdcf77d89 |  | tickbox | Injuries, near misses and incidents
boolean | 6ed9158a-8705-51ff-8ff6-0494162a2e79 |  | tickbox | Management of major hazards
boolean | 61ddcbc3-47a6-54b7-8c00-1472c82b0e19 |  | tickbox | Compliance with our Vast SWMS
boolean | 464f9fe8-0eaf-527b-a878-83ebf037ef24 |  | tickbox | Safety
boolean | 81413a7c-7e06-5211-9586-a3d0ff22f44e |  | tickbox | House Keeping
boolean | 3baf4beb-a70b-526e-a205-d9bc9a8eaeca |  | tickbox | PPE (HARD HATS & GLASSES ON AT ALL TIMES)
text | 94bed5e5-25bc-5f7b-9c26-4af7391f6d1c |  | textbox | Comments
checklist-sectioned | 6ff4e0f5-e029-43fc-89fa-7369f126a17e |  | checklist | ITR No.09 Stairwell In Slab Conduits |  |  |  |  | Yes | ITR No.09 Stairwell In Slab Conduits | 3157d6f2-f8af-46b9-a813-baecf6f3741f
checkpoint-group | 0c2aabae-6c94-40fd-8847-36d1a1d356ab |  | section | Preparation
checkpoint-status | 2d19b580-1982-400b-9dbc-be99018872a3 |  | checkpoint | Determine origin and destination
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | fd5cd9c6-4bd6-4fa2-8f2b-9f300cba98c7 |  | checkpoint | Check clear of other services, penetrations etc
checkpoint-status | e939b6b9-ebfb-4076-a9d0-be53556e26ca |  | checkpoint | Check cable size to verify conduit size
checkpoint-status | 17e9478e-3452-45be-899c-ba8ca2696593 |  | checkpoint | Check if expansion joints are required
checkpoint-group | 829ac749-a923-4f93-ae8c-6485f30641e2 |  | section | Installation
checkpoint-status | b4b3ce3b-faa4-4cf0-9c7a-bae70f05f1c5 |  | checkpoint | Mark out positions of junction boxes and penetrations where necessary
checkpoint-status | 9de640c6-cdfb-46b8-aa33-137233c3c1cc |  | checkpoint | Install bar chairs where necessary
checkpoint-status | 601a8086-6a9f-4058-a90b-fb09b60c4327 |  | checkpoint | Install junction boxes and conduits and glue
checkpoint-status | 282a9fe8-9e36-469c-8416-8ec7f64599e9 |  | checkpoint | Tie conduits securely at all joints and midpoints
checkpoint-status | 89d203f4-44ec-4055-884e-48829445a573 |  | checkpoint | Ensure all conduits are 50mm above deck
checkpoint-status | c3eb450a-8bd7-48a2-a05f-0a9634975d48 |  | checkpoint | Mark up drawing of conduit runs (if required)
checkpoint-status | eba2b7f2-c13f-4b85-bcd8-aecef90636ad |  | checkpoint | Observe conduits when concrete is being poured
checklist-flat | 8cb28587-b559-43dd-ba0c-295817a77ec0 |  | checklist | ITR. No 02 Apartment Cut Out |  |  |  |  | Yes | ITR. No 02 Apartment Cut Out | 3571e189-d34d-4b30-b06a-d1e9dc78833e
checkpoint-status | 2d6ec76e-efdb-4b11-9c30-46f1e6e06733 |  | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | ff250abc-4e06-4610-b59c-1dd8663bce93 |  | checkpoint | Cut out for light fittings
checkpoint-status | 000e8860-4689-492b-9bf6-65f5a5123392 |  | checkpoint | Cut out smoke detectors
checkpoint-status | 71f11c43-24c1-47b3-82e8-8d3b05c6b962 |  | checkpoint | Cut out kitchen to kitchen plan
checkpoint-status | 0f70a366-59c3-4d8e-b367-e5a86dd496ed |  | checkpoint | Cut out switches & GPO’s
checkpoint-status | b8413c11-2c40-4d9c-82e7-b18f399e5afc |  | checkpoint | Cut out Bathroom and Study Led Strips Fig 8
checkpoint-status | 84a9602e-b678-4ba4-92fb-c89b00d4f134 |  | checkpoint | Ensure AC isolator is in correct position
checkpoint-status | 51305615-7281-43b8-b1e2-3dc5d801eb74 |  | checkpoint | Ensure Wall light is in correct position
checkpoint-status | 558597b2-f49f-4d9a-96ee-abc1770d3ff8 |  | checkpoint | Ensure kitchen outlets are in correct position
checkpoint-status | 022ad6dd-8816-43a1-93b2-3770866d346c |  | checkpoint | Locate all cables ( including Smoke Detectors & Pendants )
checkpoint-status | c0514aef-b19c-45d1-9955-7c236d34f0c7 |  | checkpoint | Install Fire Boxes and hit all 4 tabs in
checkpoint-status | 9eb547f2-25e7-404f-981d-4932e33f5280 |  | checkpoint | Fire caulk kitchen cables ( if applicable )
checkpoint-status | c2f0f86f-14bb-4dbd-8f2a-2ffade712434 |  | checkpoint | Ensure area is left clean
checklist-flat | e9af6f1d-1769-492e-8461-70c7ff5b2b82 |  | checklist | ITR No.10 Basement Cable Support |  |  |  |  | Yes | ITR No.10 Basement Cable Support | 386e01b1-f00b-46ca-bd13-31127ab73660
checkpoint-status | 482dc08a-c0e7-4ab2-b457-6529e3607eb2 |  | checkpoint | Area clear, tidy and accessible
checkpoint-status | 3db0dad5-d668-4b08-aae6-97cac7377f2e |  | checkpoint | Coordinate with other services
text | 9d6ddb17-d9b3-5e48-8c67-7c3ee6226df5 |  | textbox | Size of cable tray
checkpoint-status | 2eda2bee-078c-4e06-a2c8-de213ae981f1 |  | checkpoint | Install fixings
checkpoint-status | ce2b31a9-49dc-4fe8-abe1-c5c3b15a94e6 |  | checkpoint | Do sketch or mark up drawing for future as builts
checklist-flat | 5640db16-e10e-44ac-87be-ed87bac85b30 |  | checklist | ITR No.26 Retail Switchboard Installation and Terminate Sub Mains |  |  |  |  | Yes | ITR No.26 Retail Switchboard Installation and Terminate Sub Mains | 397ab74d-a049-4fd9-80d4-d2d1bbc07e0a
checkpoint-status | d47cdaaf-d762-407d-89c8-baaa32e5a5f5 |  | checkpoint | Area clear, tidy and accessible
checkpoint-status | a600336c-bfdc-4bbb-b6c3-3a46d8eb1e22 |  | checkpoint | Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
checkpoint-no-status | 569343e2-5f2d-4fd4-b542-45afb7ae610e |  | checkpoint | Drawing Rev No.
text | b78e7534-b20d-5c70-bada-617ec34caa2f |  | textbox | Drawing Rev No.
checkpoint-status | 78cef78c-2936-4787-9b2a-9e8da94fbca2 |  | checkpoint | Locate & fix into position
checkpoint-status | 54888faa-7c99-440a-91ec-10ff5a6d252c |  | checkpoint | Install sub mains cabling as appropriate eg. glands, tray, duct
checkpoint-status | d7c573d8-bf13-4531-9427-c78c1849e5d7 |  | checkpoint | Install lugs and terminate
label | 7ea98fe9-f5f6-512a-a134-5671822872a7 |  | note | Any cables not terminated prior to energisation must be removed from the cubicle at origin and have ends covered in heatshrink at destination cables must be covered in heat shrink and be contained in a junction box
checkpoint-status | 105ab5fb-acba-46bf-b71c-a6ec0be6be25 |  | checkpoint | Clean & vacuum
checkpoint-status | f54758ce-5172-433b-8af9-9d269af89f38 |  | checkpoint | Organise inspection by inspector, lodge prescribed / non prescribed (as applicable) certificate of electrical safety (if required).
checkpoint-status | 0e08ede5-0c3d-4e3d-a69d-106e6626b2df |  | checkpoint | Clearly identify services
label | faaa36aa-5047-5917-a664-8241874d0513 |  | note | When ready to energise proceed in accordance with energisation procedure energize & record results on itp 116
checkpoint-status | 1e901e82-ecda-4ce7-9ce4-cbba7eb968a9 |  | checkpoint | Check the switchboard as installed matches the shop drawing.
label | 80b0afed-d1e5-54d2-9bfa-7a7abd063922 |  | note | If necessary modify shop drawing to match installed & return to office
checkpoint-status | 2323b231-5efe-48ef-87d7-1c30741e41bc |  | checkpoint | Clean switchboard cupboard
checkpoint-status | f09eda54-1ce1-4cb1-a950-42addb14d1b0 |  | checkpoint | Install sub circuit cabling in accordance with db schedule and terminate
label | 8943d744-9807-59aa-8cdc-65789e8cbd6f |  | note | If the circuit not complete at the other end, it must not be terminated but placed in a junction box at field end and in connectors at distribution board end
checkpoint-status | 8737ae3b-75cd-47a9-b59c-dd5e326c15b3 |  | checkpoint | Clean & vacuum
label | da494b80-17ed-53fe-960d-7af5951479d0 |  | note | Record relevant information and any changes on db schedule and return to administrator/office for commissioning team
checklist-sectioned | e9cb9d8d-0345-45c7-9a85-d629330f0550 |  | checklist | ITR No.22 Retail Commissioning Distribution Boards and Light and Power |  |  |  |  | Yes | ITR No.22 Retail Commissioning Distribution Boards and Light and Power | 3ac23421-e754-4d4f-b753-3301eaf01654
checkpoint-group | 3312d565-5d4d-4b82-b529-11bc0fbed980 |  | section | Distribution Board
checkpoint-status | 892d9c59-53a4-4abf-8dae-bd2d0eb29c1e |  | checkpoint | Area clear, tidy and accessible
label | 16c24d4c-9adb-5411-b43d-24da55c3c478 |  | note | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
label | 4c85fbeb-c9bd-559f-beba-13a44218c852 |  | note | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
label | d12909e2-2735-513c-b392-84b0ce1c5f90 |  | note | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
label | 22a1bef1-fd8b-55bc-af28-a1819b6ec54d |  | note | Collect material from the office and have the correct db structure downloaded.
checkpoint-status | 6fe7b460-5390-4d41-ab04-2394a51ac614 |  | checkpoint | Commence commissioning
label | de672820-424e-53e4-9c0e-572430dfbc23 |  | note | Update copies of distribution board schedule with any additions/deletions return db schedule to office for typing of switchboard schedule, leave copy in switchboard
label | c9779a80-9905-543d-8931-93651f57a426 |  | note | Check typed schedule for accuracy and install in schedule holder
checkpoint-status | 8df7934e-d243-47e2-9474-a2eeb4637ead |  | checkpoint | Clean switchboard cupboard
checkpoint-group | eee9b418-3379-470d-9f2a-593922a1d74f |  | section | Light and Power
checkpoint-status | f01f0571-8148-4010-b072-782dd6a3d36a |  | checkpoint | Energisation permit completed prior to energisation
checkpoint-status | ac409b3d-4b71-4bc3-a6b2-23a6f9daeb78 |  | checkpoint | Visual Check all items
text | 2aa84424-e126-5b87-8849-ca8be445653a |  | textbox | Dead Testing
text | 68a63bca-396f-58ac-a8b8-f2d02e53dfa9 |  | textbox | Live Test
text | 556904d4-82e9-50e0-b7a2-0486c571727b |  | textbox | Record Metrel Results and log
checkpoint-status | e47152e8-ec46-47aa-9b70-a593e44b492d |  | checkpoint | Test plug bases for switching
checkpoint-status | 71477b3f-c25b-4453-a44f-fd8e5d30b7a9 |  | checkpoint | Check light switches/Sensors for correct switching functions
checkpoint-status | 4a2f8472-a5b7-49d6-8671-99e908bc13d5 |  | checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
checkpoint-status | c8980d1a-6dbe-42fe-b95f-42afd0d0e34a |  | checkpoint | Install switchboard cover / label (take photos)
checklist-flat | a135b8f4-6897-4315-bae7-5bb482edc0f2 |  | checklist | VAST Site Induction |  |  |  |  | Yes | zSYS - VAST Site Induction | 3b080158-9a42-4e02-845a-54b365d9b99b
checkpoint-status | d3f90889-7768-409a-b99b-838a10328283 |  | checkpoint | VAST Employee
text | 40b4d4c4-1a33-586b-a691-07942b1330ef |  | textbox | Name
text | e305e11b-e33c-54e5-9771-bd666a08f2aa |  | textbox | Contact Number
text | 130d0ac1-2b87-5854-ab5e-1ddf56f99214 |  | textbox | Date of Induction
label | 629c1003-0c80-5051-90c0-8c59a28a112f |  | note | Tick if the following are understood:
boolean | e7fcbae6-d76f-5e56-93dc-0be57f852358 |  | tickbox | How to report to the site and who you report to
boolean | 2ad4c545-c276-58ab-91c8-57d7c2352a95 |  | tickbox | The working hours on site
boolean | a0d8d1fc-80e7-5da7-8059-8643d6f44913 |  | tickbox | Who the managers and supervisors are on site
boolean | 80e0d7f0-b8d2-589f-8453-8ab824ad0264 |  | tickbox | The correct minimum PPE for site
boolean | f68bb1a8-1879-5803-8ecf-62c1ee504350 |  | tickbox | How safety is communicated on site
boolean | 24bb2a35-a86b-5593-8a15-6a05ed1ae9ac |  | tickbox | Where to have lunch and where the toilets are
boolean | f8577a5c-9b26-5a94-938f-3f13f14a1a88 |  | tickbox | Where the First Aid Kit is kept and who is the First Aider
boolean | ea283bf0-551e-590a-b93c-e027ac84cdf6 |  | tickbox | The Emergency Plan and the Assembly Area for Emergency Evacuation
boolean | 388c4f16-c736-5c2a-8a2d-917cceca2088 |  | tickbox | What the high risk activities and hazards are on site
boolean | 5f14bc07-d3ba-5848-9252-c9015f468259 |  | tickbox | How to report WHS & Environmental hazards & issues
boolean | 0ea924c7-096d-5a80-a5db-bd2b5d7b0ef6 |  | tickbox | How to report a safety or environmental accident or incident
boolean | e6e058d1-934d-5844-a275-969be4301a37 |  | tickbox | Housekeeping responsibilities
checkpoint-status | 02dd4229-7ffa-46de-8ca1-6441a868057e |  | checkpoint | EWP Licence - Please take a photo
checkpoint-status | 207168a2-7b23-4dd2-bb9b-6c8a25f3c6be |  | checkpoint | Current Certificates Sighted - Please take a photo & comment on each attached certificate
checkpoint-status | 076205b4-6b8a-40f7-8ca2-07775e202f3a |  | checkpoint | VAST Employee Signature
checkpoint-status | 143751f5-ccaf-4f0f-8119-62b75485a7b4 |  | checkpoint | VAST Supervisor Signature
checklist-sectioned | a104bea1-40c0-4da3-bf45-0ecccfd4852b |  | checklist | ITR No.17 Dan Murphy's Commissioning Distribution Boards and Light and Power |  |  |  |  | Yes | ITR No.17 Dan Murphy's Commissioning Distribution Boards and Light and Power | 3dc11064-f336-45c8-8cb7-b048ed496b31
checkpoint-group | 13610bce-53bd-4099-99a3-ec3b4d8cabb5 |  | section | Distribution Board
checkpoint-status | a15a31ec-f02a-4094-826d-09c59d197791 |  | checkpoint | Area clear, tidy and accessible
label | 9988ac44-1a41-5a22-aa10-accbb690722c |  | note | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
label | dcea9a80-9536-5988-898a-2d87a2b4bb0f |  | note | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
label | d0210a9b-4540-5b08-8312-81e2f30852f7 |  | note | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
label | b56ba4d7-10a2-5758-8f14-0ceabfa03b3c |  | note | Collect material from the office and have the correct db structure downloaded.
checkpoint-status | e3aa667c-9f41-44c6-9b39-baa978df2767 |  | checkpoint | Commence commissioning
label | 0c73fd13-c52b-5471-80d1-9160cd075c0a |  | note | Update copies of distribution board schedule with any additions/deletions return db schedule to office for typing of switchboard schedule, leave copy in switchboard
label | 68bc1a92-4f7d-5241-9378-8c334fefa876 |  | note | Check typed schedule for accuracy and install in schedule holder
checkpoint-status | 341a4cb2-fd9e-4431-976d-de56dea2ff13 |  | checkpoint | Clean switchboard cupboard
checkpoint-group | c14a899a-1641-460f-a1b4-c59559912b9b |  | section | Light and Power
checkpoint-status | 72f3eae0-e538-471f-81c1-849d4b4333e4 |  | checkpoint | Energisation permit completed prior to energisation
checkpoint-status | 255aead8-4260-44a7-9d7a-fd7af3f418cc |  | checkpoint | Visual Check all items
text | 1db29d60-1116-51e0-ab14-c18ed856fc24 |  | textbox | Dead Testing
text | 40d2a3a0-0726-5759-bebc-c5fe8349d176 |  | textbox | Live Test
text | 9d826a3f-f077-5576-a8d4-30fd994293f0 |  | textbox | Record Metrel Results and log
checkpoint-status | 1433811e-7491-4d0d-bdc3-8f3fa920025c |  | checkpoint | Test plug bases for switching
checkpoint-status | cd60a12b-f065-4608-af73-f0a4b2152993 |  | checkpoint | Check light switches/Sensors for correct switching functions
checkpoint-status | f28f46e3-fe33-40d9-9054-fe473e611bf6 |  | checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
checkpoint-status | 5fad5609-5e2e-4872-b56e-1fd36a0503b9 |  | checkpoint | Install switchboard cover / label (take photos)
checklist-sectioned | e323d446-1cda-43c4-9a85-ac0ca45b962c |  | checklist | ITR No.11 Basement Light and Power fit off |  |  |  |  | Yes | ITR No.11 Basement Light and Power fit off | 3deaa8a6-e98a-4de9-b517-21c1cc865d66
checkpoint-group | a98f5e0d-b510-4aef-bc63-8fbc31f86473 |  | section | Bakelite and Power
checkpoint-status | 2c32284c-144e-44f1-b1a4-ee9da0bae31c |  | checkpoint | Check drawings for quantity, brand type and colour
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | 43675f29-40e2-4442-995f-005c48343012 |  | checkpoint | Location/compliance wet areas, hazards etc. mounting heights,
checkpoint-status | d3ceb60e-9154-48df-a86e-bc81de596f21 |  | checkpoint | fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. each circuit must be fitted off completely
checkpoint-status | 53cb0719-429a-4b7a-a30f-d816de37edbd |  | checkpoint | Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use a shroud. each circuit must be fitted off completely
checkpoint-status | 30962f13-59eb-428a-8b41-bed4a600aa9b |  | checkpoint | Fit off final appliances
checkpoint-status | 78e97a27-9f6d-463b-929a-ab1ce7191cec |  | checkpoint | Cover plates (if required)
checkpoint-status | d41c0007-c95d-4b12-a54b-22d7660589ec |  | checkpoint | Install label (if a specified requirement)
checkpoint-group | 04723ad5-d117-4829-a684-8fb8f701f3ab |  | section | Light Fittings
checkpoint-status | d165f8a0-5e4b-421a-a60f-ef5eda33c330 |  | checkpoint | Delivery check for damage and correct quantities
checkpoint-status | be5c2a93-c538-40bb-b123-7913c10a7786 |  | checkpoint | Locations coordinate with other services
checkpoint-status | 154aa57d-d268-4e59-a652-34f433f93690 |  | checkpoint | Marking out if required - refer to reflected ceiling plan for set out
checkpoint-status | c45663d1-4504-4606-970d-43b662289f08 |  | checkpoint | Plug in or fit off light / plug base
checkpoint-status | b915c389-ab4f-4139-acf7-d9986486fe0c |  | checkpoint | Install light fitting
checkpoint-status | e0bc3668-e62a-4a76-9015-0a168c83671b |  | checkpoint | Install lamps and diffuser
checkpoint-status | c71a526c-ee46-46a2-8439-376b644c48e3 |  | checkpoint | Clean fitting, lamp diffuser
checklist-flat | 71b045b2-979f-48e0-81c9-411be022c19f |  | checklist | ITR No.1 Apartment Rough In of Electrical Services |  |  |  |  | Yes | ITR No.1 Apartment Rough In of Electrical Services | 401bb35d-f04e-4afc-baab-63a88c993ef1
checkpoint-status | 1bd89e7d-1e10-4c55-87d4-8a6d21fd578f |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | 90e66c17-d34e-4adb-a56f-8aebcfe4b3b9 |  | checkpoint | Drawing Rev No.
text | f87b8813-c5df-5204-96fe-fa110e4504a2 |  | textbox | Drawing Rev No.
checkpoint-status | 40409427-e9b4-42f1-a2c0-2602a91b9956 |  | checkpoint | Rough in Hard Actives to all switches
checkpoint-status | 62fa7b00-0953-43f9-8caa-095602f2ed34 |  | checkpoint | Rough in of Switched Actives from switches to lights & Fit off Quick connects whilst on ladder
checkpoint-status | 2798b04c-9f51-4400-92b2-0cbd73d3b19e |  | checkpoint | Rough in GPOs
checkpoint-status | 324084e2-e047-480e-b8a7-50acd1c32c00 |  | checkpoint | Rough in of all kitchen general power (including island bench) above bench, gas cooktop, fridge, microwave, rangehood & dishwasher
checkpoint-status | e0e54b49-204f-4b51-b916-4103b10a9a5d |  | checkpoint | Rough in A/C & Oven
checkpoint-status | 015952c4-e0fb-4fd0-8723-8428bee5385f |  | checkpoint | Rough in single tail island bench Pendant to the nearest downlight
checkpoint-status | 24437d45-87e5-4832-9474-22981b0fa1e5 |  | checkpoint | Rough in a loop from Pendant to LED strip at rangehood
checkpoint-status | 93c20112-bd00-4d72-a0b1-18db5da45250 |  | checkpoint | Rough in bathroom LED Fig 8 downight location and switch separately
checkpoint-status | 1fa86c02-5837-4c2c-bf3f-762036fa2c5a |  | checkpoint | Rough in LED fig 8 to study desk to nearest downlight
checkpoint-status | 46b0d2db-6de2-4cee-942c-24cb10611670 |  | checkpoint | Rough in all internal lights
checkpoint-status | 9495697e-bab3-41ab-87cd-830b30f4cd2c |  | checkpoint | Rough in Balcony wall light- If 2 lights, bring 2 switch wires back to switch
checkpoint-status | 82a7d051-440b-4b07-984e-99fca4bbe5cc |  | checkpoint | Rough in smoke detector and interconnect to other detectors.
checkpoint-status | 240420eb-9f93-4d41-88b1-ba57a6dec997 |  | checkpoint | Rough in bathroom fans off power circuit and HA loop at fan
checkpoint-status | d8a84be5-ed12-4de2-a705-77c20a465ff8 |  | checkpoint | Rough in WM/DR and install SDI from dryer gpo to laundry switch
checkpoint-status | 3cfe138f-d8a0-4f60-9d54-04e2a95cf3d3 |  | checkpoint | Rough in WP GPO to balcony if applicable
checkpoint-status | 99f6a8ec-e680-4bde-a956-02835f32aee4 |  | checkpoint | Rough in intercom patch lead to LBNCO hub
checkpoint-status | 9ba95e6f-0bc1-4ee6-a510-ce4cf0e32ab6 |  | checkpoint | Rough in tv points to LBNCO hub
checkpoint-status | da0ce859-a6c1-48b4-8e4a-45d603cde723 |  | checkpoint | Rough in data points to LBNCO hub
label | b8467837-c44f-5555-af29-9809b3bb2600 |  | note | Ensure LBNCO draw string is in
label | 083d0832-e2c9-5ca4-8091-456043f90afb |  | note | Ensure Sub Mains are at Switchboard Location
checkpoint-status | 6def4f8c-bcb7-43ed-94f5-91a9d91762fb |  | checkpoint | Install switchboard & fit off
button | 3fea5cad-9081-5364-8ab1-e7bd6cd92e66 |  | button | Install 150mm stud protecting sub main and earth with nut & bolt | Yes,No,N/A
button | d161c565-95f6-5ff7-ac23-dd61343696b4 |  | button | Install 2.5mm earth tags | Yes,No,N/A
button | 7efeb4ee-0b3f-5929-a423-525a9bbdcde3 |  | button | Fire caulk sub main into DB and all cable entries | Yes,No,N/A
button | e3d1290d-7347-59f9-8105-e60f1c12a851 |  | button | Fit off 4 pin plug base | Yes,No,N/A
checkpoint-status | e6a01ca1-c676-49b6-a33f-f541294328c5 |  | checkpoint | Ensure all Quick Connects are fit off
button | 69112305-4333-5ebf-8ff3-4db294625ae8 |  | button | Ensure all cables are neat, taped to studs and easily accessible for cut out | Yes,No,N/A
button | 91917925-8c22-55d9-b605-607e5ad52cd1 |  | button | Ensure all cables are clearly labelled at DB and at party walls | Yes,No,N/A
checkpoint-status | cadd6c76-f509-47e7-920f-a81bfe487bbc |  | checkpoint | Ensure area is left clean
checklist-flat | cdd17d2e-5b50-442c-b2be-85ccfcb46543 |  | checklist | Installation of Temporary Power 33 |  |  |  |  | Yes | Installation of Temporary Power 33 | 487bfa5e-1466-4c7a-9a6d-eae258eb438b
checkpoint-status | 14fa0782-d1c9-4415-8549-e52c3852f658 |  | checkpoint | Locate & fix into position
checkpoint-status | 2e1daa37-0c9b-40fe-a3e4-b0d93338f9f2 |  | checkpoint | Bolt temporary board down with at least 2 fixings
checkpoint-status | 3d6d709b-3fee-4b51-b8fc-a8c165d5ed6a |  | checkpoint | Install sub mains cabling as appropriate eg. glands, tray, duct
checkpoint-status | 74d1a6d6-9f6e-4bd6-a36d-8087ddfcef20 |  | checkpoint | Install lugs and terminate
label | 9531bd40-20dc-57c4-8353-3bbe6be30614 |  | note | Any cables not terminated prior to energisation must be removed from cubicle at origin and have ends covered in heatshrink. At destination cables must be covered in heat shrink and be contained in a junction box
checkpoint-status | bd343ebc-3b6e-44cd-8b56-861983772a94 |  | checkpoint | Clearly identify services
label | 4bdde588-6af3-583b-9ab2-302a47aee0c3 |  | note | When ready to energise proceed in accordance with energisation procedure
checkpoint-status | fa1ee144-821e-4706-ba8e-cf0521790b07 |  | checkpoint | Energize & record results on itp 14
checkpoint-status | 45cd721a-27fb-44ca-a6da-93dc81b8230f |  | checkpoint | Update temporary power board register
checklist-sectioned | 2ce1006c-69a7-448a-9890-32857f64ea21 |  | checklist | ITR No.13 Basement Commissioning Distribution Boards and Light and Power |  |  |  |  | Yes | ITR No.13 Basement Commissioning Distribution Boards and Light and Power | 4fb64964-3b1a-4889-9dd6-a6c4cba9a67e
checkpoint-group | cfadc16a-8391-483f-b2a0-cf36938cd9ba |  | section | Distribution Board
checkpoint-status | bcc0ee23-cf82-4992-a621-2910f44bf62a |  | checkpoint | Area clear, tidy and accessible
label | 2c63370e-3f98-5cfe-a489-ec78375f7390 |  | note | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
label | 87b165e1-11e7-5a48-a18c-78e0d3f6987c |  | note | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
label | fcbef298-c846-566f-a7b5-1e05fcf894de |  | note | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
label | 0c75335d-9bc5-5aa8-b459-302b09342a9f |  | note | Collect material from the office and have the correct db structure downloaded.
checkpoint-status | 44fea7f9-fa74-47da-baee-2bf44047188d |  | checkpoint | Commence commissioning
label | c9fe3d51-43ea-5ab0-aa23-c531660e5dab |  | note | Update copies of distribution board schedule with any additions/deletions return db schedule to office for typing of switchboard schedule, leave copy in switchboard
label | a29c2200-13d6-54ca-bd49-405d472f376f |  | note | Check typed schedule for accuracy and install in schedule holder
checkpoint-status | 09cd7023-13ed-4aed-a0af-8848c3dcb58e |  | checkpoint | Clean switchboard cupboard
checkpoint-group | 96e53c1a-7bba-4a4a-8104-b823dd167d7d |  | section | Light and Power
checkpoint-status | b88e8060-9488-493a-bc96-d9443bf6276a |  | checkpoint | Energisation permit completed prior to energisation
checkpoint-status | 0f82e311-aaea-4b53-976e-e5c7156cd659 |  | checkpoint | Visual Check all items
text | 3f3f20f8-42cc-5f6c-96da-97738fad7861 |  | textbox | Dead Testing
text | 3013fde1-5bd0-5790-a012-5abde9a2d345 |  | textbox | Live Test
text | 2c0dc4f6-9ed9-57e9-8723-7c70e00fd131 |  | textbox | Record Metrel Results and log
checkpoint-status | d67be777-9091-46cd-b949-d4bab7561d44 |  | checkpoint | Test plug bases for switching
checkpoint-status | 4c623afb-7819-41f3-aa04-36314d5c951d |  | checkpoint | Check light switches/Sensors for correct switching functions
checkpoint-status | d094917a-083b-4cb5-a638-07ee24d5acc1 |  | checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
checkpoint-status | b3b88cbc-509d-407e-9ed3-56d2d93b7bae |  | checkpoint | Install switchboard cover / label (take photos)
checklist-flat | 3b18d67c-ec91-4ac8-8126-8740487a12b9 |  | checklist | ITR No.32 Woolworths Switchboard Installation and Terminate Sub Mains |  |  |  |  | Yes | ITR No.32 Woolworths Switchboard Installation and Terminate Sub Mains | 57d80696-f845-4050-8992-534169d964a8
checkpoint-status | d7cf3434-99f0-49bc-8b19-674b46f016c3 |  | checkpoint | Area clear, tidy and accessible
checkpoint-status | ac9d2849-1d70-4644-9f71-7a0e6604d177 |  | checkpoint | Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | f4f2b441-e00b-46b3-a0af-9229a10ff659 |  | checkpoint | Locate & fix into position
checkpoint-status | bbee1c23-89ea-4676-bbb2-2a39ca8550b3 |  | checkpoint | Install sub mains cabling as appropriate eg. glands, tray, duct
checkpoint-status | be6c85e1-0f56-4cd9-9982-03f8d051286d |  | checkpoint | Install lugs and terminate
label | 085db872-c447-5924-b2d0-dc3d39b81d4a |  | note | Any cables not terminated prior to energisation must be removed from the cubicle at origin and have ends covered in heatshrink at destination cables must be covered in heat shrink and be contained in a junction box
checkpoint-status | 73ee3748-5069-406c-bf3e-96e6867a29ca |  | checkpoint | Clean & vacuum
checkpoint-status | 1bf9b27d-a71f-49e2-80cf-ba49520adb8c |  | checkpoint | Organise inspection by inspector, lodge prescribed / non prescribed (as applicable) certificate of electrical safety (if required).
checkpoint-status | fa5c5570-fbc2-4a01-8a01-05bef7604dad |  | checkpoint | Clearly identify services
label | c2ef9578-e0da-5023-871a-6212cab58200 |  | note | When ready to energise proceed in accordance with energisation procedure energize & record results on itp 116
checkpoint-status | 45bf49b1-a7f2-4809-9b14-503efb5606f0 |  | checkpoint | Check the switchboard as installed matches the shop drawing.
label | 25403490-e7e8-5c8c-bb87-fb2419030a28 |  | note | If necessary modify shop drawing to match installed & return to office
checkpoint-status | 6388006c-2b37-427c-9683-d9c23cb4a87b |  | checkpoint | Clean switchboard cupboard
checkpoint-status | d164d542-40fc-41ef-b424-7eb42acadb91 |  | checkpoint | Install sub circuit cabling in accordance with db schedule and terminate
label | 40ed2e6b-8d0d-5fdf-80ab-fc0a3bdb0d82 |  | note | If the circuit not complete at the other end, it must not be terminated but placed in a junction box at field end and in connectors at distribution board end
checkpoint-status | 6b3c7a2e-3f3c-4a71-ab2d-bbbf22732b88 |  | checkpoint | Clean & vacuum
label | 7edf0054-033d-5268-9e65-d29707595ede |  | note | Record relevant information and any changes on db schedule and return to administrator/office for commissioning team
checklist-flat | 962fd80a-874f-49d3-8794-be5e09148c19 |  | checklist | ITR No.25 Retail Mains and Sub Mains |  |  |  |  | Yes | ITR No.25 Retail Mains and Sub Mains | 6177aad9-8950-43f4-bb39-b4c28136e685
checkpoint-status | c1d4b56c-c1dd-45b4-b773-9dd980987347 |  | checkpoint | Area accessible & ready
checkpoint-status | 96a26cc6-f6ab-454c-95d3-1d65771843d9 |  | checkpoint | Measure cable runs with appropriate accurate measuring instrument eg tape measure, wheel, rope in conduit
checkpoint-status | 028326e4-28c5-46b4-8dd0-458abc135994 |  | checkpoint | Confirm length of cable
checkpoint-status | 599de622-fabc-41a5-b8f9-95bc7f3bfa28 |  | checkpoint | Install cable in applicable method
label | 479a84e6-272c-5898-9cab-5507d7082498 |  | note | Eg. cable stands, electric winch, pulleys etc. any cable not terminated immediately must have the ends taped covering the bare copper. Trefoil (refer to details on back for all options) cables and tie cables to support system
checkpoint-status | 59f52cbf-5999-4673-bad4-aa9d0c832ac3 |  | checkpoint | Check requirements for cable identification and install
checklist-flat | 1c8edca6-53ed-41ef-a89f-92e9bbf51aa1 |  | checklist | ITR No.30 Woolworths Light and Power rough in |  |  |  |  | Yes | ITR No.30 Woolworths Light and Power rough in | 78c07522-eff1-41e3-86e1-f01694f4c533
checkpoint-status | 20ef74e5-9cb7-4df0-8cff-54fd81b453ed |  | checkpoint | Area accessible & ready
checkpoint-status | 563f33e1-a8b9-4754-ad58-7c288ce6d7bc |  | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
label | 8e43d256-3f58-5531-80fd-97c7147a3ade |  | note | Determine cable size as per itp 30 selection of cables for subcircuit wiring etc.
label | bc9049dc-8b27-5dd9-aa63-dcdf9f26633e |  | note | Determine cable support system ie. catinary, cable tray, fix to structure, ducting
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | 59d5adbf-a186-4135-a285-b3b5ece6b125 |  | checkpoint | Install cable support system
label | 9507c925-68ae-502a-960f-245717093b24 |  | note | Check cable size/type, black sheath for power, white sheath for light: 4mm to be used for runs over 90 metres (unless specified differently)
checkpoint-status | f0cb7d4b-301d-430c-9e8e-977ca12f291b |  | checkpoint | Install and identify cables. any cable not terminated immediately must have the ends taped covering the bare copper
checkpoint-status | b30ddf5e-ace0-4a63-b67d-19969cfdda25 |  | checkpoint | Fix cables to support system
checkpoint-status | 0b455a58-54ea-4865-bb74-01ac3041c7ce |  | checkpoint | Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
label | 4ed6bb7b-3a5e-5180-a52e-489231e01282 |  | note | All cables are to be identified as follows: db no. followed by circuit no. then feed or active, white cable mark with black texta, black cable white tape then mark with black texta.When roughing in power circuits in stud wall etc. the loop in loop out at the gpo location shall be taped together. if the cables are taped
label | eea41f80-1159-5312-9fab-4a5770ce159a |  | note | Together it will ensure that the tradesmen fitting off the gpo will connect all cables. as tradesmen complete the rough in they should mark up the drawings the locations of the feeds and runs etc. this will assist where another tradesman completes the job and fit off.
checklist-flat | 8cfd0db4-5ed7-4a2f-b357-2c5632a32a5c |  | checklist | VAST Site Induction |  |  |  |  | Yes | zSYS - VAST Site Induction (old version) | 8d9e1b13-38bf-42c8-9cac-513872f81263
checkpoint-status | 96d8d525-ed04-45d1-a257-bf921ee094d3 |  | checkpoint | VAST Employee
text | f848378c-5fe6-55e4-a580-44b8d1a58c13 |  | textbox | Name
text | b1b558f3-271a-59d2-babf-2f785c0f0411 |  | textbox | Contact Number
text | f5d30305-fed1-5be1-8546-0af862c4c3e9 |  | textbox | Date of Induction
label | 6ac7b96a-2081-5237-bf65-380b38c28528 |  | note | Tick if the following are understood:
boolean | 26dc4d72-e372-53eb-ba25-8f0f0f8cf800 |  | tickbox | How to report to the site and who you report to
boolean | 6f6a7641-93d3-5f2d-8d48-401cf550f927 |  | tickbox | The working hours on site
boolean | 1542be82-0c20-5f87-9fcc-bdcbb5cb8dc5 |  | tickbox | Who the managers and supervisors are on site
boolean | 249618fa-0c9b-5dd6-9fe6-cd017e39a64c |  | tickbox | The correct minimum PPE for site
boolean | d2c17e52-67b0-58fc-8ce0-0d3e987bb042 |  | tickbox | How safety is communicated on site
boolean | f342569b-f0e4-5132-969d-1e5f04217686 |  | tickbox | Where to have lunch and where the toilets are
boolean | 58a85351-04c0-5615-af4c-ab72a53fd40a |  | tickbox | Where the First Aid Kit is kept and who is the First Aider
boolean | a1e22243-a41f-5952-abf2-6a1679135c29 |  | tickbox | The Emergency Plan and the Assembly Area for Emergency Evacuation
boolean | 6d68cc3a-5e1a-5a3c-811b-f86ee10586c9 |  | tickbox | What the high risk activities and hazards are on site
boolean | 389d7047-37ae-5c41-aa2e-e438823e9c29 |  | tickbox | How to report WHS & Environmental hazards & issues
boolean | c0fcc7f1-7066-5d6f-95d1-0d0b6ac9a4d3 |  | tickbox | How to report a safety or environmental accident or incident
boolean | 6ee0df64-f264-51b8-9990-11b8b0bc08d5 |  | tickbox | Housekeeping responsibilities
checkpoint-status | 124d9ad0-92e7-4c59-b0bb-c85838231b04 |  | checkpoint | EWP Licence - Please take a photo
checkpoint-status | 4276c4f5-e589-43b2-840c-83ac6ff2cb55 |  | checkpoint | Current Certificates Sighted - Please take a photo & comment on each attached certificate
checkpoint-status | 7c998531-773c-4b3d-ae11-998798d344f2 |  | checkpoint | VAST Employee Signature
checkpoint-status | 684cf8af-317e-487d-8fbb-f87017706d7e |  | checkpoint | VAST Supervisor Signature
checklist-flat | 97d6298f-0e00-44a0-a138-c1a8ff847bbe |  | checklist | ITR 33. Installing Underground Services |  |  |  |  | Yes | ITR 33. Installing Underground Services | 8de9fed4-be77-49bb-82fa-37d85074bbe2
checkpoint-status | 7d443737-7858-4849-8a09-befd179395a5 |  | checkpoint | Inspect conduit material to check that it meets material specifications
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | ecab7123-515d-4c48-a9a7-a7316d2453e2 |  | checkpoint | Check conduit alignment as per plans
checkpoint-status | 5a12cce8-ccaf-4e47-8db2-c8c8022cdf58 |  | checkpoint | Set out marked, and all services located
checkpoint-status | 9dbab46c-04d0-47a7-9e71-1680399709c3 |  | checkpoint | Erect pedestrian barricading as per plan
checkpoint-status | c6adf54f-0c56-49ce-8474-fc78b6d43f54 |  | checkpoint | Check excavation depth against proposed road level
checkpoint-status | 0e668ab6-8d6d-4cac-9d9b-5b8af9b937ed |  | checkpoint | Excavate to the trench as per plan
checkpoint-status | 45cca4ca-97b5-48b0-b084-c1ea3c9c0d4e |  | checkpoint | Place specified bedding material in trench
checkpoint-status | ffbe757b-8095-4a51-af59-54549d9d50b5 |  | checkpoint | Placement of conduit of specified size in accordance with specifications/drawings
checkpoint-status | 400eb47b-2d15-4b35-871c-babdf235d6d0 |  | checkpoint | Backfill over conduit to 300mm
checkpoint-status | 14ae81e5-bced-48a5-ba3f-06b76d850f6e |  | checkpoint | Install cover slabs above conduit
checklist-flat | 6b7c7785-4998-4966-b7d1-fe49fee8d566 |  | checklist | ITR No.31 Woolworths Mains and Sub Mains |  |  |  |  | Yes | ITR No.31 Woolworths Mains and Sub Mains | 8fe996d0-bca7-425e-a9ef-76e5275e6ff1
checkpoint-status | 6378fdbd-e74f-4659-bc24-742464b98310 |  | checkpoint | Area accessible & ready
checkpoint-status | 7a6928f6-a1ff-47b7-bdf8-0d23936551e0 |  | checkpoint | Measure cable runs with appropriate accurate measuring instrument eg tape measure, wheel, rope in conduit
checkpoint-status | d6efcf47-0e99-4309-9eeb-8f447c6f2d19 |  | checkpoint | Confirm length of cable
checkpoint-status | f98a124b-d8a0-479a-aabb-31d6645e1485 |  | checkpoint | Install cable in applicable method
label | 7b30e76a-c4cf-5d01-86e5-8114ac562986 |  | note | Eg. cable stands, electric winch, pulleys etc. any cable not terminated immediately must have the ends taped covering the bare copper. Trefoil (refer to details on back for all options) cables and tie cables to support system
checkpoint-status | 0390c2f2-d2de-4856-8475-e2396158b1c4 |  | checkpoint | Check requirements for cable identification and install
checklist-flat | baf9b892-efbc-408a-9a4c-65a6e713dac8 |  | checklist | ITR No.0 5 Hallway Rough In |  |  |  |  | Yes | ITR No.0 5 Hallway Rough In | 90bfd734-ae05-421d-8aee-1759e7efb0e9
checkpoint-status | 19733715-9bf2-41a2-ab14-1c5013a9d1b9 |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | ad88bcff-2205-44ea-9738-e6abe8506579 |  | checkpoint | Drawing Rev No.
text | b6972ac8-d50b-5651-a24e-b68836349707 |  | textbox | Drawing Rev No.
checkpoint-status | fffa6e8e-36b7-4aed-92c4-e4dbe4486923 |  | checkpoint | Mark out all public L+P in hallway
checkpoint-status | 30ece6bf-d607-47b2-8813-65ab976f115f |  | checkpoint | Rough in lighting, Emg/Exits and sensors
checkpoint-status | 64227ee3-38c5-4045-b952-40c49cb2c427 |  | checkpoint | Rough in cleaners power, water meter power, window louver (CS) if applicable
checkpoint-status | 0fb00472-f9df-40d2-9d18-71e81e83d175 |  | checkpoint | Rough in comms riser power
checkpoint-status | cc70d3ed-d8fb-4d9b-b250-399ad1c7988d |  | checkpoint | Rough in lighting feed to first lighting point near elec riser
checkpoint-status | 68ed7600-e0d9-4312-bdb8-21d0a9a8a54b |  | checkpoint | Rough in power feed to first cleaners point near elec riser
checkpoint-status | e4e83005-cdb2-4f02-aac2-757ce1baeb69 |  | checkpoint | String all comms conduits
checkpoint-status | 88496152-9e0f-412d-841d-91ca2ffe2fbe |  | checkpoint | Rough in all apartment sub mains from riser to apartment DBs and LABEL
checkpoint-status | 0146c0a5-b6db-40bf-91af-6040761b3ee2 |  | checkpoint | Rough in stair doors access control
checkpoint-status | f3db0d0f-c89a-4743-9b3a-43cbea69b316 |  | checkpoint | Rough in any relevant comms/access control from one floor to another ( Backbone )
checkpoint-status | c1e435b6-b4ef-4832-beb2-855727b8f494 |  | checkpoint | Check for clashes with other services
checkpoint-status | f4eba648-d242-40f7-a2b7-62d58a719db4 |  | checkpoint | Fire caulk riser cupboard door headers ( smoke seal only )
checkpoint-status | 1208ad52-c021-4ab8-9258-1b4b00b031c8 |  | checkpoint | Fit off plug bases & quick connects
checkpoint-status | a14af2cb-c993-4a6c-bd62-9b04eba17b8d |  | checkpoint | Ensure area is left clean
checklist-flat | a4043d2e-5653-4b15-98a7-2d536d3ad8e7 |  | checklist | ITR No.19 Dan Murphy's Light and Power rough in |  |  |  |  | Yes | ITR No.19 Dan Murphy's Light and Power rough in | 910c3a57-10ec-4a66-b2a2-5bc3c8c354da
checkpoint-status | c05fe0bf-738f-44f6-abaf-f861cf7eda29 |  | checkpoint | Area accessible & ready
checkpoint-no-status | ad88bcff-2205-44ea-9738-e6abe8506579 |  | checkpoint | Drawing Rev No.
text | b6972ac8-d50b-5651-a24e-b68836349707 |  | textbox | Drawing Rev No.
checkpoint-status | b0990058-457a-4104-9108-f07fd924ad7d |  | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
label | b6972ac8-d50b-5651-a24e-b68836349707 |  | note | Determine cable size as per itp 30 selection of cables for subcircuit wiring etc.
label | 0be5eb90-c718-5755-bb39-7f894a286c3a |  | note | Determine cable support system ie. catinary, cable tray, fix to structure, ducting
checkpoint-status | 3dfc8cfd-48da-4857-a0e9-1e51bc1f9830 |  | checkpoint | Install cable support system
label | f83ae71e-bffd-50f7-82aa-568771f69c76 |  | note | Check cable size/type, black sheath for power, white sheath for light: 4mm to be used for runs over 90 metres (unless specified differently)
checkpoint-status | cd6886bf-6b9d-4296-917b-fc682181be3b |  | checkpoint | Install and identify cables. any cable not terminated immediately must have the ends taped covering the bare copper
checkpoint-status | e3b56423-2523-40f8-9426-08c1a1c7456a |  | checkpoint | Fix cables to support system
checkpoint-status | 429bba9c-1ceb-4a9f-99a0-6e5e6c88c714 |  | checkpoint | Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
label | 101f3878-b882-5da5-8f10-9b93c600d050 |  | note | All cables are to be identified as follows: db no. followed by circuit no. then feed or active, white cable mark with black texta, black cable white tape then mark with black texta.When roughing in power circuits in stud wall etc. the loop in loop out at the gpo location shall be taped together. if the cables are taped
label | 2e41b155-6667-53cf-b27c-92250c7848c8 |  | note | Together it will ensure that the tradesmen fitting off the gpo will connect all cables. as tradesmen complete the rough in they should mark up the drawings the locations of the feeds and runs etc. this will assist where another tradesman completes the job and fit off.
checklist-flat | 98c56802-345d-439d-b6ba-104df4fd907d |  | checklist | ITR. No 4 Commission Electrical & Permanent Power |  |  |  |  | Yes | ITR. No 4 Commission Electrical & Permanent Power | 913f4312-6a2c-45ce-bd95-8f3f5ef490ca
checkpoint-status | 79001fd5-f866-496e-96df-856d9b2498c1 |  | checkpoint | Energisation permit completed prior to energisation
label | a24aacf1-dbf0-5f00-9203-9160e2c4371c |  | note | Visual Check all items
checkpoint-status | cf2b6d28-e66b-4ef3-96cb-42e51e23a9b8 |  | checkpoint | Dead Testing
checkpoint-status | 65f78cbf-a92f-4ce7-8f73-6b00bbd3172c |  | checkpoint | Live Test
text | 0df7aac7-6505-5c58-a522-6f72163a6809 |  | textbox | Record Metrel Results and log
checkpoint-status | 007b3c10-9fe9-41fe-93a2-931879390dc8 |  | checkpoint | Test 4 pin plug base for switching
checkpoint-status | 7c01ff2f-198c-457a-b234-5476e950afa6 |  | checkpoint | Check light switches for correct switching functions
checkpoint-status | abfa7724-f109-4bf4-83ce-4c3d1a3f3171 |  | checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
checkpoint-status | 942c4fde-0ada-48c7-a124-1ebae3ed35c2 |  | checkpoint | Install switchboard cover / label (take photos)
checkpoint-status | 7ed83131-76e3-4a58-9cbd-eabe2612bf91 |  | checkpoint | Remove battery tabs on smoke detectors ( after MFB certification )
checkpoint-status | c0f2a214-2caf-4983-882b-3d3eba004a07 |  | checkpoint | Ensure area is left clean
checklist-flat | 601dfdfe-3a59-42c5-8c1e-16d25b53c7cf |  | checklist | ITR 14. Basement Commissioning Main Switchboard |  |  |  |  | Yes | ITR 14. Basement Commissioning Main Switchboard | 92c9af47-36e2-4519-b9fe-c3dfe1787d3f
checkpoint-status | c1415568-d88e-4340-9703-b30d48da0b69 |  | checkpoint | Area clear, tidy and accessible
label | c4fa1008-cbd0-543f-8102-5bce2ab82e79 |  | note | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
label | 061a49ab-31b5-5726-8b00-bf1e51ea3a34 |  | note | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
label | 4196b9f7-2791-56eb-865f-1f64ad965146 |  | note | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
label | 17cf5e0a-a40a-53c3-b91a-ce1bae5c3f82 |  | note | Collect material from office and have correct db structure downloaded
checkpoint-status | 8f193bee-9a6f-4980-8957-b73325d70ebc |  | checkpoint | Commence commissioning
label | fc4f4a7b-c4b2-5f0f-8cb6-e4e3f20905bf |  | note | Update copies of distribution board schedule with any additions/deletions
label | 4e4a0900-8fac-59ee-a40e-9c8bcc5cc0fe |  | note | Return db schedule to office for typing of switchboard schedule, leave copy in switchboard
checkpoint-status | ca3a6e1d-b8ce-464e-a383-d866f9cd780d |  | checkpoint | Check typed schedule for accuracy and install in schedule holder
checkpoint-status | 844e729a-b68d-4012-954d-ab0f20279912 |  | checkpoint | Clean switchboard cupboard
checklist-flat | c9dce505-d0c8-405a-ba2e-31f01383006d |  | checklist | ITR No.27 Woolworths Bakelite and Power fit off |  |  |  |  | Yes | ITR No.27 Woolworths Bakelite and Power fit off | a1a0cc1d-d5af-4d5d-8c0c-c8ecd258bdf9
checkpoint-status | 7d53aeab-84a8-40f5-a180-074c14cfa12f |  | checkpoint | Area clear, tidy and accessible
label | 25dc4afd-c172-58d3-900b-f1b9e19dcd8b |  | note | Check drawings for quantity, brand type and colour
label | 5591f2f8-7a5a-5234-bd93-4cbcb15c096e |  | note | Location/compliance wet areas, hazards etc. mounting heights
checkpoint-status | e34028f6-19b8-406e-b5bd-90cae6bb67ae |  | checkpoint | Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. each circuit must be fitted off completely
checkpoint-status | 73a73c17-490f-4e8e-8df6-c8e431829b16 |  | checkpoint | Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use a shroud
label | 47cabf10-37c2-5981-9245-afb9c6fff71e |  | note | Each circuit must be fitted off completely
checkpoint-status | 22d8f211-ece2-4a99-b259-8560e73e9bc3 |  | checkpoint | Fit off final appliances
checkpoint-status | c135b668-98af-490a-819b-1a43fcf4135e |  | checkpoint | Cover plates (if required)
checkpoint-status | 912c552d-616b-4486-964e-353aaed8458b |  | checkpoint | Install label (if a specified requirement)
checklist-flat | 31a2501e-8ef2-4a7f-91f9-03c94fd25786 |  | checklist | ITR No.6 Hallway – Hallway Cutout Ceilings & Walls |  |  |  |  | Yes | ITR No.6 Hallway – Hallway Cutout Ceilings & Walls | a7dfa97f-8d49-4a54-8001-4094f37102f2
checkpoint-status | b816a126-3538-47ef-af4e-2a5fcdce7057 |  | checkpoint | Confirm sizes off all fittings prior to cut out
checkpoint-no-status | 9ebf94aa-a132-4e0e-b2a1-63618c4db2da |  | checkpoint | Drawing Rev No.
text | 03553d64-1dfe-51b6-b971-cf28b5c2bcd5 |  | textbox | Drawing Rev No.
checkpoint-status | 27a2dd76-a0b4-4533-a08a-9c8686381045 |  | checkpoint | Cut out for all sensors, EX/EMG, light fittings
checkpoint-status | da1f7838-6bf0-4cf6-8c7f-312ef694e59f |  | checkpoint | Cut out all cleaners GPO’s, Comms Riser GPO’s
checkpoint-status | ca05d859-efbe-406c-874c-429874fb9a56 |  | checkpoint | Cut out any CCTV cameras
checkpoint-status | 4445625e-02f1-461d-b88e-7bdab2a9ec5d |  | checkpoint | Ensure Electric Strike cable is inside the pressed metal frame cut out
checkpoint-status | 2bdcdf9e-c5ad-42f0-8477-7d19576a69af |  | checkpoint | Locate all Cables
checkpoint-status | aef20a05-7068-439a-a71b-c63214b4513e |  | checkpoint | Install Firebox’s
checkpoint-status | b308b336-2b28-44bf-9e88-27260cdae1b3 |  | checkpoint | Clean Up
checklist-flat | f188a879-2241-400c-b2b0-888c04a312e7 |  | checklist | Decommissioning of Temporary Power 34 |  |  |  |  | Yes | Decommissioning of Temporary Power 34 | abc325ea-ab64-40db-a456-9a021a55caec
checkpoint-status | d78c9803-4066-493e-938a-ea2d84d42452 |  | checkpoint | Determine what the temporary board is controlling and confirm what action is required before board can be de-Commissioned.
checkpoint-status | 646880aa-abca-45cc-96f1-831728911f11 |  | checkpoint | De-commission form issued to builder, 48 hours notice to be given
checkpoint-status | 65dce7d7-dc2e-45bd-9a8e-b5bebcb70f12 |  | checkpoint | Sign off builders checklist
checkpoint-status | aadb5eec-b075-44d0-b23f-b5596d74ebbc |  | checkpoint | Safety Committee Inspection
checkpoint-status | 09c9d9c4-5063-4e33-9522-35fcbd62de8e |  | checkpoint | Final approval to be given by builder
checkpoint-status | a740e64c-c285-46ce-8d6f-2b82e57e7c3a |  | checkpoint | Perform voltage test to ensure power supply has been isolated
checkpoint-status | f438fbaf-c18c-480e-a981-56a60c80fcd2 |  | checkpoint | Disconnect supply cables
checkpoint-status | 5b0296ed-61be-4739-b331-6723d5de72d4 |  | checkpoint | Fire sealing of penetrations
checkpoint-status | 89da58cd-b70f-4cf4-930b-81d2ee3a65de |  | checkpoint | Remove temporary board
checkpoint-status | 5b19c65d-734d-4c11-bc46-942d8e593122 |  | checkpoint | Update temporary power board register
checklist-flat | 329a6179-6f30-455d-a4de-e23106cc39a6 |  | checklist | ITR No.24 Retail Light and Power rough in |  |  |  |  | Yes | ITR No.24 Retail Light and Power rough in | abe703d8-ada3-48d6-aa76-6548db300a3a
checkpoint-status | 2919ffec-772d-4e67-97a5-24df59c24e49 |  | checkpoint | Area accessible & ready
checkpoint-status | db71d442-40d9-4ecc-aba9-8bbfca49c39a |  | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
label | 039d0aa8-a3f7-5eaf-bccd-285c9f84cb3e |  | note | Determine cable size as per itp 30 selection of cables for subcircuit wiring etc.
label | 2867a715-8a24-5fee-8aea-4e50afeba962 |  | note | Determine cable support system ie. catinary, cable tray, fix to structure, ducting
checkpoint-status | c1216f4c-393c-4c1f-a64f-ab166fe9ea28 |  | checkpoint | Install cable support system
label | 2513fe39-694b-5883-9fb1-c8720c245eb3 |  | note | Check cable size/type, black sheath for power, white sheath for light: 4mm to be used for runs over 90 metres (unless specified differently)
checkpoint-status | 52b4c8bd-2db8-4246-957b-3a2d7215034a |  | checkpoint | Install and identify cables. any cable not terminated immediately must have the ends taped covering the bare copper
checkpoint-status | 634a573a-9d66-4011-9a30-e7f39640b9f5 |  | checkpoint | Fix cables to support system
checkpoint-status | b20eac00-eec5-4d6f-9a0e-09d32ccb65da |  | checkpoint | Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
label | ff2100eb-7347-58c2-ab4c-2265c1692bf2 |  | note | All cables are to be identified as follows: db no. followed by circuit no. then feed or active, white cable mark with black texta, black cable white tape then mark with black texta.When roughing in power circuits in stud wall etc. the loop in loop out at the gpo location shall be taped together. if the cables are taped
label | 3803b540-e517-59d4-8e63-0e69d1f7e082 |  | note | Together it will ensure that the tradesmen fitting off the gpo will connect all cables. as tradesmen complete the rough in they should mark up the drawings the locations of the feeds and runs etc. this will assist where another tradesman completes the job and fit off.
checklist-flat | 1d111636-6520-4aad-a5ef-cfea5c2dab37 |  | checklist | Documents |  |  |  |  | Yes | Documents | b130e2f8-15c1-46d7-88c6-67c7c6e169b0
checkpoint-status | b2d76493-dc5e-4b37-987a-843099f65a1f |  | checkpoint | Attach Document
checklist-flat | 9e913db4-0b8c-4c42-8f12-c9e2cf33c68a |  | checklist | ITR No.3 Apartment - Electrical Fit Off |  |  |  |  | Yes | ITR No.3 Apartment - Electrical Fit Off | bbc675f4-7092-46ac-9856-64a1c2272947
checkpoint-status | 40129032-69d9-42ff-876b-c7ad4d2cb21e |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | 021176fd-a140-49ea-aa11-81e9f2ea5b84 |  | checkpoint | Drawing Rev No.
text | 30daa718-9b74-537e-acfd-a0fc830be82e |  | textbox | Drawing Rev No.
checkpoint-status | e190a9ec-8b68-4f87-a1ae-684066b3c50a |  | checkpoint | Fit Off Downlights
checkpoint-status | 0035c536-241c-4cc4-ab8b-1ce475ad5a59 |  | checkpoint | Fit Off Smoke Detectors ( leave tab & dust cover on )
checkpoint-status | 2f498173-ca70-4e76-9401-f7d267ecb450 |  | checkpoint | Fit off joinery GPO's & install cover plates.
checkpoint-status | 433b0a58-a6d7-4734-9196-bb1fe3a22924 |  | checkpoint | Fit off Laundry GPO & switch
checkpoint-status | 60b06297-61f3-47ce-98e3-a0ec1bb61b63 |  | checkpoint | Fit off all GPOs - Install cover plates & switches where required
checkpoint-status | 6179eb8c-6594-4373-ac4d-0d5a419c17b8 |  | checkpoint | Fit off light switches
checkpoint-status | d066314b-7fb2-40d7-be32-60c608f10550 |  | checkpoint | Fit off TV Point
checkpoint-status | 86d91f60-9410-4707-9a4f-bff532eb456e |  | checkpoint | Fit Off Data Points
checkpoint-status | b566617d-ff6e-4cd6-828e-e079f7a519b2 |  | checkpoint | Fit off Balcony Light
checkpoint-status | 1d2d0adb-c455-49bb-a06b-152fe42c94be |  | checkpoint | Fit off AC Isolator
checkpoint-status | eaad7c40-6f6d-45a7-8229-124e9b9e74ba |  | checkpoint | Fit Off WP GPO ( if applicable )
checkpoint-status | 07526eef-cf68-414c-a275-7d181e273780 |  | checkpoint | Fit Off LED Strips
checkpoint-status | cbfea05d-9a75-4fd1-b86c-5abe1b4843b8 |  | checkpoint | Fit Off Pendant
checkpoint-status | db326b26-ac13-4b05-a713-5a8dc857b843 |  | checkpoint | Install Oven
checkpoint-status | 7feb0c71-57c7-4916-a924-a7bfce0da0ba |  | checkpoint | Ensure area is left clean
checklist-flat | 80dc4550-134c-45cd-bc37-b9cd4f5250da |  | checklist | ITR No.8 Hallway – Commissioning Electrical & Permanent Power |  |  |  |  | Yes | ITR No.8 Hallway – Commissioning Electrical & Permanent Power | bbd48b5c-b3ca-44db-bc6a-501e4a56fa0b
checkpoint-status | 2d11484b-88bb-41ef-b853-17074585007e |  | checkpoint | Energisation permit completed prior to energisation
checkpoint-status | cb98ec23-2c58-49cd-b0b3-7eb8f35b594b |  | checkpoint | Visual Check (against most current plan)
checkpoint-status | 9f44ea9d-44fb-4359-afd4-10b50b954a8d |  | checkpoint | Dead Testing
checkpoint-status | 7ca87a5f-c35a-4869-9b2c-5028f24b3d66 |  | checkpoint | Live Testing
text | 5ae3048f-1309-55cc-93ff-9332b4343142 |  | textbox | Record Metrel Results
checkpoint-status | 960b2607-0cd3-4437-a820-49ca1acb4563 |  | checkpoint | Check operation of all sensors (individually on minimum time setting )
checkpoint-status | 993d584a-ee5b-4161-81fd-e1a5bd20f5fd |  | checkpoint | Check sensors are set to specified time and lux
checkpoint-status | f024c331-f4c0-410d-995a-835cce80b4e3 |  | checkpoint | Check operation of all EX/EMG, perform 120 min test ( initial )
checkpoint-status | 2bcf5aa0-761a-4ef3-8993-37548bc2905e |  | checkpoint | Fit cover plates to all GPOs & exit signs
checkpoint-status | c0e99f70-3368-4a7d-8981-876becdd7f56 |  | checkpoint | Ensure area is left clean
checklist-sectioned | 1e854df2-f5f1-477e-a7a2-52234bbf7f09 |  | checklist | ITR No.09 Basement In Slab Conduits |  |  |  |  | Yes | ITR No.09 Basement In Slab Conduits | c3befd2c-6e43-4717-8fd5-9e55291ddaaf
checkpoint-group | 7b7052c1-fd12-4c67-b041-5cd9f151058c |  | section | Preparation
checkpoint-status | dd7eafd6-53f2-4208-bed1-cad7c1d43c6e |  | checkpoint | Determine origin and destination
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | e0857f75-722b-4d12-a928-8a070775cc8a |  | checkpoint | Check clear of other services, penetrations etc
checkpoint-status | 2d89bd67-9c33-48d4-b52b-6ed527991e66 |  | checkpoint | Check cable size to verify conduit size
checkpoint-status | 6da215ad-55b3-4f87-b5ed-1189cf34df98 |  | checkpoint | Check if expansion joints are required
checkpoint-group | c2022e7c-2dfb-4faf-b81f-7c9381ed15a6 |  | section | Installation
checkpoint-status | 5381eec4-af63-47b4-b886-1ad1e5aee1c1 |  | checkpoint | Mark out positions of junction boxes and penetrations where necessary
checkpoint-status | 0997e714-2baf-45f0-a2cb-1740b06d80a6 |  | checkpoint | Install bar chairs where necessary
checkpoint-status | 0bf37387-bc4c-4c16-b424-5d31fb2b9478 |  | checkpoint | Install junction boxes and conduits and glue
checkpoint-status | 9b171af4-cddb-47ce-a998-8a524ea4dea5 |  | checkpoint | Tie conduits securely at all joints and midpoints
checkpoint-status | 5f92197e-1d40-458f-aa4f-d4b09bfef934 |  | checkpoint | Ensure all conduits are 50mm above deck
checkpoint-status | bfbccf6b-d777-42d5-96fa-601530bf213b |  | checkpoint | Mark up drawing of conduit runs (if required)
checkpoint-status | 45c4d050-c392-4511-8d33-2eb2f8e3e2fa |  | checkpoint | Observe conduits when concrete is being poured
checklist-flat | 0f62d89e-57a0-4260-831a-65fe04aeeb47 |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | d9c66e2b-860c-4cbd-9ba0-6c914f5a676c
checkpoint-status | decd8a96-685e-4f28-8e50-47e2bd93d09d |  | checkpoint | Details
text | acd446e9-425e-519b-992d-37c653e93b3a |  | textbox | Location
text | 584c8b07-1952-52fb-96b1-d33f22ebebe2 |  | textbox | Supervisor
text | f2df7993-08bd-55a7-b963-f6a24029d7ac |  | textbox | Date
text | 86bf3f4c-4b87-5460-95df-79f833b3d475 |  | textbox | Time
text | aada1ba2-e42e-522a-ae83-93188c9d606e |  | textbox | Persons present
label | 2edb7a82-9792-5c51-b090-590b130131a1 |  | note | Topics discussed
boolean | 8620ec71-f1d1-5bde-a218-01579e56052b |  | tickbox | - Injuries, near misses and incidents
boolean | dcd8d09c-2b0c-5491-af13-836000890d20 |  | tickbox | - Management of major hazards
boolean | eb62f661-8372-533c-a886-19ced59e43bd |  | tickbox | - Compliance with our Vast SWMS
boolean | 109aba20-cfdb-59df-8651-ead89987567b |  | tickbox | - Safety - E.g., Apply LOTO processes when applicable. When Megger testing ensure that no person is working at the other end of cable being tested.
boolean | f3c0de5c-d953-5538-b42c-851b5412762b |  | tickbox | - Housekeeping
text | a8f4766f-f8aa-5b17-80ae-f20aa19b7cdc |  | textbox | Comments from the floor
checklist-sectioned | da386b53-9f92-419c-bb7c-d13563957c4a |  | checklist | ITR No.29 Woolworths Light and Power fit off |  |  |  |  | Yes | ITR No.29 Woolworths Light and Power fit off | e63b8c34-75f9-4282-b932-eefbd5450d32
checkpoint-group | 7ff9e592-c0e6-4a6a-8b21-e89e07f70c89 |  | section | Bakelite and Power
checkpoint-status | 596cd444-3f15-4e97-a1f1-c6e055ff0173 |  | checkpoint | Check drawings for quantity, brand type and colour
checkpoint-no-status | 2fc4e02c-a9c7-4188-89b4-76b5b09eda58 |  | checkpoint | Drawing Rev No.
text | ece33f95-dd6a-5636-b876-68f6cf10d96e |  | textbox | Drawing Rev No.
checkpoint-status | 038a3a00-a683-4f7b-8d1e-20eac74aa3fd |  | checkpoint | Location/compliance wet areas, hazards etc. mounting heights,
checkpoint-status | 4fc41113-a7e2-463b-88cc-28300fc8a091 |  | checkpoint | Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. each circuit must be fitted off completely
checkpoint-status | d709875d-5790-4d19-b5ec-20b031931c07 |  | checkpoint | Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use a shroud. each circuit must be fitted off completely
checkpoint-status | 79bc8ab5-8e53-4afc-af3b-17a226656dd8 |  | checkpoint | Fit off final appliances
checkpoint-status | e1a536c9-c4aa-4668-9815-fac458120c5a |  | checkpoint | Cover plates (if required)
checkpoint-status | f14b2f87-2a27-480b-acdf-b21b56d1bec3 |  | checkpoint | Install label (if a specified requirement)
checkpoint-group | 045b0acd-398c-4cfd-8be1-b44490e969df |  | section | Light Fittings
checkpoint-status | a8243e0a-1f2f-41ae-9c56-f5a2dcf0dfa0 |  | checkpoint | Delivery check for damage and correct quantities
checkpoint-status | 896b30c5-f9e5-47a3-a362-470667f560b5 |  | checkpoint | Locations coordinate with other services
checkpoint-status | 497ddc68-b6f5-4236-9ee3-a03df1194958 |  | checkpoint | Marking out if required - refer to reflected ceiling plan for set out
checkpoint-status | e198c74f-d7e0-42b1-bbe9-9ad707f81b10 |  | checkpoint | Plug in or fit off light / plug base
checkpoint-status | 923aafb4-c25f-4f78-b6d7-27573578025a |  | checkpoint | Install light fitting
checkpoint-status | 5e494b6b-f602-46f8-9a25-df327cf7ae80 |  | checkpoint | Install lamps and diffuser
checkpoint-status | 240404da-5fb6-4650-b905-119f89b00841 |  | checkpoint | Clean fitting, lamp diffuser
checklist-flat | 0344ec9c-1e53-43a6-bdf5-56e4197aecef |  | checklist | Drawings / Documents |  |  |  |  | Yes | Drawings / Documents | ea4d34b6-e70d-4e93-bf66-ee12f688be19
checkpoint-status | f8420cd9-cb60-4233-aeea-4bb74eb6611b |  | checkpoint | Attach Drawings / Document
checklist-flat | 425597c5-463b-4a67-898b-5758db6cb055 |  | checklist | Pre-Start Meeting |  |  |  |  | Yes | Pre-Start Meeting | f58c3ebc-9824-4190-93ef-799ec95ca698
checkpoint-status | b6a35b7d-53a6-4a1a-970b-1711c515201b |  | checkpoint | Attach any relevant photos or documents
text | 579753ac-51da-59e3-9936-ef636d434574 |  | textbox | Area:
text | 1dc5d0cc-2eca-59d1-a2fe-22a4c0c3817e |  | textbox | Conducted By:
text | f50469c3-d90c-5226-9deb-77b08da4ad66 |  | textbox | Task/s:
text | 21727569-7508-5df8-858f-94d8acbda4b4 |  | textbox | SWMS
checkpoint-status | b2ee3d09-cf64-46ee-a09a-64eb1c8174f2 |  | checkpoint | Have any hazards been identified?
text | fc7bd89c-b93c-5078-bbfb-9ed55e575df9 |  | textbox | Newly identified hazards are
text | 0e4b8442-b362-52f6-adb2-56e1dfe11822 |  | textbox | Control measures are
text | d03ec190-9f1b-5fde-9fe7-e4fd3063f5a3 |  | textbox | Responsible person
checkpoint-status | 772d7282-6c90-43b8-9af6-42ee3ba6a759 |  | checkpoint | Scope of work for the week was discussed and understood
checkpoint-status | 0478b72e-7f75-4b5c-8520-ddd3be837b94 |  | checkpoint | Relevant SWMS were reviewed, understood and signed by all workers
checkpoint-status | e68dc668-d5d9-472c-adb0-28012ea6eb4e |  | checkpoint | Tools and equipment are in good working order
checkpoint-status | a4234110-b4d6-4ec9-9323-ac80904a2c24 |  | checkpoint | All electrical equipment displays current test tags
checkpoint-status | 7fba354a-90d3-4687-b263-fa3e3cc64f5c |  | checkpoint | Appropriate PPE for tasks is understood and available
checkpoint-status | 990e96cf-1bd0-4b1b-a8c2-5855c0881266 |  | checkpoint | Housekeeping and clean-up has been discussed and is understood
checkpoint-status | e23e0379-df1a-44bc-82b7-998a04edb81c |  | checkpoint | Attendees - Attach name and signature
text | af6089e8-a1d7-5bf8-9079-274e1a1edb10 |  | textbox | Type Names
checklist-flat | c9ad33b9-faf9-4c3e-9de6-cabae581dd1d |  | checklist | ITR No.20 Dan Murphy's Mains and Sub Mains |  |  |  |  | Yes | ITR No.20 Dan Murphy's Mains and Sub Mains | f8b0fe02-e826-4104-be61-f67a4363ed87
checkpoint-status | 2b822e93-40ba-4646-b5b6-15ef627eb17d |  | checkpoint | Area accessible & ready
checkpoint-status | 4896ad83-374d-444d-8382-923addb60c22 |  | checkpoint | Measure cable runs with appropriate accurate measuring instrument eg tape measure, wheel, rope in conduit
checkpoint-status | 69f22425-4b1f-433e-a7cd-0de1d7e7a48b |  | checkpoint | Confirm length of cable
checkpoint-status | 58f63b69-dd4a-425a-bce6-2f37b7ff8430 |  | checkpoint | Install cable in applicable method
label | f4a7d42e-9f60-554f-867d-a67b5a3b7f5b |  | note | Eg. cable stands, electric winch, pulleys etc. any cable not terminated immediately must have the ends taped covering the bare copper. Trefoil (refer to details on back for all options) cables and tie cables to support system
checkpoint-status | 528ba8ff-3a9e-43ea-acb6-e5029f6e7a16 |  | checkpoint | Check requirements for cable identification and install