## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 37e21f7f-abe3-4fd2-9820-d190051b2379 |  | checklist | ITP No. 20 Decommission Temporary Power Board |  |  |  |  | Yes | ITP No. 20 Decommission Temporary Power Board | 0aa18cee-d4b5-4db2-9175-2fcbad36807a
checkpoint-status | 25bb6358-df6c-4c94-8ac4-d3937ed311af |  | checkpoint | Determine what the temporary board is controlling and confirm what action is required before board can be decommissioned.
label | 29f113f5-8609-5bfe-b7ab-9f2acab04e1a |  | note | De-commission form issued to builder, 48 hours notice to be given
checkpoint-status | fd3c9754-9976-4f20-b21b-cf252b9f176a |  | checkpoint | Sign off builders checklist
checkpoint-status | ac7a6128-bff6-4627-ada9-a6a2c2709b69 |  | checkpoint | Safety Committee Inspection
checkpoint-status | c53e17ec-d030-4292-b540-cd7bd732b5e0 |  | checkpoint | Final approval to be given by builder
checkpoint-status | 21315de9-1d05-49c3-a1ee-20777cf91ce3 |  | checkpoint | Perform voltage test to ensure power supply has been isolated
checkpoint-status | 671b4b35-b40a-487f-8403-6776053dfdf8 |  | checkpoint | Disconnect supply cables
checkpoint-status | 29693a9a-a1a7-44b0-988f-6f28c4a9428c |  | checkpoint | Fire sealing of penetrations
checkpoint-status | 8834bb93-ace2-406d-968d-0b7c36e4c31c |  | checkpoint | Remove temporary board
checkpoint-status | 1b02d1ba-1670-42f6-a553-656da75deec7 |  | checkpoint | Update temporary power board register
checklist-flat | 4539f3da-3fe6-4744-8a34-a9a73e9d4aa7 |  | checklist | ITR No.02 Cutout of Ceilings & Walls |  |  |  |  | Yes | ITR No.02 Cutout of Ceilings & Walls | 0c048490-e1e3-4595-bf05-c2a3ce34e906
checkpoint-status | 5085e037-b8ec-4d98-bbbe-677dd744c3a6 |  | checkpoint | Confirm sizes off all fittings prior to cut out
checkpoint-status | c9c34840-e48b-4d39-b7db-e3c110d4194e |  | checkpoint | Cut out for all sensors, EX/EMG, light fittings
checkpoint-status | e89c29c4-734d-4f56-be17-b4b88046c9dc |  | checkpoint | Cut out smoke detectors
checkpoint-status | a011c509-c9bc-4ea0-bbd2-59040a09242a |  | checkpoint | Cut out kitchen to kitchen plan
checkpoint-status | 42ff713f-3b11-4647-b9dd-31f7be6e1fa9 |  | checkpoint | Cut out switches, GPO's & Comms Riser GPO’s
checkpoint-status | be977085-cf99-4320-a84c-b02215a792ab |  | checkpoint | Cut out Bathroom and Study Led Strips Fig 8
checkpoint-status | 6fd57cf3-1735-40e3-9fa7-80ddfa77dad5 |  | checkpoint | Cut out any CCTV cameras
checkpoint-status | b6687fcc-3e0a-4063-acaa-4002cffc27e0 |  | checkpoint | Ensure AC isolator is in correct position
checkpoint-status | 228afa8c-abcd-4f84-85d1-826eec46d4a1 |  | checkpoint | Ensure Wall light is in correct position
checkpoint-status | b706b45d-2e6a-42be-a99d-44f7e602eb15 |  | checkpoint | Ensure kitchen outlets are in correct position (where applicable)
checkpoint-status | f63b1cb0-1c54-4c7e-a06e-cf076e118fe5 |  | checkpoint | Ensure Electric Strike cable is inside the pressed metal frame cut out
checkpoint-status | df7e6f39-e1e4-4d07-b872-ff4fa9f5a1c3 |  | checkpoint | Locate all cables ( including Smoke Detectors & Pendants )
checkpoint-status | 760b66cc-5b02-49d0-9b13-336df95f6fa2 |  | checkpoint | Install Fire Boxes and hit all 4 tabs in
checkpoint-status | 61abd6bc-d4d9-4c7b-b479-6fe283597db3 |  | checkpoint | Fire caulk kitchen cables ( if applicable )
checklist-flat | 66d98cc3-08df-4b28-8de7-6a6a524ff57f |  | checklist | ITP No. 08 STRUCTURED CABLING FIT OFF |  |  |  |  | Yes | ITP No. 08 STRUCTURED CABLING FIT OFF | 0fef2c9d-ce2f-4976-916e-30b0b81565bf
checkpoint-status | cc7e60f9-aab7-4fb3-b6e1-6fa09027041a |  | checkpoint | VISUAL CHECK ENSURING CABLE TO BE FITTED OFF IN CORRECT POSITION.
checkpoint-status | 02303266-97a1-4939-88ae-26814b5cd2e0 |  | checkpoint | SELECTION OF CORRECT TOOL TO BE USED FOR TERMINATION TYPE.
checkpoint-status | e3e9d8d0-619f-444b-bc94-78e9d3cc7c84 |  | checkpoint | ENSURE CABLES ARE STRIPPED NO MORE THAN THE SPECIFIED DISTANCE. CHECK TERMINATIONS AT COMPLETION FOR COLOUR CODE AND SEQUENCE.
checkpoint-status | a89b397c-4103-4787-a800-18c449c0e90a |  | checkpoint | ATTACH WRAP AROUND LABEL TO CABLE NO MORE THAN 60MM FROM THE JACK. ENSURING CORRECT NUMBER SEQUENCE.
checkpoint-status | b07367c7-fd0d-427f-87db-e519c7f8e239 |  | checkpoint | DRESS CABLES TO FINAL LOCATION. ENSURE VELCRO STRAPS FOR CAT 6 CABLING
checkpoint-status | eb35c837-b2fd-41d4-a731-88b09ccc8e33 |  | checkpoint | INSTALL JACK INTO WORKSTATION OR WALL OUTLET.
checkpoint-status | b5aa6953-461b-449c-8ecd-3cb49fabfc3d |  | checkpoint | INSTALL PATCH PANEL INTO CABINET LOOM CABLES TO THE BACK OF THE PATCH PANEL. TIE INTO POSITION USING VELCRO STRIP AND/OR CABLE TIES SUPPLIED.
checkpoint-status | efba7eb4-774d-4a49-855e-0b2ebc060a6d |  | checkpoint | PATCH OUTLETS TO HARDWARE DEVICES WHERE APPLICABLE AND CHECK FOR CORRECT OPERATION.
checkpoint-status | e9f531ce-45ca-4567-8bc7-c68523cf833e |  | checkpoint | LABEL OUTLET ENSURING CORRECT NUMBER SEQUENCE
checkpoint-status | 8a7bfcd0-cc5b-42c5-974b-f30e09bdae2b |  | checkpoint | COMPLETE CERTIFICATION AS REQUIRED
checklist-flat | 688c875f-88f5-458a-b0b6-60f0e48e83fb |  | checklist | ITR 33C. Installing Underground Services (Comms) |  |  |  |  | Yes | ITR 33C. Installing Underground Services (Comms) | 1fab3ee9-e008-4613-9c50-648635dafadf
checkpoint-status | f470b6d7-5835-4ec1-894c-3afd531a3759 |  | checkpoint | Inspect conduit material to check that it meets material specifications
checkpoint-status | 226b84b3-8796-4abf-98a6-702c50eceb13 |  | checkpoint | Check conduit alignment as per plans
checkpoint-status | b12daebf-e33c-4ff9-a557-5faf76a721d2 |  | checkpoint | Set out marked, and all services located
checkpoint-status | 65c9e210-28b6-435c-983a-40b7a646646d |  | checkpoint | Erect pedetrian barricading as per plan
checkpoint-status | 4afcda50-61fa-41ab-9629-a235167f885a |  | checkpoint | Check excavation depth against proposed road level
checkpoint-status | 4d53fcdb-1a4d-4b79-ad96-c13b67e0fdd0 |  | checkpoint | Excavate to the trench as per plan
checkpoint-status | ee9461c2-b53b-45aa-bd1c-4e2f8eeab40b |  | checkpoint | Place specified bedding material in trench
checkpoint-status | fc974b35-58da-47ec-beac-d01a89a9f491 |  | checkpoint | Placement of conduit of specified size in accordance with specifications/drawings
checkpoint-status | 1f0c03d7-2b84-4934-b5eb-6074eea1e6a6 |  | checkpoint | Backfill over conduit to 300mm
checkpoint-status | fe3b93c9-0fa3-43cf-ad72-918ad4f19f6c |  | checkpoint | Install cover slabs over conduit
checklist-flat | 50cd7b49-543a-4574-9879-6293b4a9ba8c |  | checklist | ITP No. 16 EXIT & EMERGENCY INSTALLATION & TESTING |  |  |  |  | Yes | ITP No. 16 EXIT & EMERGENCY INSTALLATION & TESTING | 25825e32-2652-4350-9e98-fd7179ed30f2
checkpoint-status | 729fc84f-5a72-42fb-954c-9b938dcce35b |  | checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
checkpoint-status | 074640cc-bf45-4f81-bd17-81655db8c2ff |  | checkpoint | COORDINATE LOCATIONS WITH OTHER SERVICES
checkpoint-status | f7e753a2-39bb-46b5-82b7-e589ae196b0c |  | checkpoint | MARKING OUT (IF REQUIRED) REFER TO DRAWINGS FOR LOCATIONS
checkpoint-status | 45a70ccd-a27a-4fd2-bbba-2b396270a9e0 |  | checkpoint | PLUG IN OR FIT OFF LIGHT, FIT OFF DATA CABLE IF REQUIRED
checkpoint-status | 02e122ed-2524-4fd4-8a3c-5bdd1bcf418f |  | checkpoint | INSTALL LAMP & DIFFUSER AND CLEAN FITTING
checkpoint-status | 0c67e657-5253-429d-8832-1ae2aee65c10 |  | checkpoint | INSTALL EMERGENCY BARCODE TO FITTING AND TO DRAWINGS (IF REQUIRED) OR,
checkpoint-status | 84fcf94d-80c9-4268-bf60-69ec48dd5f3f |  | checkpoint | NUMBER FITTINGS AS PER VAST SHOP DRAWINGS.
checkpoint-status | c2f790dc-d13d-4d06-8066-e1010351324f |  | checkpoint | UPDATE ANY CHANGES FOR AS BUILTS
checkpoint-status | 3670a237-88c5-434b-b57a-20b25b8f9e08 |  | checkpoint | COMPLETE LOG BOOK
checkpoint-status | bed8f7cf-7b39-48b2-ac70-2fade11cea3b |  | checkpoint | COMPLETE INITIAL 2 HOUR TEST
checkpoint-status | dd060118-df5f-4296-a502-6e60d3b974f0 |  | checkpoint | RECORD RESULTS
checklist-flat | dbf26a94-adb7-430c-b230-2abad86ff9c2 |  | checklist | ITR 33. Installing Underground Services (Electrical) |  |  |  |  | Yes | ITR 33. Installing Underground Services (Electrical) | 2c893a1b-c762-4da9-88bc-078639dd18bf
checkpoint-status | 24450496-2c82-487a-b0a4-c33ec51ed16c |  | checkpoint | Inspect conduit material to check that it meets material specifications
checkpoint-status | 9d4396ed-b020-487f-b38a-bd440d859b33 |  | checkpoint | Check conduit alignment as per plans
checkpoint-status | 018670cd-bcb3-4981-ae65-335fbf4c7722 |  | checkpoint | Set out marked, and all services located
checkpoint-status | 0adfed02-49cd-40bd-b003-94a6e58e4864 |  | checkpoint | Erect pedetrian barricading as per plan
checkpoint-status | 3d0326ac-e39c-43e6-96e1-2bcbefa70a4a |  | checkpoint | Check excavation depth against proposed road level
checkpoint-status | a6b0aa9b-0a94-45b1-b599-de59edcd994a |  | checkpoint | Excavate to the trench as per plan
checkpoint-status | 88f2c7a9-9d35-453e-b019-a37b06e143f8 |  | checkpoint | Place specified bedding material in trench
checkpoint-status | dccf0066-5c2c-4105-b9de-e7a6f38064e6 |  | checkpoint | Placement of conduit of specified size in accordance with specifications/drawings
checkpoint-status | f806c69c-086a-4218-83d0-3d47dfa6a860 |  | checkpoint | Backfill over conduit to 600mm
checkpoint-status | c0959b33-dcf3-4156-80b6-f241164bc7c1 |  | checkpoint | Install cover slabs over conduit
checklist-flat | 6c83396a-84de-43dd-aa48-3b457ebbb740 |  | checklist | ITR No. 34 Installing Light Pole Cages |  |  |  |  | Yes | ITR No. 34 Installing Light Pole Cages | 3356e286-9c84-4745-b545-79c11cd023f3
checkpoint-status | d0cf762a-0787-4372-8e9f-7a971cf340a0 |  | checkpoint | INSPECT CAGES FOR ANY DAMAGE PROIR TO INSTALLATION
checkpoint-status | 9fc45585-c034-4a46-aa33-a522157d3a71 |  | checkpoint | SET OUT LIGHT POLE LOCATION, ALIGNMENT AND HEIGHT AS SPECIFIED
checkpoint-status | 8f63f49a-0be1-49ce-9d32-81f16fc96f69 |  | checkpoint | ERECT PEDESTRIAN BARRICADING AS PER PLAN
checkpoint-status | 6815faf1-da86-49cd-8f6d-f9ec9a629a7c |  | checkpoint | EXCAVATE AS PER PLAN
checkpoint-status | a3a16712-c3b8-4882-b949-51de6f4e7076 |  | checkpoint | PLACE SPECIFIED BEDDING MATERIAL AS PER REQUIREMENT
checkpoint-status | 1f956054-e2c7-481c-8f5d-f5e5c8424d7e |  | checkpoint | INSTALL LIGHT POLE CAGES AND CONDUITS AS REQUIRED
checkpoint-status | d8691a1a-4b70-460e-afb0-0cf884026a3c |  | checkpoint | RE-CHECK FINSHED HEIGHT AS PER CIVIL DRAWINGS
checkpoint-status | 146c9bf7-f095-4738-b834-42b0ec8a1f06 |  | checkpoint | POUR CONCRETE FOOTING WITH SPECIFIED MPA
checkpoint-status | a267f179-d344-45f8-bf1e-5ac92cc887dd |  | checkpoint | CLEAN UP AND BARRICADE WORK AREA
checklist-flat | 40dc5d5c-413d-449d-909a-7c1704934a11 |  | checklist | ITR. 12 Switchboard Commissioning |  |  |  |  | Yes | zSYS - ITR. 12 Switchboard Commissioning (old version) | 34bdeb24-4e06-4365-bc8d-30f8838f6928
checkpoint-status | 29f36bd2-c076-451d-96bd-21acd7c5c263 |  | checkpoint | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure And All Steps Undertaken To Ensurecompliance With This Procedure
checkpoint-status | 0ab4bbda-ab99-41a2-b8e7-3db4dc7ed120 |  | checkpoint | Refer To As Installed Drawings
checkpoint-status | 4b449f06-3a36-4151-9885-980265f23f86 |  | checkpoint | Obtain Copy Of Switchboard Schedule And Schematic Drawings
checkpoint-status | ccece931-b26a-4dfc-90c6-9f3bf7ad08c9 |  | checkpoint | Mark Up Any Additions Or Deletions Found Whilst Commissioing
checkpoint-status | 621c2dc3-f1f0-4bd3-9a6a-e39766190307 |  | checkpoint | Complete Visual Checks
checkpoint-status | ac3117c2-89f8-4989-b842-0d2dbb9f9540 |  | checkpoint | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below
checkpoint-status | 3dd9cb2b-72c2-4b64-bba5-f13ced9140f5 |  | checkpoint | Complete Mandatory Tests Using Metrel Tester, Save And Log Results On Tester
checkpoint-status | 9510d5bd-6c7f-4ba3-9081-06a207f72f7c |  | checkpoint | Any Failed Results To Be Rectified Saved And Logged On Tester
checkpoint-status | afa6392c-e5bb-498b-9f19-35c601ef3cfe |  | checkpoint | Ensure Correct Opertation Of All Control/Equipment Installed In Switchboard
checkpoint-status | dd9b55f8-2ead-49ba-a7be-a60b05131d42 |  | checkpoint | Ensure Vast Witness Test Has Been Completed
checkpoint-status | e1880eff-5161-4e7e-8ddd-7f28e5d32d15 |  | checkpoint | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated
checkpoint-status | f6f11d11-8582-4c1f-b90a-72ac97e88cab |  | checkpoint | Ensure No Access To Live Parts
checkpoint-status | 38685966-3d57-4cb1-8804-dc46ca5770bc |  | checkpoint | Complete Switchboard Schedules On Vast Template, Install And Fix To Allocated Postion In Switchboard
checkpoint-status | be71ec92-39a1-4c16-ad30-79730fa69aaf |  | checkpoint | Download Test Results From Metrel Tester And Save To Project Folder
checkpoint-status | bc825402-852f-4846-8b4c-449b9803c1ae |  | checkpoint | Complete Certificate Of Electrical Safety And Save To Project Folder
checklist-flat | 6abd258a-f4dd-41bc-941e-d125b260bdf4 |  | checklist | ITR No.35 Installing Underground Pits |  |  |  |  | Yes | ITR No.35 Installing Underground Pits | 4db0a784-7ae9-4cb2-a59a-6af79d5e591f
checkpoint-status | 36870f73-4a1e-4fa2-84ac-8624ebbe96c7 |  | checkpoint | INSPECT PITS FOR ANY DAMAGE PROIR TO INSTALLATION
checkpoint-status | c6d029ca-81f9-41e3-9f49-d9264961513c |  | checkpoint | SET OUT PIT LOCATION, ALIGNMENT AND HEIGHT AS SPECIFIED
checkpoint-status | d03b96e2-374c-47c6-abfb-eed6cd79bafd |  | checkpoint | ERECT PEDESTRIAN BARRICADING AS PER PLAN
checkpoint-status | 27cc139e-1cfc-4e64-b56a-2a1176c49a2c |  | checkpoint | EXCAVATE AS PER PLAN
checkpoint-status | 7d48d9d7-477b-4909-8c73-164127ea5577 |  | checkpoint | PLACE SPECIFIED BEDDING MATERIAL AS PER REQUIREMENT
checkpoint-status | 886c8309-0076-4348-9dd2-d6064b5ce18b |  | checkpoint | INSTALL PIT AND CONDUITS AS REQUIRED
checkpoint-status | fec37b12-3249-46d4-8d0c-a2316a8826be |  | checkpoint | RE-CHECK FINSHED HEIGHT AS PER CIVIL DRAWINGS
checkpoint-status | 07d7e72c-b4a1-44d3-84cf-23fe7b1fa3fa |  | checkpoint | BACKFILL AND REINSTATE GROUND AS REQUIRED
checklist-flat | 8a055686-4059-4c8d-b837-c668e46a0aeb |  | checklist | ITR No.0 5 Rough in |  |  |  |  | Yes | ITR No.0 5 Rough in | 6b992d44-48f5-4090-90b4-1cdbe38a115c
checkpoint-status | 76ebadf1-b032-41af-89b3-2e5e4e4b6600 |  | checkpoint | Area clear, tidy and accessible
checkpoint-status | cb8c15e9-0ffb-4e52-9191-58db9070f3ac |  | checkpoint | Rough in of all lighting circuits- inc Emg/Exits and sensors
checkpoint-status | 95626124-131e-4c1a-8c9b-ae593190b5ac |  | checkpoint | Rough in of all external lights
checkpoint-status | c399a871-e157-4796-b523-d7dfebf55224 |  | checkpoint | Rough in of all power circuits
checkpoint-status | f911314d-0ccc-43a1-bb90-167c58205d76 |  | checkpoint | Rough in all lighting feeds and label on plan
checkpoint-status | 54bf311a-d793-44db-8f0a-acd3bb5218d7 |  | checkpoint | Rough in all power feeds and label on plan
checkpoint-status | 4b8c3aa6-40f4-42e3-809f-a9f7b8f1fe13 |  | checkpoint | Check for clashes with other services
checkpoint-status | 8c65a6ef-4582-40b6-bb47-6a1ab7293984 |  | checkpoint | Level fire caulked by contractor
checkpoint-status | 201c2e59-589b-4a3d-b024-caab82989f64 |  | checkpoint | Ensure area is left clean
checklist-flat | 51a387c2-4cdf-44f6-9d6c-15d39cc0674f |  | checklist | ITR No. 10 Cable Tray Installation |  |  |  |  | Yes | ITR No. 10 Cable Tray Installation | 6d3cc96b-97f7-4c03-bc0f-3e523068e0f5
checkpoint-status | 2727449d-e689-44af-9773-2b3fd08b8563 |  | checkpoint | CO-ORDINATE WITH OTHER SERVICES (CHECK FOR ANY CLASHES)
checkpoint-status | ec63411e-eec0-492d-8ed0-c524732b84d8 |  | checkpoint | CONFIRM SIZE OF CABLE TRAY
checkpoint-status | d578eaaf-9496-4e6b-b65b-5d1169c6c80d |  | checkpoint | INSTALL FIXINGS AND SUPPORTS AS NEEDED
checkpoint-status | 0b4862b0-4edd-41c4-a3ef-2ea5a7ef0713 |  | checkpoint | INSTALL CABLE TRAY
checkpoint-status | de953d19-add8-458a-92ce-b89e93e7af5f |  | checkpoint | COMPLETE SKETCH/MARK UP DRAWING FOR FUTURE AS BUILTS
checklist-flat | b787ca09-9d8d-406d-9b68-b8e85097d331 |  | checklist | ITR No. 18 Light and Power Fit Off |  |  |  |  | Yes | ITR No. 18 Light and Power Fit Off | 7488546e-1a58-4515-8e67-255d860ee3df
checkpoint-no-status | fb9494ba-b0bb-4f0a-aa1e-770d1825a1ff |  | checkpoint | Bakelite & Power
label | fe6c9fc7-e97a-531c-af75-33a6d5cd320b |  | note | Bakelite & Power
checkpoint-status | 7cd537f6-2dfc-4951-b917-c2189cee68f9 |  | checkpoint | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
checkpoint-status | 3827d337-db9a-4eca-9352-a6c88c9ab3c4 |  | checkpoint | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS,
checkpoint-status | d085e76e-c219-427c-b56b-8281aab40d48 |  | checkpoint | FIT OFF AND FIX SWITCHES, WHERE MULTI GANG SWITCHES WITH MULTI CIRCUITS ARE INVOLVED USE SHROUDS ON EACH SWITCH. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
checkpoint-status | 9ac95c51-eded-4b52-9ed0-a592c15a4e8e |  | checkpoint | FIT OFF AND FIX GPO’S, WHERE A GPO IS LOCATED WITHIN 150mm OF A METAL STUD, USE SHROUD. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
checkpoint-status | fb0c4a6d-aa84-48d3-bc86-dfd2b415d204 |  | checkpoint | FIT OFF FINAL APPLIANCES
checkpoint-status | e8e39fe6-9a52-46c4-bc6b-ab1dee849cc0 |  | checkpoint | COVER PLATES (IF REQUIRED)
checkpoint-status | a23ed553-ed57-441e-94e4-7a790752cd5c |  | checkpoint | INSTALL LABEL (IF A SPECIFIED REQUIREMENT)
label | d5b31c5d-c03e-5c3c-b310-724d6c062959 |  | note | Light Fittings
checkpoint-status | f8e824bf-4ac8-4ba7-9e28-f92b700fa7b6 |  | checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
checkpoint-status | 132e9ebe-c129-47c3-b0d7-95829262a872 |  | checkpoint | LOCATIONS CO ORDINATE WITH OTHER SERVICES
checkpoint-status | db83629a-564d-4653-948a-9e21af0dbe95 |  | checkpoint | MARKING OUT IF REQUIRED - REFER TO REFLECTED CEILING PLAN FOR SET OUT
checkpoint-status | d0f819dc-3c55-483f-a14f-ac0df794c637 |  | checkpoint | PLUG IN OR FIT OFF LIGHT / PLUG BASE
checkpoint-status | efe36ff0-e526-4d2b-9d0b-1ec2fc9cba0b |  | checkpoint | INSTALL LIGHT FITTING
checkpoint-status | dc768686-f1f5-4005-bdf8-f68754fc19b9 |  | checkpoint | INSTALL LAMPS AND DIFFUSER
checkpoint-status | 69dc40c3-6dec-4854-af17-210fcd6aba06 |  | checkpoint | CLEAN FITTING, LAMP DIFFUSER
checklist-flat | 05e04520-f25b-43c0-9a46-bcb29aa12906 |  | checklist | ITR No. 16 Switchboard Installation and Terminate Submains |  |  |  |  | Yes | ITR No. 16 Switchboard Installation and Terminate Submains | 86240f1f-0500-417a-9b60-f8945936bd0d
checkpoint-status | e98744ee-cb2f-4858-a29f-8c5e883995f6 |  | checkpoint | DELIVERY CHECK FOR DAMAGE, PAINT FINISH, DIMENSIONS AND DOORS AGAINST APPROVED SHOP DRAWING
checkpoint-status | 61a449d6-6829-4fc6-b440-2755004a35c8 |  | checkpoint | LOCATE & FIX INTO POSITION
checkpoint-status | b3607d89-d454-4b91-96f4-d3e94b24f59d |  | checkpoint | INSTALL SUBMAINS CABLING AS APPROPRIATE EG. GLANDS, TRAY, DUCT
checkpoint-status | fbd0de90-98ff-40ec-ad71-fea6f9073a87 |  | checkpoint | INSTALL LUGS AND TERMINATE
checkpoint-status | 5174255e-92ac-4f38-a07d-f300072ed9e4 |  | checkpoint | ANY CABLES NOT TERMINATED PRIOR TO ENERGISATION MUST BE REMOVED FROM CUBICLE AT ORIGIN AND HAVE ENDS COVERED IN HEATSHRINK. AT DESTINATION CABLES MUST BE COVERED IN HEATSHRINK AND BE CONTAINED IN A JUNCTION BOX
checkpoint-status | d4b35702-f33e-4a51-becc-9c5c89f832c4 |  | checkpoint | CLEAN & VACUUM
checkpoint-status | 4b1f2d8a-51f1-4bae-ada0-97c0ccc6b36b |  | checkpoint | ORGANISE INPECTION BY INSPECTOR. LODGE PRESCRIBED / NON PRESCRIBED (AS APPLICABLE) CERTIFICATE OF ELECTRICAL SAFETY (IF REQUIRED).
checkpoint-status | df1a61d7-af50-477b-a661-5b36f8d893c0 |  | checkpoint | CLEARLY IDENTIFY SERVICES
checkpoint-status | 45722e34-ede7-4cca-a5b6-1b9dd888f1aa |  | checkpoint | WHEN READY TO ENERGISE PROCEED IN ACCORDANCE WITH ENERGISATION PROCEDURE
checkpoint-status | 06ac1182-2d0b-4243-8dd9-795d49c29e04 |  | checkpoint | ENERGIZE & RECORD RESULTS
checkpoint-status | cce6527d-00c1-460f-8cf4-da88e5ab687a |  | checkpoint | CHECK SWITCHBOARD AS INSTALLED MATCHES SHOP DRAWING. IF NECCESARY MODIFY SHOP DRAWING TO MATCH INSTALLED & RETURN TO OFFICE
checkpoint-status | 3638f9ae-7e72-4cd6-a4fa-e8fb0461e9cd |  | checkpoint | CLEAN SWITCHBOARD CUPBOARD
checkpoint-status | b806f52e-080b-4621-93e0-606c836691b4 |  | checkpoint | INSTALL SUB CIRCUIT CABLING IN ACCORDANCE WITH DB SCHEDULE AND TERMINATE. if circuit not complete at the other end, it must not be terminated BUT PLACED IN A JUNCTION BOX AT FIELD END AND IN CONNECTORS AT dISTRIBUTION BOARD END.
checkpoint-status | 76f77065-6abf-4fe2-af39-f8bb5bb6a067 |  | checkpoint | CLEAN & VACUUM
checkpoint-status | 91237bbe-04f6-4b3e-a97a-5fce78ae5a0a |  | checkpoint | RECORD RELEVANT INFORMATION AND ANY CHANGES ON DB SCHEDULE. AND RETURN TO ADMINISTRATOR/OFFICE FOR COMMISSIONING TEAM
checklist-flat | 3819e2da-6a05-4c08-8aea-2d6662eec9d6 |  | checklist | ITP No. 14 Installation of Temp Lights/Power |  |  |  |  | Yes | ITP No. 14 Installation of Temp Lights/Power | 91781e4b-fcd7-4981-9432-7b9fcae4ded3
checkpoint-status | f213f109-ae78-4ef9-bddd-9a78189d3a16 |  | checkpoint | Area accessible & ready
checkpoint-status | 379ddd11-3c9e-40bf-9f69-a009a5248f8d |  | checkpoint | Rough in cable
checkpoint-status | fe6238f2-f972-4c76-8e59-ea7772d9f16f |  | checkpoint | CABLING MUST BE SUPPORTED AND PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES. TEMPORARY WIRING MUST NOT BE INSTALLED WITH PERMANENT CABLING
checkpoint-status | ccf1cca5-5d4e-4e5e-93cf-67f6d541744b |  | checkpoint | Fit off plug base and or powerpoint/isolator
checkpoint-status | b8a84307-a413-4960-9e63-a31b2af3a9e6 |  | checkpoint | Install light fitting, exit/emg, power
checkpoint-status | 2b89732e-7e8d-4d31-98ee-4e27043178f0 |  | checkpoint | Terminate cable to temp board. Ensure temp board is isolated! Test Test Test
checkpoint-status | d532dbbb-4599-4cc8-b85b-50723c4e5240 |  | checkpoint | Test & commission
label | ce613ef3-a1c8-5b32-8e37-89e9f9e77030 |  | note | Lodge non prescribed certificate of electrical safety
checklist-flat | 1f181f23-39ac-4799-b239-2a8c56fe2a2e |  | checklist | ITR No.7 - Ground Fit Off |  |  |  |  | Yes | ITR No.7 - Ground Fit Off | 9fce358e-ffc1-4d70-9e59-972716928c86
checkpoint-status | 7af2fc57-02c0-4c4d-99db-2d670f18ccac |  | checkpoint | Area clear, tidy and accessible
checkpoint-status | 8ec73238-fb5f-4717-9452-498d28ab4dd2 |  | checkpoint | Ensure danger tags have up to date contact & isolation details
checkpoint-status | 283753cb-75d8-42c0-a316-b24ac049b730 |  | checkpoint | LOCK OFF & TAG circuits that require isolation (Ensure key is with supervisor)
checkpoint-status | 873dedb4-3303-4d2e-8023-526cff9cc0a7 |  | checkpoint | Test circuits to ensure they are isolated
checkpoint-status | 5042947d-ce0d-4fba-9baa-e42039516851 |  | checkpoint | Area clear, tidy and accessible
checkpoint-status | 40abc9b9-6228-4177-b7f1-3ecf1e39fd33 |  | checkpoint | Fit off all Lights
checkpoint-status | eb2e5aef-c9ab-4139-bb69-7ebdf118cdd0 |  | checkpoint | Fit off of 4 pin plug
checkpoint-status | ac52cb90-47cf-4d1e-98a1-31c4de4e07fb |  | checkpoint | Fit off all Sensors and SET TIME TO MINIMUM
checkpoint-status | 7e1e15ab-b18d-4b20-ae8b-8a51cace68fe |  | checkpoint | Fit off all EX/EMG’s
checkpoint-status | 7343d2d7-df28-4b16-bf20-4b9eae9a35d4 |  | checkpoint | Label all EX/EMG’s as per plan number
checkpoint-status | c5a32ec9-255a-45da-a8e7-6e9d5a79bd36 |  | checkpoint | Fit off all GPOs
checkpoint-status | 09bd66b8-4623-41cc-9e8d-00ed51432a12 |  | checkpoint | Fit off of all isolators (signs, hand dryers, hws)
checkpoint-status | f6a919e3-8d5c-453b-937e-5661bd3e45a4 |  | checkpoint | Ensure all fit off has been ticked off on plans once completed
checkpoint-status | 8815b77d-6a0f-4d35-8d7b-f6f956c395c5 |  | checkpoint | Ensure area is left clean
checklist-flat | 3507c245-1665-4778-a402-7bf2e58e97b5 |  | checklist | ITR No.09 In Slab Conduits |  |  |  |  | Yes | ITR No.09 In Slab Conduits | a34d6a57-9169-4884-8a0e-0852e3689a43
checkpoint-status | f5dd8daf-a45a-4d3a-8449-b89967b23f55 |  | checkpoint | Determine origin and destination
checkpoint-status | a5b8d150-c694-4119-8f92-ba46794eb711 |  | checkpoint | Check clear of other services, penetrations etc
checkpoint-status | 0c4f8aa7-a92c-4f6f-a2f1-2b764076cfa3 |  | checkpoint | Check cable size to verify conduit size
checkpoint-status | d257e0da-15b3-4afb-b429-5888f8b0a007 |  | checkpoint | Check if expansion joints are required
checkpoint-status | 56b77f14-1afc-48b3-9646-55c3a8fdf2b9 |  | checkpoint | Mark out positions of junction boxes and penerations whee necessary
checkpoint-status | 2f4173d8-141a-4e0d-88ed-179e508dddb7 |  | checkpoint | Install bar chairs where necessary
checkpoint-status | a6fba480-93fc-4661-ac81-024cbc01c889 |  | checkpoint | Install junction boxes and penetrations where necessary
checkpoint-status | 4242636e-158c-4699-b2d9-f82deef13c78 |  | checkpoint | Install junction boxes and conduits glue
checkpoint-status | 6d54cf1d-d4d0-41c3-bca7-ca7221833b4d |  | checkpoint | Tie conduits securely at all joints and midpoints
checkpoint-status | 34cc5118-a6cd-437a-bd35-4dc46bfbff72 |  | checkpoint | Ensure all conduits are 50mm above deck
checkpoint-status | b90edefa-3f34-4ce4-93e7-033226fa3cfb |  | checkpoint | Mark up drawing of conduit runs (if required)
checkpoint-status | b8ce1812-8f7a-4925-a59b-ed502203e109 |  | checkpoint | Observe conduits when concrete is being poured
checklist-flat | c2d35ba2-b669-430b-858b-8852e2f3659b |  | checklist | ITP No. 29 Installion of Electrical & Communication Pits |  |  |  |  | Yes | ITP No. 29 Installion of Electrical & Communication Pits | a8abdc53-daf9-4f01-a9b8-4f2f6aa93e23
checkpoint-status | d6940d0e-bfc4-41a0-a071-ea5ae5ed845e |  | checkpoint | Inspect pits for any damage on arrival to site
checkpoint-status | 52e8832a-2db6-4771-99c8-392a2de609bf |  | checkpoint | Mark out pit locations and alignment/arrangement
checkpoint-status | 8d72550b-954d-4e45-aebb-106587b26f91 |  | checkpoint | Check finished heights of pits against civil drawings/finished floor height
checkpoint-status | 1c70a796-9a5e-4d33-830a-43f45b4a56e6 |  | checkpoint | Erect pedestrian barricading
checkpoint-status | b7d149a2-6a38-4a18-8379-ff8438052e98 |  | checkpoint | Excavate ground around pits as required
checkpoint-status | 6b01ecac-7fa9-4f4d-b960-50cf6239b372 |  | checkpoint | Place bedding material as per pit installation requirements
checkpoint-status | 4cc6f182-a363-4ad5-b01e-7c2171272232 |  | checkpoint | Cut out pit entry as required
checkpoint-status | d7d3f892-4b71-4d25-8280-00208550b1a4 |  | checkpoint | Install puts in ground (using correct lifting equipment)
checkpoint-status | dad42097-4117-4ffe-b84a-4396dc31b1cd |  | checkpoint | Check finished heights of pits against civil drawings
checkpoint-status | e7916efc-423d-4edb-b282-eea51607f7b6 |  | checkpoint | Install relevant conduits
checkpoint-status | d783a261-ee91-4840-9be1-23c9b7db643f |  | checkpoint | Backfill and reinstatement of ground
checkpoint-status | 4cefe332-13a8-4d53-82e0-2ef7a02b725a |  | checkpoint | Check stabilised FCR backfill 200mm below proposed road level, compacted FCR above that
checklist-flat | 4bd4bd86-01e2-465f-917d-c6a76537db8b |  | checklist | ITP No. 19 Installation of Temporary Power Board |  |  |  |  | Yes | ITP No. 19 Installation of Temporary Power Board | b019ae96-0c77-47ba-a28f-55a896452ec9
checkpoint-status | 26c0abcd-30f9-4543-abdc-e5660fca9778 |  | checkpoint | Area accessible & ready
checkpoint-status | 0450cf7b-caee-45bd-bba7-9d80aef1b8b8 |  | checkpoint | Locate & fix into position, bolt temporary board down with at least 2 fixings
checkpoint-status | b9a9ee93-f0cb-4184-a6ae-0e7541fc91ba |  | checkpoint | Install submains cabling as appropriate eg: glands/tray/duct
checkpoint-status | 4213bd92-cad6-49f9-9ace-33db771244af |  | checkpoint | Install lugs and terminate
checkpoint-status | 203e0989-5598-4294-967d-424c52b37e4c |  | checkpoint | Any cables not terminated prior to energisation must be removed from cubicle at origin and have ends covered in heat shrink. At destination cables must be covered in heat shrink and be contrained in a junction box
checkpoint-status | 0b984fe0-d863-4e5a-a6c4-4d35fa7ae26b |  | checkpoint | Clearly identify services
checkpoint-status | fc7fac08-79e9-4532-9cdb-074b3d66f1c7 |  | checkpoint | When ready to energise proceed in accordance with energisation procedure
checkpoint-status | b60700d4-2277-46a8-b216-10cdb2a4fb68 |  | checkpoint | Energise & record results on Vast RCD test sheet
checkpoint-status | e111d2d2-de87-48e7-886e-d3ba6001948c |  | checkpoint | Install A3 laminated sign on face of temp board with floor plan and where the board is fed from
checkpoint-status | 17e906e8-1098-49c4-86ed-67bc97865aa0 |  | checkpoint | Update Temporary Power Board register & save to project folder/design control/temp const.
label | f205c3cb-094a-5bcf-abd7-3973d82ed7ce |  | note | Lodge non prescribed certificate of electrical safety
label | 869ba2b8-352d-55cf-bce9-09c110e94a43 |  | note | RCBO'S must be fully tested initially and then tested every month with results recorded and c/b’s labelled
checklist-flat | 2f9fecf5-9e8a-4cc1-b7c4-79c68eea7781 |  | checklist | ITP No. 13 SUB-CIRCUIT CABLING FIT OFF |  |  |  |  | Yes | ITP No. 13 SUB-CIRCUIT CABLING FIT OFF | b2bcece5-f280-4827-b61d-1c1061283096
checkpoint-status | 37d73cdc-7840-4a81-8911-f8d832441b78 |  | checkpoint | COMPLETE WALL OR CEILING CUT OUT WHERE REQUIRED
checkpoint-status | 58edf2a4-59d1-4548-b79f-09f01aba5735 |  | checkpoint | TEST & ENSURE SUB CIRCUIT CABLING IS NOT LIVE PRIOR TO FIT OFF
checkpoint-status | 87d4ed08-70db-42f8-8ddf-0f63966621e1 |  | checkpoint | TERMINATE CABLE TO OUTLET OR PLUG BASE, CHECK CORRECT CONNECTIONS AND FIX TO SURFACE, IF CIRCUIT CAN NOT BE FULLY TERMINATED A JUNCTION BOX MUST BE INSTALLED WHERE REQUIRED
checkpoint-status | e2c428bf-a243-47ba-bfbb-65a1a8b1e294 |  | checkpoint | CLEAN AREA AS REQUIRED
checkpoint-status | f0d92385-65f6-46d9-bf47-47e3d33d1f37 |  | checkpoint | RECORD ANY RELEVANT INFORMATION ON DRAWINGS.
checklist-flat | b46f978b-7a7a-4b54-83c1-8c4e71d5a15d |  | checklist | ITR No.09 Basement In Slab Conduits |  |  |  |  | Yes | ITR No.09 Basement In Slab Conduits | b762ae8d-0fe3-4eb5-92c9-124fe6ae65b2
checkpoint-status | 97fdabb1-1e9f-479c-8beb-a87a867121a1 |  | checkpoint | Determine origin and destination
checkpoint-status | c35bb759-f81e-4be6-b869-92e665b1c22b |  | checkpoint | Check clear of other services, penetrations etc
checkpoint-status | a025710a-deae-4297-ae5b-bc396f2194ff |  | checkpoint | Check cable size to verify conduit size
checkpoint-status | cc212ad8-c136-4fad-9775-3aed197131a4 |  | checkpoint | Check if expansion joints are required
checkpoint-status | 96d60e5e-6d53-4f18-a2eb-078d1096f5bc |  | checkpoint | Mark out positions of junction boxes and penerations whee necessary
checkpoint-status | 449011e9-bf9f-4a3b-a394-3db008532bb1 |  | checkpoint | Install bar chairs where necessary
checkpoint-status | 737c6a9c-40c0-4c2b-a28d-c96533114f05 |  | checkpoint | Install junction boxes and penetrations where necessary
checkpoint-status | 67c6b3c3-7d8a-4f28-814b-9f27dd792839 |  | checkpoint | Install junction boxes and conduits glue
checkpoint-status | 1d3885df-b737-451c-aef9-2be04c2ec3cc |  | checkpoint | Tie conduits securely at all joints and midpoints
checkpoint-status | f9c4b7ce-0ba6-41f6-a244-ed6c5bff1f03 |  | checkpoint | Ensure all conduits are 50mm above deck
checkpoint-status | a3a25f86-d0a6-4794-8174-bee6d5222acc |  | checkpoint | Mark up drawing of conduit runs (if required)
checkpoint-status | 952d364e-a869-4138-a95b-07f74e9e6224 |  | checkpoint | Observe conduits when concrete is being poured
checklist-flat | 2eb00af9-a7bc-4d5c-9e26-f9565ab8241a |  | checklist | ITP No.07 Structured Cabling Rough In |  |  |  |  | Yes | ITP No.07 Structured Cabling Rough In | dd9c1245-b086-4c27-a148-4ec7a9f19d65
checkpoint-no-status | c87d7f7f-d832-4287-93d8-b2d39e16dd56 |  | checkpoint | REFER APPROVED DRAWINGS AND SPECIFICATION.
label | 47d0d114-9c0a-5857-bdc9-f95031beda02 |  | note | REFER APPROVED DRAWINGS AND SPECIFICATION.
checkpoint-status | 709dfad3-8745-4bc0-a49b-ff4cbb82de05 |  | checkpoint | INSTALL CABLE SUPPORT OR CONDUIT WHERE REQUIRED.
checkpoint-status | 67dee5c1-eaf4-4433-a39d-a8bf83f7c12f |  | checkpoint | VERIFY CORRECT CABLE TYPE.
checkpoint-status | e50d1680-d817-436a-a7e1-49d334f44bc4 |  | checkpoint | REFER TO APPROVED DRAWINGS FOR CABLE NUMBERING SEQUENCE RELEVANT TO FINAL FIT OFF SEQUENCE & RECORD
checkpoint-status | 56bf889d-a248-4537-85ee-52f0a1a38a60 |  | checkpoint | INSTALL CABLE WITHIN OR ON CABLE SUPPORT SYSTEMS MAINTAINING MIN SEGREGATIONS, ENSURE VELCRO CABLE TIES ARE USED AS PER SPECIFICATION
checkpoint-status | 73cbf865-dc4c-414f-91c3-fe9b711bcf87 |  | checkpoint | FORM CABLES INTO RELEVANT FIT-OFF GROUPS AT THE CABINET END.
checklist-flat | c32609e7-c13c-4ca8-a004-e53225f492ef |  | checklist | ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM |  |  |  |  | Yes | ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM | fabc814e-dcd6-4cf9-aedd-bb84ab6c5e89
checkpoint-status | 555d30cd-ef21-44e8-a6df-0de5e549f3b8 |  | checkpoint | REFER TO INSTALLED DRAWINGS
checkpoint-status | 112d2124-62e5-43ec-a68f-77a945c6d7a8 |  | checkpoint | test terminations using COPPER STRUCTURED CABLING tester AND LOG RESULTS
checkpoint-status | ce989294-bb61-4e0a-bd00-0686fd9a5082 |  | checkpoint | RECTIFY ANY FAILED RESULTS, RE-TEST AND LOG
checkpoint-status | 1fd29e78-5171-4cba-8ad1-3d06aebd8e67 |  | checkpoint | LABEL FRAMES AND PATCH PANELS
checkpoint-status | 3ca3c526-ffa3-4f3f-aa4f-da323409e281 |  | checkpoint | COMPLETE PATCH PANEL SCHEDULE
checkpoint-status | d043a3d1-c4c3-4488-8c2e-89e090165691 |  | checkpoint | DOWNLOAD RESULTS FROM TESTER TO PROJECT FOLDER
checklist-flat | b04880a7-f757-4c39-889f-b4353da8fed2 |  | checklist | ITR No.14 Mains and Sub Mains |  |  |  |  | Yes | ITR No.14 Mains and Sub Mains | fcf26e27-5f05-4242-b5f3-279a6b6a6247
checkpoint-status | 6c7109e2-e4d8-4de7-8754-d26116a20d6a |  | checkpoint | Measure cable runs with appropriate accurate measuring instrument eg: tape measure, wheel, rope in conduit
checkpoint-status | 006cd61d-a25f-4f2c-ab7a-f82e2709bc33 |  | checkpoint | Confirm length of cable
checkpoint-status | 71ebe4a3-8296-449d-9148-9558a6cd2e0e |  | checkpoint | Install cable in applicable method eg: cable stands, electric winch, pulleys etc
label | 58051238-96cb-5b9d-bfce-baa170f8b08c |  | note | Any cable not terminated immediately must have the end taped covering the bare copper
checkpoint-status | 7e8266ab-d48d-4e4c-ad03-c72d0862712f |  | checkpoint | Trefoil (refer to details on back for all options) cables and tie cables to support system
checkpoint-status | e5af50c3-eae7-42c0-b6bc-3047db2f8fb0 |  | checkpoint | Check cable requirements for cable identification and install
checklist-flat | 84394b94-5389-41e0-a27e-a6568ac90ecd |  | checklist | ITP No. 14 Construction Wiring, Installation, Test and Tag & Removal |  |  |  |  | Yes | ITP No. 14 Construction Wiring, Installation, Test and Tag & Removal | ff94897f-5cb9-44b2-bff9-8d4652282c59
checkpoint-status | 79b37745-3e8d-40f1-80ad-9d61555f2c91 |  | checkpoint | Area accessible & ready
checkpoint-status | 7acddf75-a5b2-465a-b21f-3d9be3c168bb |  | checkpoint | Refer to temporary wiring setout plan
label | 4a1b425a-bc13-5698-bf40-2feff15d3df7 |  | note | CABLING MUST BE SUPPORTED AND PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES. TEMPORARY WIRING MUST NOT BE INSTALLED WITH PERMANENT CABLING
checkpoint-status | 6be5118f-0cbb-4857-952f-c415bcc7f58b |  | checkpoint | Fit off plug base and or powerpoint/isolator
checkpoint-status | 3fd01dcf-a532-474a-b1d7-17296b810823 |  | checkpoint | Install light fitting, exit/emg, power
checkpoint-status | 778385b3-0cc0-41f2-b01c-675f9d10b81d |  | checkpoint | Terminate cable to temp board. Ensure temp board is isolated! Test Test Test
checkpoint-status | 73b590a1-7a18-4c75-afba-7664c690e026 |  | checkpoint | Test & commission
label | 0f0f8f9f-54e7-5219-8fbb-f82e9079e761 |  | note | Lodge non prescribed certificate of electrical safety