## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Main Switchboards | [5 empty] | Testing & Commissioning - Main Switchboards
section | WSA20-MPX-04000-EL-ITC-31032000 - Construction Tests (Pre-energisation)
checkpoint | Physical Checks
button | 1. Confirm boards dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section) | PASS,FAIL,N/A
button | 2. Confirm correct MSB Form of Separation, Provide actual Form of Separation in Comments section | PASS,FAIL,N/A
button | 3. Confirm the Layout of fitted components (ACBs, MCCBs, MEN, ATS) is in accordance with approved shop drawings (provide drawings reference in the Comments section) | PASS,FAIL,N/A
button | 4. Confirm that Brand of fitted components is in accordance with approved shop drawings (provide drawings reference in the Comments section) | PASS,FAIL,N/A
button | 5. Confirm meters location, types and labels are in accordance with approved shop drawings | PASS,FAIL,N/A
button | 6. Confirm the circuit breakers rating is in accordance with discrimination study (provide discrimination study reference in the Comments section) | PASS,FAIL,N/A
button | 7. Confirm Trip units and protection relay settings are set in accordance with discrimination study | PASS,FAIL,N/A
button | 8. Confirm correct circuit identification and labelling | PASS,FAIL,N/A
button | 9. Confirm easy access to controls termination | PASS,FAIL,N/A
button | 10. Confirm correct location, access and sufficient support for incoming cables | PASS,FAIL,N/A
button | 11. Confirm correct location, access and sufficient support for outgoing cables | PASS,FAIL,N/A
button | 12. Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in a Comment section | PASS,FAIL,N/A
button | 13. Confirm correct phase identification of busbars and cables inside the board | PASS,FAIL,N/A
button | 14. Confirm correct size of incoming power cables as per approved cable schedule | PASS,FAIL,N/A
button | 15. Confirm correct size of earthing conductors | PASS,FAIL,N/A
button | 16. Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any) | PASS,FAIL,N/A
signoff | Checked By (Heyday):