## Project Structure (2)
The Grey |  |  |  |  | Checklists needed
| Scope of work | Sub Area
Site QA
Basement 1
|  |  | Undserslab | prepopulate | QA - Basement Underslab
|  |  | Common Waste & Stacks Checklist | prepopulate | QA - Waste / Stacks
|  |  | Main Water Reticulation | prepopulate | QA - Main Water Reticulation
|  |  | Manholes | prepopulate | QA - Manhole
Level 0
|  |  | Common Waste & Stacks | prepopulate | QA - Waste / Stacks
|  |  | Main Water Reticulation | prepopulate | QA - Main Water Reticulation
|  |  | GL01 | prepopulate | Apartment Waste QA Checklist
|  |  |  | prepopulate | Apartment 2nd Fix QA Checklist
|  |  | GL02 same as GL01 | prepopulate
|  |  | GL03 same as GL01 | prepopulate
Level 1
|  |  | Common Waste & Stacks | prepopulate | QA - Waste / Stacks
|  |  | Main Water Reticulation | prepopulate | QA - Main Water Reticulation
|  |  | 101 | prepopulate | Apartment Waste QA Checklist
|  |  |  | prepopulate | Apartment 2nd Fix QA Checklist
102 same as 101
103 same as 101
104 same as 101
105 same as 101
106 same as 101
107 same as 101
108 same as 101
Level 2
|  |  | Common Waste & Stacks | prepopulate | QA - Waste / Stacks
|  |  | Main Water Reticulation | prepopulate | QA - Main Water Reticulation
|  |  | 201 | prepopulate | Apartment Waste QA Checklist
|  |  |  | prepopulate | Apartment 2nd Fix QA Checklist
202 same as 201
203 same as 201
204 same as 201
205 same as 201
206 same as 201
207 same as 201
208 same as 201
Level 3
|  |  | Common Waste & Stacks | prepopulate | QA - Waste / Stacks
|  |  | Main Water Reticulation | prepopulate | QA - Main Water Reticulation
|  |  | 301 | prepopulate | Apartment Waste QA Checklist
|  |  |  | prepopulate | Apartment 2nd Fix QA Checklist
302 same as 301
303 same as 301
304 same as 301
305 same as 301
306 same as 301
307 same as 301
308 same as 301
Level 4
|  |  | Common Waste & Stacks | prepopulate | QA - Waste / Stacks
|  |  | Main Water Reticulation | prepopulate | QA - Main Water Reticulation
|  |  | 401 | prepopulate | Apartment Waste QA Checklist
|  |  |  | prepopulate | Apartment 2nd Fix QA Checklist
402 same as 401
403 same as 401
404 same as 401
405 same as 401
406 same as 401
Level 5
|  |  | Common Waste & Stacks | prepopulate | QA - Waste / Stacks
|  |  | Main Water Reticulation | prepopulate | QA - Main Water Reticulation
|  |  | 501 | prepopulate | Apartment Waste QA Checklist
|  |  |  | prepopulate | Apartment 2nd Fix QA Checklist
502 same as 501
Sump Pump
|  | Basement 1 | sump | prepopulate | QA - Sump Pump
|  |  | lift | prepopulate | QA - Sump Pump
Booster pump
|  | Basement 1 |  | prepopulate | QA - Cold Water Booster Pump
Testing
Basement 1
|  |  |  | prepopulate | Testing - Waste / Stacks
|  |  |  | prepopulate | Testing - Cold Water Main
|  |  |  | prepopulate | Testing - Hot Water Main
Level 0
|  |  |  | prepopulate | Testing - Waste / Stacks
|  |  |  | prepopulate | Testing - Cold Water Main
|  |  | GL01 | prepopulate | Apartment Waste Test Sheet
|  |  |  | prepopulate | Apartment Water Test Sheet
GL02 Same as GL01
GL03 Same as GL01
Level 1
|  |  |  | prepopulate | Testing - Waste / Stacks
|  |  |  | prepopulate | Testing - Cold Water Main
|  |  | 101 | prepopulate | Apartment Waste Test Sheet
|  |  |  | prepopulate | Apartment Water Test Sheet
102 same as 101
103 same as 101
104 same as 101
105 same as 101
106 same as 101
107 same as 101
108 same as 101
Level 2
|  |  |  | prepopulate | Testing - Waste / Stacks
|  |  |  | prepopulate | Testing - Cold Water Main
|  |  | 201 | prepopulate | Apartment Waste Test Sheet
|  |  |  | prepopulate | Apartment Water Test Sheet
202 same as 201
203 same as 201
204 same as 201
205 same as 201
206 same as 201
207 same as 201
208 same as 201
Level 3
|  |  |  | prepopulate | Testing - Waste / Stacks
|  |  |  | prepopulate | Testing - Cold Water Main
|  |  | 301 | prepopulate | Apartment Waste Test Sheet
|  |  |  | prepopulate | Apartment Water Test Sheet
302 same as 301
303 same as 301
304 same as 301
305 same as 301
306 same as 301
307 same as 301
308 same as 301
Level 4
|  |  |  | prepopulate | Testing - Waste / Stacks
|  |  |  | prepopulate | Testing - Cold Water Main
|  |  | 401 | prepopulate | Apartment Waste Test Sheet
|  |  |  | prepopulate | Apartment Water Test Sheet
402 same as 401
403 same as 401
404 same as 401
405 same as 401
406 same as 401
Level 5
|  |  |  | prepopulate | Testing - Waste / Stacks
|  |  |  | prepopulate | Testing - Cold Water Main
|  |  | 501 | prepopulate | Apartment Waste Test Sheet
|  |  |  | prepopulate | Apartment Water Test Sheet
502 same as 501
Sump Pump
|  | Basement 1 | sump | prepopulate | QA - Sump Pump
|  |  | lift | prepopulate | QA - Sump Pump
Booster pump
|  | Basement 1 |  | prepopulate | QA - Cold Water Booster Pump

## Pump Test Sheet
Waste Water Pump Commissioning
name | Pump Model Matches Spec
checklist | Waste Water Pump Commissioning
Checkpoint | Chain connected and secure
Checkpoint | Float Valve operating free of obstruction
checkpoint | Flow test pump
checkpoint | Visual check for leaks
checkpoint | Non return valves fitted
checkpoint | Installers name & date works completed
text | Installers name
text | Date:
checkpoint | Tested by & date
text | Tested by:
text | Date tested:
checkpoint | Council inspector sign off and date

## Apartment 2nd Fix QA Checklist
type | name
checklist | Second Fix Plumbing - Water & Waste
checkpoint | Flush all water pipes before connecting fittings
checkpoint | Correct Taps And Fittings Provided
checkpoint | Silicone Applied To Fixtures Where Required
checkpoint | Check All Tap Connectors For Leaks
checkpoint | Check Screwed Nippling In Walls For Leaks
checkpoint | Check Traps For Leaks
checkpoint | Check Cisterns For Leaks
checkpoint | Check cisterns flushing correctly
checkpoint | Check All Fixtures Function Correctly
checkpoint | Test TPR on HWC and safetray drains away & airgap
checkpoint | Check HWC For Correct Valve Installation
checkpoint | Check Restraints & Timber chooks are installed on HWC
checkpoint | Element Position on HWC Is In A Serviceable Position
checkpoint | Check FWG & Shower wastes are clean & clear
checkpoint | Check Flanges Have Been Installed Where Required
checkpoint | Check All Soll Pipe Connections Are Connected To Drain
checkpoint | Kitchen overflow working and no leaks
checkpoint | Picked Up All Left Over Material & Retumed to Office
checkpoint | All your rubbish removed or in bins provided
checkpoint | Check All Hot/Cold Pipes For Correct Position
checkpoint | Temperature set point
checkpoint | Downpipe & overflow cover installed on balcony
checkpoint | Correct screws on balcony drain
checkpoint | Installers name & date works completed
text | Installers name
text | Date:
checkpoint | Tested by & date
text | Tested by:
text | Date tested:
checkpoint | Council inspector sign off and date

## Apartment Waste Test Sheet
Checklist | Testing - Waste / Stacks
Text | Area / Stack
checkpoint | Flood Test in accordance with ASNZ 3500 (15.2)
text | Duration
text | Notes
checkpoint | Install Tests completed, reviewed & approved
checkpoint | Local Authority Inspection Passed
text | Witnessed by
Text | Representing (Company)
Signing box
text | Date

## Apartment Water Test Sheet
checklist | Apartment Water Test Sheet
checkpoint | Connections welded/crimped correctly
checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
checkpoint | Valves fitted correctly
checkpoint | Checked for crossovers
checkpoint | Lagging installed and neat
checkpoint | release TPR and CW expansion valve
checkpoint | Test overflow & safe tray
checkpoint | Set tempering valve temperature 55deg C
checkpoint | Tidy work areas
checkpoint | Pressure 1500 kpa or as per spec
text | Duration
checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
label | Attach photos of completed area
checkpoint | Pre Line Inspection Passed - Foreman
holdpoint | Add Signature
checkpoint | Pre Line Inspection Passed - Inspector
holdpoint | Add Signature

## Checklists
checklist | QA - Basement Underslab
section | Area Prestart / Acceptance & Drawings
text | Zone / Area
checkpoint | Area ready for works (grids setout, area accessible and approval to start)
checkpoint | Current Dimensioned Slab Set Out Drawings numbers and revisions recorded
section | Under Slab Pipe install
checkpoint | Correct pipe laid to specified level and grade (all joints sealed correctly as specified)
text | Zone / Area
text | Start Invert
text | Finish Invert
text | Grade of Pre-Line %
text | Product Type
checkpoint | Pipe supported
checkpoint | Install Tests completed, reviewed & approved
text | Test method used
text | Duration
checkpoint | Local Authority Inspection Passed
text | Witnessed by
holdpoint | Signoff required
text | Representing (Company)
text | Date
checkpoint | All relevant test plugs removed where applicable
checkpoint | Open ends sealed
checkpoint | General photos, comments and observations
checkpoint | Pipe Laying Completed
text | Laid by
bool | Bedding Sound
bool | Soil Removed
bool | Trench Compacted
bool | Hard Filled
section | Area Completion/Signoff
checkpoint | Specified Protection Around All feeds/pipes penetrating slab
checkpoint | All Measurements Double Checked
checkpoint | As-Built Drawings recorded (drawing & revision number(s)
checkpoint | All relevant under slab works completed, reviewed and approved
text | Completion Date
checklist | QA - Manhole
section | Manhole Install
checkpoint | Latest consented drawings
text | Drawing Ref No.
checkpoint | Setout Completed checked and accurate
checkpoint | Excavation Accurate - Location & Depth
checkpoint | Ground conditions checked & acceptable
checkpoint | Bedding depth and material correct & compacted
checkpoint | Correct manhole installed to specified height and sitting level
checkpoint | Manhole Risers Installed (if applicable)
checkpoint | Joints & connections correctly sealed as specified
checkpoint | Manhole benching completed and acceptable
checkpoint | Concrete Lid Installed and sitting appropriately
checkpoint | Cast Iron Lid Installed and sitting flush
checkpoint | Signoff on Completed Work (Council etc)
section | Backfill
checkpoint | Backfill methodology and material confirmed
checkpoint | Any formwork/ debris removed from area
checkpoint | Any waterproofing/ drainage / service requirements completed and inspected
checkpoint | Approval given to commence backfill - attach any other relevant inspections and observations closedout
checkpoint | General photos and observations during backfill
checkpoint | Backfill completed correctly and heights checked/ correct
checklist | QA - Main Water Reticulation
section | Cold Water Main
checkpoint-no-status | Zone / Area
text | Zone / Area
checkpoint | Connections welded/crimped correctly
checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
checkpoint | Lagging installed and neat
checkpoint | Labels installed
checkpoint | Correct valves fitted correctly
checkpoint | Seismic bracing completed
checkpoint | Tested
section | Hot Water Main
checkpoint-no-status | Zone / Area
text | Zone / Area
checkpoint | Connections welded/crimped correctly
checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
checkpoint | Lagging installed and neat
checkpoint | Labels installed
checkpoint | Correct valves fitted correctly
checkpoint | Seismic bracing completed
checkpoint | Tested
checklist | QA - Sump Pump
section | Unit check
checkpoint | Area acceptable and ready for work to begin
checkpoint | Pump mounted on base, & housing condition good - no leaks
checkpoint | Alignment checked (field alignment performed where required)
checkpoint | Pump impeller works correctly
section | Pipework
checkpoint | Strainer installed & cleaned
checkpoint | All isolation valves set correctly - non return valve, isolation valve
section | Electrical
checkpoint | Local isolator located
checkpoint | All power and control wiring correctly installed
checkpoint | All electrical connections correct and tight
checkpoint | Controls point to point check completed
section | Float levels
checkpoint | invert - low level alarm
checkpoint | invert - mid level for dual pump operation
checkpoint | invert - high level alarm
checkpoint | Rail / lifting chains installation
checklist | QA - Cold Water Booster Pump
section | Zone / Area
checkpoint-no-status | Details
text | Zone / Area
section | Pumpset mainfold
checkpoint | Connections welded correctly
checkpoint | Clip Spacing to manufactures specs horizontal/ vertical
checkpoint | Valves fitted correctly
checkpoint | Line strainer fitted between pump & tank
section | Pumps
checkpoint | Pump 1 Startup KPA
checkpoint | Pump 1 kick out pressure KPA
checkpoint | Pump 2 Startup KPA
checkpoint | Pump 2 kick out pressure KPA
checkpoint | Pressure vessell pressure
section | General
checkpoint | Mains water change over
checkpoint | Flow test pump
checkpoint | Pressure tests pipework
checkpoint | Visual check (for leaks form valves, tees, saddles, etc)
checkpoint | Non return valves fitted
checkpoint | Installers name & date works completed
text | Installers name
text | Date:
checkpoint | Tested by & date
text | Tested by:
text | Date tested:
checkpoint | Council inspector sign off and date
checklist-flat | Testing - Waste / Stacks
checkpoint-no-status | Details
text | Zone / Area
text | Area / Stack
checkpoint | Flood Test in accordance with ASNZ 3500 (15.2)
text | Duration
text | Notes
checkpoint | Install Tests completed, reviewed & approved
checkpoint | Local Authority Inspection Passed
text | Witnessed by
text | Representing (Company)
text | Date
checklist-flat | Testing - Cold Water Main
checkpoint-no-status | Details
text | Zone / Area
checkpoint | Pressure 1500 kpa or as per spec
text | Duration
checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
label | Attach photos of completed area
checkpoint | Pre Line Inspection Passed - Foreman
checkpoint | Pre Line Inspection Passed - Inspector
checklist-flat | Testing - Hot Water Main
checkpoint-no-status | Details
text | Zone / Area
checkpoint | Pressure 1500 kpa or as per spec
text | Duration
checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
label | Attach photos of completed area
checkpoint | Pre Line Inspection Passed - Foreman
checkpoint | Pre Line Inspection Passed - Inspector
checklist-flat | Testing - Cold Water Booster Pump
section | Installer Details
text | Installers name
text | Date:
checkpoint | Tested by & date
text | Tested by:
text | Date tested:
checkpoint | Council inspector sign off and date
checklist-flat | Testing - Sump Pump
section | Installer Details
text | Installers name
text | Date:
checkpoint | Tested by & date
text | Tested by:
text | Date tested:
checkpoint | Council inspector sign off and date