## Master List Templates
Id | Type | Name | Values | Prompting Name | Prefix | Postfix | Resource Id
38f7b193-f498-4cb4-a36f-155cc5378a88 | checklist | As-Built Drawings |  | As-Built Drawings |  |  | 07d8a3a7-a1d6-4f91-8093-b50e4663166a
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6d9a76c3-0a69-4449-b1e7-11ce6b7f2835 | checkpoint-no-value | As-Built Drawings - attach scanned documents
17517af2-db4a-45b7-8883-f495d7b7f393 | checklist | Certificate of compliance (COC) |  | Certificate of compliance (COC) |  |  | cfc3c06a-f98c-44e3-b7d0-645c7885e8ba
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
85c1dfac-a6c1-4c34-99e6-d95ecb814741 | checkpoint | Please upload Certificate of Compliance here when complete (COC)
d3d640a6-f0e5-4dbe-a426-bbdfbd9e88f1 | checklist | Entec Daily Report |  | Entec Daily Report |  |  | 127baa78-0e3e-4937-97c5-81d0d89ec8bd
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
dfe33494-f1f3-416d-b200-985468c449e7 | checkpoint | Daily Report
aa373969-8b60-5d14-ae15-1d6c7fac2904 | date | Date:
4309b494-9321-536c-9669-b5bc5278607c | textbox | Site:
2afe42e3-2bd3-57c9-b2b9-374ad261339b | textbox | Work completed:
6dcd5e0d-0473-5824-8763-de1db794e25a | textbox | Issues:
5599a652-8b14-57c2-b35e-1f30796f07f0 | textbox | Weather:
419ec26a-ceb3-50a3-9ab8-b04b2aeb95db | textbox | Labour:
22314894-b51d-5b55-b048-3270208b4497 | textbox | Plant & Equipment used:
b64aca17-4380-4800-aa48-02e9df10ac6f | signoff | Signed/Approved:
33eeb655-8fc5-4587-8848-ab5f145d0d04 | checklist | ITR-E-01 General Electrical Equipment |  | ITR-E-01 General Electrical Equipment |  |  | 8143f5ab-7daf-4361-a784-b6b6f44f35be
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d139f885-6b04-4b13-bf57-d43946c82785 | checkpoint | General Electrical Equipment
f24a6d46-064d-5007-89b6-08e5a6aa5b81 | textbox | Type of Electrical Equipment:
526a1dc9-2115-5588-901c-e088f357a407 | textbox | Make, Model, Manufacturer, Serial No. (if applicable):
a80bedce-6442-558f-8500-f31bff171804 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
851d3207-0dfb-553b-8bd5-2f03ff90f6fd | button | No mechanical damage and paintwork in good condition. | Yes,N/A
00affb01-bea6-54e3-845e-a0095ff5c0a6 | button | Installation is clean and tidy | Yes,N/A
dcd02f0c-34e6-51d0-97bb-5c8c4b93024d | button | Mounting arrangement correct | Yes,N/A
7e02d73a-f7df-5bc8-96b2-ea31007f7d98 | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
4bcd63bd-b13b-5193-ad6b-82b095c805e8 | button | External cabling is correctly installed and labelled. | Yes,N/A
ddec469b-3dcb-59c9-a0b6-27fe97260a6f | button | Check that Equipment is correctly earthed. | Yes,N/A
4125063c-912b-52fd-9dea-349915d1fdc7 | button | Check gland, plate, frame & door earth continuity | Yes,N/A
8615a7f4-0844-5b7a-823a-03af29f1e0f1 | button | All spare entries blanked off with correct plugs. | Yes,N/A
e8d1c308-0754-5074-937b-ac6399de82f4 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
ab993f4d-92d7-5c37-b373-a94bcbce4bec | button | Conforms to Specifications and Drawings. | Yes,N/A
2f16a4a4-09bc-523e-bf3f-54b4cf5f8161 | button | As-builts complete. | Yes,N/A
62ecc20d-eb0b-43c8-8df6-3b4431f83c74 | checkpoint | Electrical Checks
eb13e9e1-28e4-5083-bed2-08682b9fe200 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  |  | MegaOhms
9e017e75-cd6e-4daf-b69c-9ab86497457f | signoff | Installed by:
dce2442e-473b-45e1-b4f4-f1db22abc700 | checklist | ITR-E-02A Conduit/Ducting Below Ground |  | ITR-E-02A Conduit/Ducting Below Ground |  |  | 31303eea-7298-4b79-8e97-2061f8859659
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
baa5c3a5-81ba-47c9-8796-77769f0b1520 | checkpoint | Conduit/Ducting Installation Below Ground
a3f53098-de4a-5654-ad6d-b5cd12693d12 | button | Check equipment details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
c33f3bf6-cd6f-5bd7-a4a4-9f5378af6039 | button | Check conduit cable enclosure installation is as-per design, layout drawings and specifications. | Yes,N/A
93b967f6-04f1-5e41-8870-d010f912e4f6 | button | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed. | Yes,N/A
097b091d-a31d-512e-b3a9-581c562bc8d9 | button | Confirm that there are no obstructions, and that the installation will be accessible for maintenance. | Yes,N/A
8e8d50ff-7db6-5a9d-bd03-4576cebad1e5 | button | Check all fixings are tight and secure. | Yes,N/A
fb2ff21c-612b-55e6-b6c6-c0b7697b63b2 | button | Check bends do not exceed the maximum cable bend radius. | Yes,N/A
21a8957a-0281-594e-a72b-985b277e7c70 | button | As-builts complete. | Yes,N/A
9fd3e0da-f083-46d4-a37e-b9d8c3ae83e9 | signoff | Installed by:
c5367bd5-57ee-430c-bc37-3b44c8c48918 | checklist | ITR-E-02B Cable Supports Above Ground |  | ITR-E-02B Cable Supports Above Ground |  |  | 59ea2db1-f775-4419-97b2-e37e62b5b284
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
51b0cdf7-e7f7-4e01-a1e2-97de133014d8 | checkpoint | Cable Supports Above Ground
0ff06d0f-3927-5dec-bd26-a04d85b9fc86 | button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
7d16f92d-00ba-5dd2-bd5e-43023b4d6fe2 | button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
305f9fff-80a4-535c-9f43-ca015b0e3f58 | button | All covers fitted if applicable. | Yes,N/A
2a9a9324-f2b0-5a64-9670-d9609bc59747 | button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
9d0fe764-f105-51b9-93d5-5990a515f1b9 | button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
eb247cf2-5b63-53da-9806-24f61d632b70 | button | Splice plates, barriers, earthing system secure. | Yes,N/A
5398c8e4-0817-50d5-b80b-fa09616c94e3 | button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
1ac061ad-b2d0-5d21-8d51-306c38ca001a | button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
bec04255-7273-546e-9b5f-11f086c19b81 | button | Cables have adequate mechanical protection as and where required. | Yes,N/A
96ee41e1-e167-5c58-8cd5-5a29b8555258 | button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
ed83f13f-1928-58e2-8b76-3d21c77bdd2b | button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
63fc5170-920e-5151-8e27-50535016068b | button | Tray bonded to structure at correct locations. | Yes,N/A
bd2871b7-90a8-5bc1-b72f-4719488e3858 | button | Earth bonding continuity tested – record result: | Yes,N/A
0f0f5eea-31fa-5827-8dd3-c5498217cd68 | button | As-builts complete. | Yes,N/A
942aa3a9-43c6-4d97-a50b-7b0c47b3c202 | signoff | Installed by:
80d3958b-a705-48a5-bfe9-bb7e7bcd591d | checklist | ITR-E-02C Cable Transits |  | ITR-E-02C Cable Transits |  |  | f5660104-129e-486d-a194-84e5c19400ba
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
12d31784-91c5-44ee-b2e8-b90e9064fc94 | checkpoint | Cable Transits
b6c22cde-585b-5fb9-9677-546686ea9a96 | button | Transit frame installed as per drawings. | Yes,N/A
7f1d569b-d335-539a-a498-4c9133984e01 | button | Transit frame identification marked correctly and visible. | Yes,N/A
bb40e444-f59b-5bd1-949c-ffe285a7ed27 | button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
8a676f04-edc1-5b8b-be2a-2f6e671c9be3 | button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
604af95a-67d9-5d4d-a305-e05d4d50ca0f | button | Rated insulation installed to transit (where required.) | Yes,N/A
7a009815-5646-5afb-98b2-227cae9c1207 | button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
fb9277f2-304f-5318-ad81-608e26af3d4a | button | Cables pass through frames without strain on blocks. | Yes,N/A
7f2a61b1-0609-57c9-b87b-f95b49e48223 | button | All cables identified on both sides of transit and visible. | Yes,N/A
d03997d8-5f3f-5228-ad48-f392a02e749f | button | As-builts complete. | Yes,N/A
dbca1073-d4f6-4823-b1e8-920f19ac2a5a | signoff | Installed by:
bf33efd7-7fdc-4ee8-ad94-85572ce1fad2 | checklist | ITR-E-03 Entec - Distribution Board Installation |  | ITR-E-03 Entec - Distribution Board Installation |  |  | f86170f8-7ea0-4f2e-a5cd-714d009b2106
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
caf98d32-47eb-406b-871b-f750aef6247b | checkpoint | Distribution Board Installation
f015421c-60bb-5bab-a3e7-a2964aad1fab | button | Inspect for mechanical damage from freight and handling | Yes,N/A
487ac857-464e-5b51-86cd-3a44cd879f44 | button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
f5c5967c-021d-5d79-9dde-2d1ff4712787 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
628017af-39cc-54f5-884b-6dfdaea8e1fa | button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
bfb1e5bd-15b7-514d-b598-7becdff5382d | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
bb796a9f-d2fe-5543-a811-b2dd12d64c4b | button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
6911bbff-0edd-5ff5-86a8-da3f65526ffc | button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
00dee7bf-301b-571b-8405-702bfd85e681 | button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
d703aedf-5175-5b86-bc9e-16d4fcda3a54 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
496c9f9e-bc22-51c0-b8d9-5733598836fe | button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
d422d809-4cdd-5a52-ae02-f5cf50125a62 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
9c082b80-594f-4e90-94b2-76cf1706e8cc | checkpoint | Test Results
a9602e32-074f-5d03-82fd-e2a68033cf02 | textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  |  | MegaOhms
8642df89-b8eb-5343-8059-efb9362fc8f9 | textbox | Earth Continuity |  |  |  | Ohms
e3e39187-6914-509f-a78a-69178b590797 | textbox | Earth Bond |  |  |  | Ohms
c72bd529-ccc2-5f86-b01f-bb1e63cebd38 | textbox | Fault Loop Impedance, PSSC.
b065b3c4-4820-5d69-b5b5-922b3ee1b034 | textbox | RCD Test results (1/2x I, 1x I, 5x I)
92c9acaa-6cda-5b6a-a3db-a702d16ae3b7 | textbox | Voltage and Phase Rotation
773bb8bf-b90e-5d26-8a45-a959c17269a8 | button | As-builts complete. | Yes,N/A
7d8a6516-3026-4763-a997-c0609824d887 | signoff | Installed by:
8e6b9c6f-617e-4d4b-8c90-5d48dff979ae | checklist | ITR-E-05 - Low Voltage Cable |  | ITR-E-05 - Low Voltage Cable |  |  | 0e3649ae-f3e8-45ae-8af1-64d7f1590d41
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2f5ad445-c40c-4244-b687-84b3e699bb14 | checkpoint | Low Voltage Cable
156bbd6c-8abf-51ca-8897-b7e7d186db1d | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
bc027436-e8e4-50c5-828a-241d7e247b87 | button | Check dressing / cleating, cable undamaged | Yes,N/A
96e157b5-49aa-5fc6-be49-ce3119b8271d | button | Check cable cores correctly identified and labelled. | Yes,N/A
e4710480-8414-5c50-ab42-d48d32ebf32a | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
52aa32ef-252f-54ee-80d1-72cbddfde3aa | button | Check Armour / Screen correctly made off. | Yes,N/A
cf28a489-676c-56b3-99fb-22555742179e | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
14875044-d55f-52f4-b072-68f6446107ff | button | Glanding / Locknuts correctly installed. | Yes,N/A
add83237-0b54-56dd-8fe8-2d015520732c | textbox | Gland type - from: |  |  | Haz. Area Rating
59639503-006f-5d1d-aaf1-2a0d29dffa48 | textbox | Haz. Area Cert Details.
2b1b4665-1d0f-5c53-9112-df825491aa27 | textbox | Gland type - to: |  |  | Haz. Area Rating
ec1216fd-bca8-560f-bbb6-b77b8b53f0fb | textbox | Haz. Area Cert Details.
75052bdf-97d3-4e40-8308-f190bcdf67ea | checkpoint | Electrical Checks
27be0295-fff4-5750-b0bc-d5a9f39f63a9 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
3d2e034d-4031-4dd8-801a-6c67bc650b6a | signoff | Installed by:
c02734ea-0792-4ebd-a79a-3552c121d80f | checklist | ITR-E-06 Control Panel |  | ITR-E-06 Control Panel |  |  | a07428d2-e371-4ae0-856c-57410a3b22d5
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7dd21e7b-e18b-4e99-82f5-270cd5b72450 | checkpoint | Control Panel
e22e4e0c-85b7-52bb-927e-accff231a3bb | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
277295f9-88e3-5f43-ad90-fefd99161849 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
f2b72ebd-e39e-5bba-a3cd-2418daf6ff6a | button | Check holding down/mounting arrangement is correct. | Yes,N/A
3c15f2d9-ab55-5aa3-b892-d161bb288fb2 | button | Check for mechanical damage. | Yes,N/A
095aec2d-0071-5d3a-877a-2e3098b7c5ba | button | Check tightness of circuit connections. | Yes,N/A
0f517158-a955-5f09-bfa4-ea02380ec93d | button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
9881164c-9de5-54bc-895d-5582de684ce6 | button | Ammeter scale and current transformer correct. | Yes,N/A
ebb5cd6e-1af4-518b-85fe-7c961d587a1d | button | Check internals for cleanliness. | Yes,N/A
6e1c1811-1e48-5cef-8a04-65ab8aa36a73 | button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
5e13febe-f959-576f-9458-2edba4230f92 | button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
fae30941-0452-580e-bd1c-3f14c6787349 | button | Heaters correctly installed. | Yes,N/A
1c2c8b9b-08e5-5436-885f-9c8db97983e6 | button | Fuse rating correct. | Yes,N/A
836fe62e-6247-57c8-9b76-a803e7df8a96 | button | As-builts complete. | Yes,N/A
3f1bfa22-9a18-4658-8db5-0fc8391bc2c1 | checkpoint | Electrical Checks
5e1fcf0a-178f-5227-ae91-c04ab5049eae | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
ca4705cd-8031-4169-8dc2-f1886281bda7 | signoff | Installed by:
0eb01682-f406-4118-836a-f8b45e7a7bd3 | checklist | ITR-E-07 - Junction Box |  | ITR-E-07 - Junction Box |  |  | 0378e440-7eaa-4c8e-93db-a0670042fe00
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5e7c86f1-3cb2-4011-9302-25ab438d2627 | checkpoint | Junction Box
a2f145ed-b723-5db6-a0c1-0d1ae84eadc4 | button | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule | Yes,N/A
22165f4c-4ae2-5418-93e7-023c90d230c2 | button | Check mechanical damage | Yes,N/A
e46008e8-1369-50f2-a2ad-1754a4761815 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
9dd67505-4e59-5256-9754-5dbdbda4e0b7 | button | Earthing installed correctly and as per drawing | Yes,N/A
4dfb6921-76df-5fd9-b312-48e8be4e7cec | button | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable) | Yes,N/A
47813101-1c3c-5d6d-a1c5-04148fe67bf0 | button | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating | Yes,N/A
114a00d0-ceb3-51df-96aa-577805cfcaa3 | button | Check all Cables & Cores are correctly identified | Yes,N/A
9a039a8e-761b-5ee0-a21b-baf6e29c57b5 | button | Check internals for cleanliness | Yes,N/A
701f9bbd-30c9-527b-b504-152f22118091 | button | Check manual operation of selector switch, MCB, push button, etc | Yes,N/A
2b4ca514-e2ec-5333-a588-fe5b81a6f7ba | button | Check MCB/Fuse ratings (If applicable) | Yes,N/A
bd6e9820-818a-412b-b178-6f193e1cd3a9 | checkpoint | Tests
7829a2cf-f522-54c6-a922-02ebf3d26e44 | textbox | Record earth bar resistance to earth bond
d52a9407-b5c5-5005-94fa-294257bac855 | textbox | All other relevant tests:
403506e1-e490-5861-8454-63364b7bdf93 | button | As-builts complete. | Yes,N/A
0f784c87-e73c-4a5a-adbb-e7327f34776a | signoff | Installed by:
2854bd88-ca5c-4f31-bd00-8845bed5babb | checklist | ITR-E-08 Heat Tracing Circuit |  | ITR-E-08 Heat Tracing Circuit |  |  | f0e67114-0088-4bdd-acdc-8917bf3e1d59
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
fd3b2d7b-803c-45e5-b6e3-93297f6b4504 | checkpoint | Heat Tracing Circuit
8cf6586a-805f-5119-8a4a-21ced91da719 | button | Circuit installed, connected & identified according to design drawings. | Yes,N/A
67711521-b5dd-51bd-b5e4-19ac65099dbf | button | End caps and connection kits correctly installed. | Yes,N/A
67477c64-570a-5f14-83e7-18c21018b895 | button | All junction boxes properly supported, and all cables protected against sharp edges. | Yes,N/A
d8663b86-3943-58f2-90fb-bd5dcf83e1bc | button | Cable termination and glanding at all junction boxes correct. | Yes,N/A
3676c4c2-2f6b-5d4c-af0f-d5535a7bc157 | button | All spare entries blanked off correctly. | Yes,N/A
b1f35cff-5531-5a77-a1b2-e57c978388e2 | textbox | IR test: Phase - Earth, Phase - Neutral
639d0575-4f8a-5d2b-bde8-c8498ec1623a | button | Equipment certification meets the area classification requirements. | Yes,N/A
1bc98040-51bb-5bbb-b190-8a7f437777d1 | button | Confirm warning labels are fixed on outside of pipe lagging | Yes,N/A
f3f8f40d-17aa-5f46-857d-099bf52573c2 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
7257c0ec-837b-539a-8227-08f039c5f866 | button | As-builts complete. | Yes,N/A
a47c07cd-cac9-460a-9eee-ca49c3c1cc76 | checkpoint | Electrical tests
0eca3484-5828-5511-8882-87029f5bd5d5 | textbox | Insulation Resistance: Phase - Earth
fce475ea-571d-57d4-9ca2-1503ad84e60d | textbox | Insulation Resistance: Phase - Neutral
9a67b744-c537-496c-863a-fd3a149c2565 | signoff | Installed by:
0c454dbf-9750-4207-90dd-150c63a4a947 | checklist | ITR-E-09 Electrical Switch Rooms |  | ITR-E-09 Electrical Switch Rooms |  |  | f8422d50-b3b6-4ee6-9914-1d919c3ddc85
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
812ec408-d112-4df0-9856-8ba137cffb3e | checkpoint | Electrical Switchroom
8cc332a5-0fa5-58b3-a5e1-2f3f4f455d39 | button | Ensure all equipment is installed in accordance with layout drawings and equipment schedule. | Yes,N/A
713c36d6-2ca0-504c-bba0-b36af1d88b0f | button | Ensure all equipment is installed as per manufacturers instructions. | Yes,N/A
ad0c857c-7bfb-5727-844b-ac31f044ed4a | button | Ensure there is no visible damage to installed equipment. | Yes,N/A
7d4d7738-721c-5a0b-bab8-bd8cc8761b07 | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
3564835e-6bb2-5a67-865f-ab94d0a6baf5 | button | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified. | Yes,N/A
4aa0a1de-b88b-5bdc-bcef-83e6bcf95abe | button | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar. | Yes,N/A
8e7595d5-3eb4-5022-8ae6-349201d06695 | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
003947d8-154f-5e29-9b00-839dcc3f5379 | button | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
860c2e0f-1d7f-52ae-9bbc-6ba3522dc2e4 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
76a89181-4e17-5625-9878-ed4a603363c7 | button | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel. | Yes,N/A
d948cbb3-2bdf-5d4a-8e9b-31eab9ede572 | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
5ada87b2-3bb2-5237-a994-38e12832dd09 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
583d8273-d856-5bcf-a5ab-86a0cee181c3 | button | Equipment IP, Ex ratings correct. Check tightness for all circuit connections | Yes,N/A
f55e1351-2cb1-5589-9944-ac6d37553c3f | button | All internal cables and wiring is correctly numbered, colour coded and terminated | Yes,N/A
b5d19c4d-fc08-52e7-b244-23168e16cc60 | button | Check internals for cleanliness | Yes,N/A
ea2445f3-8345-5b8a-99f9-2af3635d5075 | button | Relays Metering and Protection ratings are correct as per design | Yes,N/A
2e705c39-8686-5bfd-9bda-1849a2d9f524 | button | As-builts complete | Yes,N/A
0e742957-1685-4137-a7ee-efe10b43c2cc | signoff | Installed by:
eb1f0dc3-6d8a-4528-b995-692460175685 | checklist | ITR-E-10 Electrical Equipment Package |  | ITR-E-10 Electrical Equipment Package |  |  | 84eca4da-0a8d-49e0-bd61-eb338c596587
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
26430df5-1930-4b7e-abe8-99c68981d086 | checkpoint | Electrical Equipment Package
10c398a2-d13b-56a8-9e69-e3c08abbb33e | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
63108cb3-aa8f-50e5-9131-480874b0dfa3 | button | Check equipment is correctly rated for the area. | Yes,N/A
992215cf-d073-5e33-b083-8512a8ea17c8 | button | Check if package is complete with all accessories. | Yes,N/A
d459e985-ea3e-5507-b722-0cbfd5978b27 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
68fee541-fa09-5337-987d-3dab075f3a8f | button | All transportation supports, stops and fastenings removed. | Yes,N/A
63a09c22-588c-5edb-8e1a-12935bfd25af | button | Package fixing down bolts/shims/washers installed and tensioned. | Yes,N/A
259b1420-2387-58b4-add7-6ac94edc9396 | button | Check package is installed on a level plane. | Yes,N/A
5583e30e-d33b-5640-8f42-cfc247ab27c8 | button | External cabling (if required) correctly installed. | Yes,N/A
a6986835-241e-5ae6-a1f8-e599517c244f | button | Internal equipment installed and all tests complete and accepted. | Yes,N/A
56d3d08b-405a-50e1-9cd9-9c3ab8bc0d6e | button | Verify package using vendor and/or project P&IDs. | Yes,N/A
feb625aa-f430-504b-b5e0-27248080fdac | button | Check that equipment is correctly earthed. | Yes,N/A
e4ad2a2c-df31-52b5-8c52-0d4d88398fa3 | button | As-Built drawings completed | Yes,N/A
2b19fbf1-cf5e-584c-8a88-a9ade6311cd0 | textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  |  | Ohm
2eebda35-7ba5-4be6-8afb-d36bea458cb1 | signoff | Installed by:
f9fe90f2-a208-4363-847f-c8b9d3cc5106 | checklist | ITR-E-11 Generator Package (LV) |  | ITR-E-11 Generator Package (LV) |  |  | 18726414-df48-417c-9086-8de7639a364e
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
61e18106-1fdd-4654-85e3-2bc9b016fccc | checkpoint | Generator Package (LV)
7ee98ff0-4c98-5682-89ee-74715b037c3f | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
6d9c42d4-b497-5a4d-8918-480b4557c99d | button | No mechanical damage and paintwork in good condition. | Yes,N/A
d562ee2c-3538-5e83-9af6-58378304ea3d | button | Check terminal boxes and glanding correct. | Yes,N/A
1abd9208-b4a0-5e3d-9ab2-3838296b0654 | button | Instruments correctly installed. | Yes,N/A
5037aee0-2ba8-5aa9-8804-5e87de4a4c88 | button | Heaters correctly installed. | Yes,N/A
3dd63d68-92a8-520f-adc0-eb2d1e649756 | button | Check unit for cleanliness. | Yes,N/A
6f825a3d-1c1b-5ad4-a0ac-112dd652cf48 | button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
1deccbd9-87ca-56a5-99a0-51177a232337 | button | External cabling correctly installed. | Yes,N/A
ac2c3c52-ec07-593e-bf72-37b000e37e69 | button | Protection of live parts adequate. | Yes,N/A
4bec6530-e3c0-5120-864a-b6d160fc3cec | button | Main terminal box complete and terminations correct torque. | Yes,N/A
2ec7c859-40f4-5743-a2bc-e02ffb20c48e | button | Ensure direction of rotation is clearly marked. | Yes,N/A
e9c5ea46-dd93-53d3-a916-c4b713d72647 | button | Check gasket and seals are not damaged. | Yes,N/A
c59200dc-e9f1-5819-9358-09796dc48350 | button | Unused cable entries are correctly sealed. | Yes,N/A
e5a795b0-f5f1-5d87-94f1-9452f5b71869 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
fbea4f4e-da96-5a3a-be21-59116eec06b4 | button | As-builts complete | Yes,N/A
c3c96b25-9cc6-4e11-8d88-d6cbcaf1ad44 | checkpoint | Electrical Checks
b5e7a400-01f4-5fc6-b581-6f332271361a | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
64d38cac-4b7f-590c-bffb-b3b48e8cdb2d | textbox | Heater circuit insulation resistance:
8f387beb-6c26-460b-a2e8-22fec3ebe881 | signoff | Installed by:
79b1c311-9734-4e06-b6b8-a03071d02204 | checklist | ITR-E-12 Electrical earthing |  | ITR-E-12 Electrical earthing |  |  | 4a7db931-b4b1-462c-a54b-93ecaab57860
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
963491f5-16ba-4a4c-80ef-5f3f0eade886 | checkpoint | Earthing System
565f82de-bf50-5fbb-9b18-fc822d28b51d | textbox | Electrode Type:
6bb632d0-f36e-59db-87ad-265f703b4f8b | textbox | Electrode Length/Size:
2cf8c12e-5c14-5b83-a466-ad03a065d0af | textbox | Location of Electrodes:
3dcbfe74-28a6-592c-863c-6df57db7ee0d | textbox | Method of installing electrode:
e0aabd45-e4b3-599b-8cff-1de8747e8db2 | textbox | Method of attaching to electrode (E.g. Clamp, Cad Weld, Lug/Bolt):
52d4c870-75d0-5539-9e13-f2a56fd27746 | textbox | No. of electrodes:
67676f05-26b7-4eb1-871e-6ae28fe9a806 | checkpoint | General
0d4979d6-a84a-5c8f-9cf9-8f5f9295283e | button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
404f59f5-c9a4-541f-a28b-585b3104ace5 | button | Ensure that all metal work is earthed as required. | Yes,N/A
50c4c2f1-8a17-57f1-bb2e-37c2703f8e9a | button | Check welding of earth bosses and associated surface finish. | Yes,N/A
b3b45868-275c-56d8-9068-b7d047778f04 | button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
f067b7e3-c599-5d85-ae91-fbdb6333f72d | button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
2e6710ea-0a48-52f8-9a69-562614fb9924 | button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
e076c2ae-5005-5c14-a9cf-56f3cbf0c135 | button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
56be7626-f798-51ed-9db6-6543d9d96fe7 | button | MEN Link installed: | Yes,N/A
6450751c-1b00-40a7-b4d1-413db37cbaa8 | checkpoint | Earthing Conductors
0263c6a9-de56-5f20-a80e-f373ff6cb706 | button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
a6453be3-4646-50ba-9229-53f8d66b6d5c | button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
1bf16bb6-5b4b-5b87-a5c7-039de680ccb0 | button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
8ffc6562-c26c-5393-8364-ce4d087e84a2 | button | Ensure that earth cable identification markings are in place. | Yes,N/A
fbbe3e60-16a7-56b0-ba6e-b3fcca1ead1a | button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
6fcdeef6-4002-5963-8346-6692753da9a8 | button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
c680d239-7b9f-4809-affc-97c18c0b2e39 | checkpoint | Test Results
2095a1f8-ee98-5ee8-a5f9-1113b88be300 | textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
fec29192-41ee-561d-a1db-5a8633b0fa52 | textbox | 3-Wire earth test results (If applicable).
83162fea-7e46-5cad-88bd-4c19f5060687 | textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
b760fbb8-ece3-568d-8f74-395d9897ce93 | button | As-builts complete | Yes,N/A
0c86c192-efe1-4681-86f8-71d7e60c9e43 | signoff | Installed by:
1cbbc953-43f4-4ac1-a785-506fe8cf2b24 | checklist | ITR-E-13 Motors |  | ITR-E-13 Motors |  |  | c8261753-e793-42b7-83c4-d46cde61c32c
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6e4532cf-3099-4be2-94e2-590c09582364 | checkpoint | Motors installation
61750882-4125-521b-b73c-b7051d3406dd | tickbox | Tag number, area classification, IP rating correct as per drawings and equipment schedule
e130c550-72c1-51f8-81b8-0219b954ace5 | button | Space heater | Yes,N/A
a559e828-7758-5db9-9d60-200ac0c46111 | textbox | Space heater specification (Power (Watts) and Voltage:)
34d1fd14-6726-42ad-aacd-31948501b13a | checkpoint | Nameplate details correct and in accordance with the data sheet
b97992de-183b-5143-a5b6-52cea09e05e3 | note | Upload clear photo of nameplate
da16705e-dabf-4188-b85b-f6356ce64d71 | checkpoint | Checklist items
711648ec-6edc-5299-ab2d-9686309b4661 | button | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets | Yes,N/A
06c5534a-41e8-520d-b510-3224dd5b141d | button | Identification Tag and Rotation Plate correctly fitted | Yes,N/A
865238fb-7145-5f60-9f8d-9f9e2bb7be40 | button | Motor electrical coupling (Delta/Star) is correct. | Yes,N/A
7606fe02-d33d-5ae3-8cb4-62b2c335868d | button | Check for mechanical condition, air ducts and fan free of debris | Yes,N/A
60b81a0c-4625-53ec-a6ef-14f076c8786c | button | Correct glanding for area classification. | Yes,N/A
388db27f-efb4-5e44-8a12-2b41f84cc711 | button | Holding down bolts fitted correctly. | Yes,N/A
57f4a0f1-0a9f-592a-a7f3-3e108c273591 | button | Check bearing lubrication, free rotation with shaft uncoupled | Yes,N/A
1ac1fde7-7252-5a6d-bf77-c85724cb4eba | button | Cable(s) correctly terminated, labelled and colour identification | Yes,N/A
274fada2-247f-548b-bff8-8aae618ee11f | button | Terminations/connections torqued correctly to data sheets. | Yes,N/A
1d0db54f-2bc5-4db4-a768-1776a2e2b68e | checkpoint | Motor Installation Testing
e1da392d-f7db-5e38-84cb-6d9cab103b1c | textbox | LV Motor winding insulation resistance with supply cables disconnected; 1 minute test
c035618a-8630-5786-bbc5-c4f6dd08e27a | note | Insulation resistance U, V, W
a14001cc-8f70-529e-9c1b-9f34ba3b17f7 | textbox | LV Motor winding insulation resistance with supply cables disconnected; 10 minute test
33c015db-c880-5adb-8d3b-7e8bfe2ef0b3 | note | Insulation resistance U, V, W
c1178978-de0d-5ebf-bc20-17d5381b03c8 | textbox | Motor continuity between windings
41daeb51-2610-596f-9a67-f4e7524b2167 | note | Continuity U1-U2, V1-V2, W1-W2.
88febfce-c285-56e9-a5af-26d7f5101d46 | textbox | Space heater continuity & resistance check
d1720914-31bf-54c2-bcef-1e740890eebd | note | Continuity & Insulation resistance results:
10ea7776-d3c9-58a1-b1de-703a8c5b7d9a | textbox | Thermostat or RTD wiring resistance check
4397f33c-d36a-5fc5-973c-9931d8965486 | note | Resistance:
d70902e6-a19d-593a-9b9f-0308d8aee3c4 | textbox | Check motor is earthed correctly and record motor earth bond:
389779f6-b200-4eb0-99f6-bf4ad90dc6c5 | checkpoint | Additional checks
ca89657d-8274-5b54-90a8-84da7ae9711f | tickbox | Winding temperature detector
bd1fc1d9-c0db-52e5-a38e-0516b08a7c30 | tickbox | Air temp detectors
d0637198-bc05-5217-a05d-48ba0cc8adc2 | tickbox | Bearing temp indicators
f295dfc8-c2f6-5580-8223-5f5450847f2e | tickbox | Vibration Monitors
504a4890-9193-5aad-953e-600d1199849f | tickbox | Condensation detector
1de0af8b-e450-508d-a5a7-bcfc9d12fe15 | button | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable) | Yes,N/A
e42644f8-65bf-52ce-9d7e-9f8740c13e0c | button | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable) | Yes,N/A
c83a97b3-cf6f-58ee-8732-b49b09c133ee | button | Installation conforms to specification and drawings | Yes,N/A
d31e85a1-a5a7-54ca-af23-6d073e938c85 | button | As-Builts complete | Yes,N/A
b19580dd-b596-4a2e-95e9-e0f9d10d8ae6 | signoff | Installed by:
7a5bbaef-38d2-4487-8e8a-bef08ed3ad22 | checklist | ITR-E-14 Motor Control |  | ITR-E-14 Motor Control |  |  | 99619c94-b2e9-4115-ab7b-991f38c85c03
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
fd03434c-5f78-4e17-ba2c-8722e0cb18e0 | checkpoint | General Motor Control
ccb4081a-fb55-5dee-b67a-d0711d40dbe0 | button | Check all labelling and warning signs are correctly installed and visible | Yes,N/A
b4b13c23-1f1c-5ba4-8434-0905765a774c | button | Check control equipment is clean and free from dust, debris and tools, no mechanical damage | Yes,N/A
14347cdf-8b80-51a6-96ce-717884a64cb6 | button | Check preservation and transit items are removed | Yes,N/A
74479542-0f89-5032-b3ed-bbee38ee9f1d | button | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor | Yes,N/A
e3c382fe-0548-59da-962a-070f1617c62c | button | Check all cabling to control gear and motor is undamaged, supported and tidy | Yes,N/A
1db92ae3-c0a7-5543-aace-c4b53b30080e | button | Check earthing bar and connections are correct and tight | Yes,N/A
0c135c8d-802b-5e6b-ae33-bd7a95e65c1c | button | Check incoming and outgoing power cables are terminated and glanded correctly | Yes,N/A
335f5f55-db51-52a6-8c4b-e03f5f9c7aff | button | Check phase identification on power cables is correct and visible | Yes,N/A
265e105e-4595-5290-8963-8ad76e981387 | button | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque | Yes,N/A
6db44574-d2a8-5dc9-82c6-0bf1bb21372a | button | Check all other nuts and bolts are tight | Yes,N/A
62338469-1dd3-5f4f-90b2-718dfe6411b2 | button | Check spare gland entries are plugged with correct rated plugs | Yes,N/A
fe2c1d62-af2f-58da-bc6a-cb432af7b28d | button | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected | Yes,N/A
7a1a5ede-42c3-4db3-8b1b-367e09dc91ea | checkpoint | Variable Speed Drives (VSD)
2c824ae5-729f-5694-b03d-c1c59cc8cee7 | note | Record VSD Details
35149931-e067-5a50-9fbe-b3e5434a6dcb | textbox | Volts (Input) |  |  |  | V
aa7fc944-e808-52dc-abab-70b32996531b | textbox | Amps (Input) |  |  |  | A
54e75ea6-77cf-54c7-ad0a-05a64dc82994 | textbox | Amps (Output) |  |  |  | A
533a4361-f81c-5bbf-965d-3e7c1afbf157 | button | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input) | Yes,N/A
0b15a2de-075d-5d08-9b98-5f3828917084 | button | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used. | Yes,N/A
30b49193-3ae5-5f64-bd99-5cc14c470e72 | button | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged | Yes,N/A
45422c23-0edb-5577-8b32-06b3df6cc9fb | button | Check control signal cables use twisted pairs | Yes,N/A
b1e66efc-3444-5130-99e5-d93ecce73b1d | button | Check control signal and profibus cables shield is earthed at one end | Yes,N/A
7de01878-e2e1-5a11-a664-874935d30da0 | button | Check analogue and digital signals are run in separate cables | Yes,N/A
2c48e9b4-74be-4bb3-8389-5e34acf8714c | checkpoint | Voltage segregation
a83cdd18-fead-5c8a-a41e-3b7a0ecadfdf | button | Distance between input power and motor cable >300mm | Yes,N/A
8eb1fd02-fc13-554e-846b-979d3409d46c | button | Distance between input power and control signal cable >200mm | Yes,N/A
5aa26150-5ca2-5718-b8e5-aa9199f26ae7 | button | Distance between motor cable and control signal cable >500mm | Yes,N/A
187f10bb-d5fa-5244-b94d-0a51356ca175 | button | Check there are no power factor compensation capacitors installed on the outgoing power cables | Yes,N/A
a6d9bcca-8fc7-55d1-b229-abab1bf8d352 | button | Check gland plates with single core power cables are non-magnetic at VSD and LIS | Yes,N/A
e94f5873-21db-5ab1-adc3-f5c1f67e21e7 | button | Check mains voltage cannot be applied to the VSD output by means of a bypass connection | Yes,N/A
206ca093-7416-5cf3-aefb-91b1930d3076 | button | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC | Yes,N/A
9abe4b2f-00fd-57d8-b371-fea8405e2e6e | button | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position) | Yes,N/A
d7bf9fe1-d342-4a15-b696-ceb8ed614ef6 | signoff | Installed by:
283e8841-342e-4083-9b8c-95ea445fe6d2 | checklist | ITR-E-15 - UPS Installation |  | ITR-E-15 - UPS Installation |  |  | 11d46121-522e-4e22-bf34-8a1099a201fc
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
fd1b3421-ee2b-4887-96e2-49de5d69b3e3 | checkpoint | UPS Installation
ee74dfb4-5173-5b30-918b-15fd4dcbf3e9 | textbox | Make, Model, Manufacturer, Serial No. (if applicable):
5fda5ed0-2eb8-5d28-a8c3-9569c2c604af | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
c2819b3f-184d-5e11-a421-83f0adacb1ee | button | Check for mechanical damage. | Yes,N/A
5d0d10c2-f8a3-5b03-bf19-7f1888e4a650 | button | Panel IP rating is correct. | Yes,N/A
a9d753cd-19f1-5d75-8e4b-d3c801298831 | button | Holding down arrangement and seat alignment correct. | Yes,N/A
1ea722dd-1f38-5b3b-b8aa-dce6d9996a51 | button | Panels aligned correctly. | Yes,N/A
44d275cb-d9a8-5a3f-8f61-2770ea603c35 | button | External bonding correct | Yes,N/A
6bc83a0f-92c7-5650-8ecc-308844db006b | button | Phase identification correct. | Yes,N/A
f28650b9-bc97-5325-a4ad-d165c4a7cd18 | button | Instrument, indication lamps & interlocks correct. | Yes,N/A
48ea3162-ff9c-5a2b-b70d-c129c74e9580 | button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
d4a7329d-2367-59c0-ba77-f307c2404077 | button | Check Main Isolator and Bypass switch operation | Yes,N/A
be331f86-40e6-55c0-b56d-10d3bc2dfb73 | button | COM Interface & Mod Link. | Yes,N/A
722dd572-1032-5552-8252-a0993dc022a4 | button | Padlocking facilities correct. | Yes,N/A
2225f314-4bf1-585f-a646-0a3d29fcae34 | button | Check internals for cleanliness. | Yes,N/A
2362929e-a691-57c8-bb94-c8a8ad32d6f8 | button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
fb454ce3-f7c3-55e2-aca2-ffe72a629ea9 | button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
544af1fb-3766-50d5-a3a4-49ed80b200d9 | button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
7937ff8b-3bf0-5d24-a87f-1a1bd9f41fc8 | button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
00f5cc09-0a5a-456c-985d-8deb0629d1dc | checkpoint | Test results
32e3f623-a202-58ad-bc0a-05434e90a4ac | textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
743ea08e-c504-4f08-9204-26a503a950f1 | signoff | Installed by:
9633db95-b606-4bdd-bc04-a65463f18517 | checklist | ITR-E-16 Lightning Protection |  | ITR-E-16 Lightning Protection |  |  | 23cf2d03-ba39-45e1-a91c-087985324bd7
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2bbf38c8-774b-495e-b428-f02bd3e34259 | checkpoint | Lightning Protection Earthing system
97a77683-4eb3-5818-a875-eeb5e4987b8e | button | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007 | Yes,N/A
dc47af06-0f52-5b94-8f23-f47cb32f2ef2 | button | Lightning conductor is 2 metres or more above the entire protected area | Yes,N/A
00bdd8f3-9829-570b-b76d-ba08244baed9 | button | Check the materials and equipment used for the down conductors are suitable | Yes,N/A
94ee2008-9ab5-5c1b-bb1e-32e0c3f58a90 | button | Check the down conductors are routed, located and electrically bonded as required | Yes,N/A
8f67d4b5-b41a-5819-ad80-efa1ebd9b97f | button | Check all installed components are firmly secured | Yes,N/A
94ca0927-1018-53fe-a278-24915e108dec | button | Check the method of protection against electric shock, including the measurement of distances | Yes,N/A
2c691269-3270-5a2c-aa0a-b0fe18eafaf3 | button | Check earth termination systems are interconnected | Yes,N/A
1d93cd4a-2feb-532c-b2c8-5a337b1724ce | button | Check isolating and switching devices correctly located | Yes,N/A
bb82a593-c701-5062-8a35-1ec8b3352a55 | button | Check warning signs and diagrams are installed | Yes,N/A
2eb9b452-7641-5e6f-b803-3a233ab14b66 | button | Check accessibility for operation and maintenance | Yes,N/A
bca6a705-69d3-4ba4-8c0e-b7f81f746e1e | checkpoint | Test Results
d7c62a0f-6b02-5b4c-9154-10602d18b9a4 | textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  |  | Ohm
fce6b836-ea9b-5588-a447-c07ab865e1b1 | textbox | Earth termination system resistance is correct and record value |  |  |  | Ohm
8ff597f6-dea0-518c-be94-8f1a8cdb5637 | textbox | Record the insulation resistance of the electrical installation |  |  |  | MegaOhm
d45e645a-e6ff-5f2b-b8ee-5534cf81d734 | textbox | Continuity of the main and supplementary equipotential bonding: |  |  |  | Ohm
a7d9a615-ff54-49e2-ba2a-d8539e7ae3cf | signoff | Installed by:
19efb3b5-56fe-471a-8f7c-6851d373a8a9 | checklist | ITR-E-17 Cable Test Record |  | ITR-E-17 Cable Test Record |  |  | b79a14d8-2565-401f-a636-ff1eec33e789
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f0ac3927-ad33-4de5-8eaa-8b62fb15c9e6 | checkpoint | Upload completed ITR scans
513fd42c-05fe-465d-a5a6-60e84336e1b1 | signoff | Installed by:
73616095-fd80-4247-9a4d-ebe3a0b85254 | checklist | ITR-E-18 Earth Fault Loop Impedance Testing |  | ITR-E-18 Earth Fault Loop Impedance Testing |  |  | 064727a7-08ad-4cbd-89af-4fa727360dd3
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
46a3e14a-ab31-4288-b25e-bf17097d5e06 | checkpoint | Upload completed ITR scans
ff12af13-adc8-4349-941c-bbd3bdc32ca2 | signoff | Installed by:
0dc4e203-08f7-4c87-81ea-c1cf21ee20f3 | checklist | ITR-E-19 HV Cable Install |  | ITR-E-19 HV Cable Install |  |  | 26a7fc84-21b8-43a2-9be3-cfc9ab0cabf1
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
90ad256a-cc82-47b2-be68-9a9ef3ab8b3d | checkpoint | HV Cable Install
cc29fa55-5fe5-542d-aae6-b5a317818561 | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
3733b5ca-b64f-54bd-ba7c-aed07846a861 | button | Check dressing / cleating, cable undamaged | Yes,N/A
2bbb5df0-4010-557e-b31d-498f09f1e5ce | button | Check cable cores correctly identified and labelled. | Yes,N/A
3cf74f56-d88c-5ab3-8481-56c37a833142 | button | Check cable is terminated correctly | Yes,N/A
b7192934-0b91-5863-a040-df3cc234946a | button | Cable has been installed as per client specification | Yes,N/A
db79cc67-bcee-5799-9eb7-63146f45bafc | button | No visible damage to sheath | PASS,FAIL
429d748c-2b60-5309-9d6f-cc4108496a9c | dropdown | Cable Voltage | 11kV,33kV
1d3abe04-a329-541d-ba46-ea69fd91659a | textbox | Temperature:
1b9d8cb2-e175-5a88-878b-c5f1b97638f3 | textbox | Cable Point to Point:
7591ec71-d9d8-40f4-9572-07a1a6b71781 | checkpoint | Electrical Tests
a598796e-f8b5-560f-8616-052299e798ea | note | Testing for the below should be done at 5kV for 10 minutes. If result is below 1.25GΩ this indicates a low test and will need to be re tested. A brand new cable should have a result above 2GΩ. Please insert photo of test results.
b23c38ff-795d-555a-9db5-6b118428b720 | textbox | R-WBE |  |  |  | GΩ
b58fc05a-668d-5951-9d0a-e0aa26497667 | textbox | W-RBE |  |  |  | GΩ
d3aee404-6d4b-545e-8f34-01439b4d5763 | textbox | B-RWE |  |  |  | GΩ
d920a905-8990-5944-98ae-7117035d7879 | textbox | One Core |  |  |  | GΩ
e522260b-45be-4509-97a6-67cc2cb9a311 | checkpoint-no-value | Sheath Integrity Test
a83836d2-51e2-5b6d-bcbf-973658a28930 | textbox | Test Duration:
ff9b4409-cb93-5d68-bb8a-2f8ec1f70f82 | textbox | Test Voltage: |  |  |  | GΩ
01dafb52-67d2-56bb-95ea-97d522e08cec | textbox | Result (GΩ):
17ec1322-89c4-48fa-8d02-aed878f0ef01 | checkpoint-no-value | Test Equipment Details
01c20c58-3ecd-59fd-b3f2-5af833fc28e4 | dropdown | Make | PHENIX
23d953f4-0d53-5dcc-9e1a-6456cb5f82cc | dropdown | Model | PM10A
d97c7ddc-da00-5bf1-aed1-7ae042f0ca07 | dropdown | Serial No | 20-4331
ad61610c-21d8-57dd-9641-37d7310f5550 | textbox | Calibration Expiry Date
db024b07-edc6-49ca-bee7-7aeaad1efdad | checkpoint-no-value | Installer Sign-off
4997561d-fb4f-4a8a-998f-ad8ecb55915c | signoff | Installed by:
7be88078-9aeb-46ce-91d8-a16e2f8f9102 | checklist | ITR-E-20 Cadwelds |  | ITR-E-20 Cadwelds |  |  | 5005dc5d-fdd1-4f5b-b310-9bf148f1ee18
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
241a2515-5a2a-4e6b-9a09-d09b755df5e1 | checkpoint | Mold type, # and cable size identified
2f7320b4-2cff-5f71-8fe6-e7f3902dd6e1 | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee
abb76751-a881-52a1-8f7e-4fab54e87329 | dropdown | Select mold # | GTC-312C, XBQ-2C2C, TAC-2C2C, ZC-11159Z, TAC-3D2C, XAC-3D3D, ZC-11160Z, TAC-3D2V, TAC-3D3D
9126dd07-27cd-5c38-af56-01b35b0377d9 | dropdown | Select cable size | 50mm to 16mm Earth Rod, 50mm to 50mm Tee, 50mm to 50mm Cross, 185mm to 185mm Tee, 185mm to 120mm Tee, 185mm to 120mm Cross, 185mm to 185mm Cross, 185mm to 50mm to 50mm Cross, 50mm to 70mm, 50mm to 50mm flex Tee
d6cb8840-eb8b-4f4e-9456-f882faae229e | checkpoint | Cadweld Visual test
84038c1c-95a6-42cf-85b8-5e4cd21c417a | checkpoint | Cadweld Ductor test
c2a2a535-a905-5103-a824-0237c5ce931c | textbox | Result :
5654c549-fbd1-5ee9-82d1-23e4cfcf31ca | note | Pass if <50 micro ohms
4430fdf3-e236-438b-976b-0ff2ee98875e | checkpoint | Cadweld wrapped in 3M SCOTCH 23 RUBBER or 3M TEMFLEX 1500 GREEN TAPE
39c42f92-3ab2-47be-9a45-d4a7e350530a | checkpoint | GPS coordinates taken
ffe1514b-1ea7-557b-9a87-02c3973e71c8 | textbox | Coordinates:
a4ca5367-a6f3-4ed3-b094-27c73bbca1a7 | signoff | Installed by:
6d2d8201-3fe9-493d-90da-d2199883941f | checklist | ITR-E-23A Coaxial Cable |  | ITR-E-23A Coaxial Cable |  |  | 9131f0e2-ac76-4db3-9bd2-cbbd27e0983a
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
069ba5b1-0491-4ab2-b284-8d947dba7012 | checkpoint | General
9d2657db-c036-530b-b905-785b1ff65656 | button | Cable passes visual inspection | Yes, N/A
fcef5917-93c0-5def-9aff-b3a303bccde4 | button | Verify cable type, size, colour code and tags are as per cable schedule | Yes, N/A
6470c79f-e95e-5fe1-b8d2-1d14953e3cbf | button | Check cable cores correctly identified and labelled. | Yes, N/A
27988787-0621-54b8-8e89-2e873b615368 | button | Confirm cable routing and segregation is correct. | Yes, N/A
f60b55de-b0db-51b5-9641-5c2bca20e01e | button | Check that cable core polarity is correct | Yes, N/A
d34715e9-cb68-51d4-9459-06b8b0947351 | button | Glanding / Locknuts correctly installed. | Yes, N/A
c1aaf9c7-9181-5a97-ae9b-b6eb2bf4401f | textbox | Gland type - from:
abcdba45-87c3-5449-8ed6-677975e720de | textbox | Haz. Area Cert Details.
802301b2-5caa-5b67-b60d-64bd13507cc7 | textbox | Gland type - to:
85457fe0-6983-5535-a92b-658418636c2b | textbox | Haz. Area Cert Details.
75d73dfd-de5c-5b57-be3c-b88734d4fb0b | button | All ‘spare’ cores have been made safe and are identified | Yes, N/A
e3b3e37f-9543-5373-af51-47303881b1ef | button | Bending radius satisfactory and as per manufacturer's recommendation. | Yes, N/A
55fee049-b8b0-4635-9988-e574e5602249 | checkpoint | Coaxial Cable
d13fb974-2014-5d4a-b1a1-b6cb0ed77f23 | button | Check cable terminated with correct crimps. | Yes, N/A
baa37f6b-b258-573c-99e2-f5a57e075595 | button | Check Continuity | Yes, N/A
c9c68288-7159-5f06-8d44-33b8de8ad146 | button | Check shield/screen correctly made off | Yes, N/A
c9bb02f6-8ac5-4f4f-9487-2a7b4d80e9d2 | checkpoint | Electrical Checks
ce9e2637-ed47-5bc6-9675-d6e7f2610e93 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
7be5548a-6921-4e13-9778-63d77a986cc8 | signoff | Installed by:
1add05d4-0852-4823-8d5d-908f68bf7c78 | checklist | ITR-E-23B Data Circuit |  | ITR-E-23B Data Circuit |  |  | b6c41a75-1a97-4497-bea3-1fecfb40d6ec
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f1d87c70-5a0d-43a8-a5ea-f3de1781c58f | checkpoint | General
cefb7fa4-580b-5907-bd96-24bfe6261d71 | button | Cable passes visual inspection | Yes, N/A
f7692762-dd5d-552e-966b-b67504b02d6a | button | Verify cable type, size, colour code and tags are as per cable schedule | Yes, N/A
9f946950-9800-5089-a7d2-57e425e51626 | button | Check cable cores correctly identified and labelled. | Yes, N/A
8582991d-38d9-5d33-853e-cd59d18fe964 | button | Confirm cable routing and segregation is correct. | Yes, N/A
e6922dba-a113-58e8-bd5b-a88650f2207f | button | Check that cable core polarity is correct | Yes, N/A
2d7d335c-e7d2-5606-bbc0-461a51d2cf41 | button | Glanding / Locknuts correctly installed. | Yes, N/A
c4719cd9-c024-5f1c-bd15-1e6c403955eb | textbox | Gland type - from:
91885013-2da1-57ad-927f-723caf8ebdfd | textbox | Haz. Area Cert Details.
af5e0a1d-d591-5f7b-94e6-10e71e781db4 | textbox | Gland type - to:
5361fe1e-8d73-50c8-ab3e-c5b8c74f7997 | textbox | Haz. Area Cert Details.
32ba3d03-e26d-5a27-a803-ffbcfe251e02 | button | All ‘spare’ cores have been made safe and are identified | Yes, N/A
a95bd152-b724-5687-8136-78135f85c8ee | button | Bending radius satisfactory and as per manufacturer's recommendation. | Yes, N/A
8152e388-00c5-44bf-8900-7c3da99595ea | checkpoint | Data Cable
2a029111-dd2e-559d-a297-eb1011222815 | button | Check cable terminated with correct crimps. | Yes, N/A
317b6569-567a-57d3-acf5-465e6396a43d | button | Check Continuity | Yes, N/A
b29a0269-7637-5a2e-9974-20f7659a954e | button | Check shield/screen correctly made off | Yes, N/A
2bd1a639-9717-4227-a259-980d082a737d | checkpoint | Electrical Checks
14d77239-2f10-522c-8756-5595cd52bb13 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
b756062d-afa9-4063-b2e0-977ea24035c2 | signoff | Installed by:
3cac879e-0ebd-418d-b453-b0f651405394 | checklist | ITR-E-25 Cable Lug Installation |  | ITR-E-25 Cable Lug Installation |  |  | 09debe55-17a6-4fd1-9bce-58e47110a374
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
494ee713-1f5c-4a42-b947-f113356e6374 | checkpoint | Cable lug
b4da03c1-8749-5f09-bfc2-374ac65a14e5 | button | Appropriate lug for cable size has been used. | Yes,N/A
9d4b1f51-de3d-576d-862f-a8d083765d4a | button | Lug has been correctly seated with no loose copper strands outside of lug. | Yes,N/A
363cce8b-dbbc-5348-be35-34c96d368a58 | button | Lug has been crimped with 60 tonne crimper. | Yes,N/A
262a3f8a-7f6d-5cea-93c4-a313b1519b40 | button | Joint sealing paste has been correctly applied to the contact surface of lug | Yes,N/A
a06ba470-150f-434b-b668-c51955fbac37 | checkpoint | Bolts
69ae2587-50e2-5271-82a7-c84e5555dfbb | button | Bolt has been torqued to manufacturers requirements | Yes,N/A
92f863e9-9769-5d14-b9b4-2801dd763abd | note | If no manufacturer torque spec, use torques below. M8-20NM, M10-40NM, M12-70NM.
d5c3518f-b52a-502f-844f-b34662539eed | textbox | Manufacturers torque requirement (if applicable)
d573f1d7-1b65-4041-9334-cbda550e7835 | checkpoint | Test Results
8514f77d-1ee6-52f7-97e5-204673608330 | textbox | Continuity test results
032e8a57-e21b-5eda-987a-780b7af7eba2 | textbox | Ductor test results if applicable
971fb58b-92a5-4681-8180-6eecb303a025 | checkpoint | Test Equipment Used
442655ff-c82f-5a54-8aee-346fe5834ed3 | textbox | Description
207feb44-b8f6-5f72-8b31-a539f70d4357 | textbox | Manufacturer
01e0704f-055c-5e3b-9f99-90d63018090f | textbox | Model No:
b5beb6da-e67e-5865-9e22-3182dcbd8b74 | textbox | Serial No:
5afeccf3-3aaa-4317-b4b5-347451828a7c | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
024a2cba-f57d-42cd-9986-26bc29123baa | checklist | ITR-E-29 Cat 6 Communication Cable |  | ITR-E-29 Cat 6 Communication Cable |  |  | 36a8c938-bd30-4a87-ba50-74b41af58f66
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
81a7ef9b-5539-4bdd-bad8-1d749799842e | checkpoint | Common to all circuits
4ff6ab71-dce5-5077-86aa-864d2f1dab65 | button | Check cable for damage | Yes, N/A
99590348-80fb-5f6c-a801-6fd0620b3e4e | button | Check cable is correctly identified and labelled | Yes, N/A
166b40e9-3476-5c78-b3df-40dc4cb4f585 | button | Check glanding/locknuts correctly installed | Yes, N/A
90a29622-865f-5a8a-97b0-392abe2a99f3 | button | Confirm cable routing and segregation is correct | Yes, N/A
cb6adcca-2839-54dc-97e4-c056c3962e7c | button | Confirm to and from destination as per design. | Yes, N/A
19e08cdd-8192-42ba-a4b2-99206ee1fe76 | checkpoint | Data Circuits
3fb22e8b-c878-5047-8b00-61c058265792 | button | Check cable terminated with correct crimps | Yes, N/A
883378a9-1b30-5dac-ac31-3a51ef84c313 | button | Check shield/screen correctly made off | Yes, N/A
3b706ab5-639e-5c4f-a970-1aa8f1f6bd2c | button | Check Cat6 end-to-end certification (outlet and cable) | Yes, N/A
33a7ffd4-a62a-4fd3-b167-84ef33e7fd1e | checkpoint | Electrical Tests
8437f22e-b9b2-5507-9504-825e461f724d | button | Confirm LAN Link Tester is used to check continuity | Yes, N/A
66b1d4e2-78dd-5a61-8262-0cd62f4a2e57 | textbox | Insert Continuity results: |  |  | ohm
e94f230c-3390-4ff4-9f51-e5ebcc226562 | signoff | Installed by:
89690ab6-afc4-4063-bcab-0149059ba804 | checklist | ITR-E-30 Earthing Electrodes |  | ITR-E-30 Earthing Electrodes |  |  | 9f573800-b1f7-4d5a-b36b-56cf3343591d
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a5bfa3a7-da27-4a04-935a-1396c4a22636 | checkpoint-no-value | Earthing Electrodes
ab301dbb-aa29-5568-8e65-39baf9c5313e | textbox | Location of electrodes:
3443ba6c-d4ca-5108-9120-9bfae58fa263 | textbox | Electrode length/size:
8d2f5a8e-70a4-5bd1-a15d-68ca16d2a5c6 | textbox | Electrode type:
6c595855-eb8a-57c5-92d8-a0ac1a421b2b | textbox | Method of installing electrode:
41b5d6eb-47a8-5eee-8fc0-b77c5a55c9d0 | textbox | Method of attaching to electrode (E.g. Clamp, cadweld, lug/bolt):
c4aa50fd-35f5-5644-a936-050abdab6727 | textbox | No. of electrodes:
031b001b-56b3-5941-bfae-1045ea1fda65 | button | Earth pits correct as per specifications, covers, no damage | Yes,N/A
23c2f581-c33c-546c-891d-627b093dacaa | button | Connections to electrodes are secure | Yes,N/A
b073d3d1-981a-514e-8584-5f0e2d1a70ac | button | Structural and equipment earth connections secure | Yes,N/A
945aa7ea-460b-5c3c-a9d5-df99aa45dc26 | button | Earth cable lugs secure, cable passes through concrete in PVC. | Yes,N/A
41aabb29-9afb-552c-9358-4014187fe36a | button | Equipment bonding, connection to main earth bar secure | Yes,N/A
793a1926-e194-535a-ae34-b1d67fe0de6b | button | Earth electrode identified, MEN linked, installed and labelled | Yes,N/A
8063742b-83d6-4226-a7a4-2500cea1f0e8 | checkpoint | Earth Electrode Test and Continuity Tests - Disconnected Electrode
8917ff85-066a-5e99-9db4-205629d84d61 | textbox | Electrode 1 |  |  | Ohm
d5e6b662-0e9d-59c3-ad87-2b3434424707 | textbox | Electrode 2 |  |  | Ohm
4aa60d1b-f626-5ab4-8900-3c8f9342cba7 | textbox | Electrode 3 |  |  | Ohm
371fa17e-0fad-5db3-b52b-ac10edacc4c0 | textbox | Electrode 4 |  |  | Ohm
ec6c3370-3613-5d85-974d-d5c1dc6895c2 | textbox | Electrode 5 |  |  | Ohm
9c2ed006-0cca-5dbc-8560-e7fb5b38f3ae | textbox | Electrode 6 |  |  | Ohm
47a8bcbb-2de8-5b97-a20a-eb44e071e5b8 | textbox | Electrode 7 |  |  | Ohm
9eadce2d-5c41-5123-8cd4-f1a3293a4022 | textbox | Electrode 8 |  |  | Ohm
b0979ca6-e684-4b3a-bf94-38c88acb2803 | checkpoint | Earth Electrode Test and Continuity Tests - Earth Grid Test Results
efe0bd15-6b4c-5c14-987f-12a8d398912c | textbox | HV earth grid |  |  | Ohm
7fac14b5-0cfa-51d6-acb9-275432c4c2a2 | textbox | LV earth grid |  |  | Ohm
fb8edbdb-c998-5443-a19e-42a95b8be934 | textbox | Combine HV and LV earth grid |  |  | Ohm
9afb7e81-aa4f-58df-9701-bff34ac056a6 | textbox | Instrument earth |  |  | Ohm
e2b2d84b-ecf1-47c6-a90c-abe61a47e324 | signoff | Installed by:
15fcd947-670f-4f5d-9be0-8306a1fd28e4 | checklist | ITR-E-32 Battery |  | ITR-E-32 Battery |  |  | 6257b4c8-feab-4cba-ae15-18714d65d74d
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
82580a12-4ba7-472c-bfbb-9c954acf8ce2 | checkpoint | Batteries
ef1575d5-be8a-5950-b506-c7e6f7cd0e9b | button | Check equipment and nameplate details are correct in accordance with the data sheet and drawings | Yes,N/A
71b07843-1c7c-5601-9ee7-2c2478dc7bc9 | button | Transportation packing and plugs removed | Yes,N/A
2399f8b0-d1b1-57b4-80ce-4231f1ca3948 | button | Battery cells correctly rated and numbered accordingly | Yes,N/A
631ec1e2-f9ab-572a-a160-69a0050cf0e5 | button | All cells correctly mounted, links tight and shrouds fitted | Yes,N/A
d4b04a18-7231-55e7-84a8-7f9164cc8dfa | button | Internal cables correctly installed | Yes,N/A
8385b974-1a45-57f1-9ae5-fe977417b91d | button | Protection of live parts correct and adequate | Yes,N/A
813995dd-998f-5dca-bfca-c94165a3220a | button | Electrolyte level correct in each cell | Yes,N/A
ba5fe2d7-9b75-5bb5-9264-0131bf49629a | button | Check specific gravity in each battery cell | Yes,N/A
e182744e-f48d-51f6-99e3-d9160822fa1c | button | Check cleanliness of cells and battery racks | Yes,N/A
378615ec-75c2-5930-a061-ecab70d23fe9 | button | Verify approved grease applied to battery terminals | Yes,N/A
79226d91-7761-5e48-87ee-8c7578dd9569 | button | Earthing correct and tight | Yes,N/A
291b1a35-6d70-5fa6-bc22-09140ee622a7 | textbox | Verify polarity correct per drawings and record voltage
bcfd9582-6e05-58f8-9650-c81d622eed9e | textbox | Preservation as per supplier instructions
4f54d7ed-f368-5bf5-9cb2-fd213ce86628 | button | Leave equipment with any isolators and/or circuit breakers switched and locked in the off position | Yes,N/A
c0a0103f-01a9-4700-a8c7-0e3b5b1a7803 | signoff | Installed by:
2f5ed2d1-fba5-4b85-a950-ff5c2b5b5c24 | checklist | ITR-E-34 Low Voltage Switch Board |  | ITR-E-34 Low Voltage Switch Board |  |  | 8d296356-2fce-4cc5-a430-c6c5bb4f18b8
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
910d5a43-fef8-40a7-b2e1-26d6da8e2445 | checkpoint | Low Voltage Switch Board
cd235430-64d2-5e69-837b-7b306b6ed6b0 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
5efdf7dd-5482-53b5-8e2b-4201a1fade6f | button | Check holding down/mounting arrangement is correct. | Yes,N/A
1c52c74b-67d5-5020-a850-472b4fcd9bcc | button | Check for mechanical damage. | Yes,N/A
141296eb-cb9c-57e0-8f35-2844ddc3e6e2 | button | Confirm that all temporary supports, jumpers and ties have been removed. | Yes,N/A
4f9896f6-45a1-5350-9c5b-8966ad659bc9 | button | Incoming cables correctly installed, terminated and supported. | Yes,N/A
572d7dc0-38c5-56a1-b48b-7fa756928cdc | button | Phase identification correct. | Yes,N/A
bd57fe01-0c2d-5fad-84ec-2bb7c13bf569 | button | Confirm that padlocking facilities are provided and operate correctly allowing all circuit breakers to be locked in the open position and safety shutters locked in the closed position. | Yes,N/A
c7bb178f-0922-5441-b9af-aa0fee8330c3 | button | Confirm all cubicle doors can be opened without obstruction and minimum required clearances are retained | Yes,N/A
3fb275b2-3c22-5954-b7fd-bfbc62f45fd5 | textbox | Bus bar alignment to manufacturer's specification and connecting links tight to specified torque.
76875fc5-210c-5e5d-a925-bdc79e4fdb64 | button | Confirm components, fuses etc. correctly sized and identified as per design drawings and Single Line Diagrams. | Yes,N/A
c1f9a3c2-fbde-5a3e-b362-c5c533e85977 | button | Instruments, indication lamps and interlocks correct. | Yes,N/A
52671435-bcc3-578c-994f-dfc5e5e9dd4f | button | Ammeter and current transformer correctly installed. | Yes,N/A
2bbf6ab3-d915-53e0-91b4-a668800b71d7 | button | Check internals for cleanliness. | Yes,N/A
4b88915f-0582-5941-923b-1861f6d23df1 | button | Check that Switchboard is correctly earthed. Check door, escutcheon, gland plate, gland and frame. | Yes,N/A
7ab3b1ee-5e2c-5587-9738-106c1274938e | textbox | Test and confirm the earth resistance between switchboard and local earth system is less than 0.5ohms
1613d7af-085d-5246-9107-60bb31d65ac7 | button | All internal cabling and wiring neat, correct, and undamaged. | Yes,N/A
7d708cfc-6394-5090-8ee6-3496d831fff8 | button | Unused cable entry sealed. | Yes,N/A
9b1076d3-6838-548a-b8e3-ab0a622759f0 | button | Heaters correctly installed. | Yes,N/A
4e4def6e-6ff9-5e08-bb27-150eb0627a78 | button | Confirm that all insulating bushings and barriers are satisfactory. | Yes,N/A
8661e92b-bb89-4509-907d-c561fdee93b2 | checkpoint | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
0d9750f0-65ef-515a-b46d-a076e60ab753 | note | System KV ¦¦ Test V (dc) ¦¦ Min IR Reading
044fe293-acab-5704-8aca-55c379535825 | note | <1.0 ¦¦ 500 ¦¦ 10 MΩ
155c7645-eabb-5f54-8a96-122cf3697180 | note | <2.5 ¦¦ 1000 ¦¦ 50 MΩ
c5a0227e-a0c0-52e5-8ca1-dcd11c4a653d | note | < 4.6 ¦¦ 2500 ¦¦ 100 MΩ
5b0a160a-f689-5523-9f35-a871b09dde33 | note | >4.6 ¦¦ 5000 ¦¦ 250 MΩ
47c66daa-50b1-55ab-92b7-e33343a96925 | textbox | L1 - Earth |  |  |  | mega ohms
c6be092f-0c6d-50af-85a3-c2674691b16c | textbox | L2 - Earth |  |  |  | mega ohms
6d4e070c-21a6-5fdc-afa6-c7889a4356b2 | textbox | L3 - Earth |  |  |  | mega ohms
6dc67cb9-40ff-572a-a417-d2c2b962ae79 | textbox | L1 - L2 |  |  |  | mega ohms
68259625-2eab-5b5a-aae5-fc107b04a1b8 | textbox | L1 - L3 |  |  |  | mega ohms
708e02ba-268d-55a5-a88b-64b2bb90082b | textbox | L2 - L3 |  |  |  | mega ohms
bbab0288-3756-5591-a178-53f344fe69e5 | textbox | N - Earth |  |  |  | mega ohms
2313dd27-72aa-4632-9715-f23737f8f507 | signoff | Installed by:
90c1f14b-635c-44d1-99f9-c6073d90ec6d | checklist | ITR-E-40 Bus Bar |  | ITR-E-40 Bus Bar |  |  | b0239a9c-1b06-4d81-85ab-f186597cc780
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
010083bf-8e3f-4bcf-a92f-68344f7f7ffc | checkpoint | Bus Bar
419586f1-81de-588e-ad92-22b8f7ceda33 | button | Check entire Bus Bar and confirm there is no damage | Yes,N/A
8d9fffd4-7f32-5bcf-a4cc-b5ac7c4972fa | note | Please attach photo of Bus Bar
48033efa-e8a9-54f8-b71d-43d5e146dfe4 | button | Bus Bar alignment is correct | Yes,N/A
6d83dd9a-ce84-52f7-8bc6-260de41d0dd2 | button | Confirm all jointing bolts are present and have been torque tested in accordance with the manufacturer and design requirements. | Yes,N/A
cd5a8c2f-1101-5cad-84fa-6aa51de73ad7 | note | Acceptable Bus Bar Torque Settings:
510b6263-66d7-5633-9831-f42b2173fb32 | note | Bolt: M6 ¦¦ M8 ¦¦ M10 ¦¦ M12 ¦¦ M16
d48e325a-dbb7-5ed5-bb82-e0da679374d2 | note | Torque: 10Nm ¦¦ 20Nm ¦¦ 30Nm ¦¦ 40Nm ¦¦ 60Nm
0b9f7360-eed0-5684-86bd-759036036131 | button | Confirm all transit packing and preservation materials have been removed. | Yes,N/A
a404a903-244d-59f7-9421-98b0fb8b582d | button | Confirm Bus Bar clearances conform to manufactures and design requirements. | Yes,N/A
695b8602-4984-5340-80e3-b556dbc206d1 | button | Confirm all Bus Bars are secure within the supports. | Yes,N/A
8949e3d6-37ba-5856-825f-a1295f980a6e | textbox | Insert applicable test results
5b26a5c0-2eec-4e4d-88e0-2490b8a13e0e | signoff | Installed by:
fc2523e6-51f7-4b90-86a4-401ac5f520cd | checklist | ITR-E-45 Local Control Station |  | ITR-E-45 Local Control Station |  |  | 958af9de-e059-4236-8ba3-174ea58d851f
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
862532a2-b133-45c8-ab79-92ec02ab002b | checkpoint | Local Control Station
f601df52-7e6f-52d9-ac22-b6cf95871883 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
e0c38cd3-9f08-5608-bcfd-87782cfa4ffe | button | No mechanical damage and paintwork in good condition. | Yes,N/A
a5129bcc-a64c-5e49-960a-059d04cd3ab9 | button | Glands correct size and type | Yes,N/A
a885f228-a93b-5662-8621-fe5dbdd95b82 | button | LCS properly supported and accessible | Yes,N/A
b8c82542-7662-55fc-9ea7-54fafa907c58 | button | Spare entries correctly plugged | Yes,N/A
4881f7ed-1c86-53d3-8ebf-32ee6a90cea9 | button | Check internal cleanliness | Yes,N/A
a6e866e4-fe81-5ce4-a14e-6ad7a11d073e | button | Check push button/control for mechanical function | Yes,N/A
d914740e-3620-5876-9d78-14e40a5dc2b7 | button | Check connections and terminations tight | Yes,N/A
7230ef78-bd63-558b-a310-16f7aa4d22cf | textbox | Check that LCS is correctly earthed. Test and confirm the earth resistance between LCS and local earth system is less than 1.0
e596f28c-da51-57e0-969a-39307d47690b | button | Check gasket and seals are installed and not damaged | Yes,N/A
248d51e1-e6b5-5201-b8a7-f6c7ecd894b0 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
21a69e32-25df-5f0d-948d-4f4fe486c048 | button | As-Builts complete | Yes,N/A
f5e7f44c-ed2a-44ec-bd73-655074f21cf7 | checkpoint | Electrical Checks
403741ef-2f04-5ff0-b708-6d9c38d96d3a | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
ac7b91d6-d913-44f1-ad06-21f32f1e6338 | signoff | Installed by:
c96c36d5-b05a-47aa-9758-e28c288b2bff | checklist | ITR-E-48 General Lighting |  | ITR-E-48 General Lighting |  |  | 6ebf2218-f3d6-4a32-b170-82125d49e827
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
72525231-4041-43d5-b2a0-1dcd8a4e1e7c | checkpoint | General Lighting
3c6824bf-6d79-558a-9b5f-c17baf105882 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
6daf77b6-8b50-510a-a02c-3b2a67d62b35 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
2c39e37f-9b79-5518-986c-3dac578cf42a | button | Operation of emergency lighting fixtures checked | Yes,N/A
bcf670dd-fc30-51a3-8df1-f619bed62c6a | button | Mounting arrangement and degree unit is installed is correct | Yes,N/A
42ae753b-ddd0-50fb-ae2c-edcb6b4b1109 | button | External cabling is correctly installed and labelled. | Yes,N/A
0f3360fe-e87c-5127-a2a1-4838638465d3 | button | Battery run-down test per manufacturers specification | Yes,N/A
b301fd42-45dd-5b8f-9f1c-89ae319e08d7 | button | Power / load balance on distribution board checked | Yes,N/A
da5ccec9-531e-568d-9b75-34df9dd4b687 | button | Operation of remote lighting control checked | Yes,N/A
3352d4f5-83b3-56e7-a103-c0df76cabdc7 | button | All spare entries blanked off with correct plugs. | Yes,N/A
7ae46989-20ae-5e12-9a19-9db265456240 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
3c9772df-31b5-56f3-8aeb-46209b5ac02d | button | Conforms to Specifications and Drawings. | Yes,N/A
a0707218-4354-5a9d-b15d-8614ccd30615 | button | Insulation resistance of final sub-circuits checked | Yes,N/A
12a18436-08e1-58a7-a3e8-5007f7044f76 | button | Operation of photo-electric cell control checked | Yes,N/A
84e84693-1262-5d5c-8f8f-aa028bac1125 | button | Lighting pole is adequately earthed | Yes,N/A
87a14146-1e70-5089-850f-1aa44924e4d3 | button | Circuit ID fitted to all light switches | Yes,N/A
86e4401b-d1ef-5ec9-8969-8eef73f89a2c | button | All fittings correctly labelled | Yes,N/A
dbfb30e5-8902-5caf-9f8e-c6908b6a9e7c | button | All switching tested and confirmed as correct (two way, intermediate, on/off/auto etc | Yes,N/A
017e8688-26f3-5362-9047-3dabe7a020c8 | button | As-Built drawings completed | Yes,N/A
6deddb91-9235-417e-8828-ce15a175a384 | checkpoint | Lux Levels
f7e7c702-59c1-5ffc-866a-cee27ecdd80f | button | Lux levels meet minimum client specifications. (Closed door and measure lux level at darkest point of personnel accessible area) | Yes,N/A
9335e9ba-130c-59bd-80a4-2fbe40cb7d5a | textbox | Lux Results:
8577837f-56a0-4f29-be2d-f3fb5ecc71f0 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
697270ae-4e5a-415c-ab9c-a57082e96b63 | checklist | ITR-I-02 Instrument Tubing Installation |  | ITR-I-02 Instrument Tubing Installation |  |  | 97508a2a-c8cd-4e53-a99a-ea246812a5d8
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
754a2d32-7738-4e27-95c6-ac2c3ef96e67 | checkpoint | Checks Pre-Installation
49159251-6dcf-5cfc-910a-abe92ecda659 | button | Tubing connection to and from equipment as per drawings. | Yes,N/A
40506286-5029-559e-8989-69a8e035b394 | button | Tube material type, size, gauge and standard confirmed and available | Yes,N/A
4eb3c4e0-23a1-5ea8-86f0-50ed7148722b | button | Tube fitting size and type confirmed and available | Yes,N/A
5d9c4872-4e9c-4794-bc7e-610b67c60dc7 | section | Checks During and Post-Installation
cc7d0830-c26f-4543-abe4-fb2d689a2156 | checkpoint | Checks During and Post-Installation
4ac924f1-4423-5dc4-8710-3c0438cba621 | button | Correct thread compatibility and engagement | Yes,N/A
cbbfed41-cbe9-522c-a048-88e0dc759d58 | button | Correct thread tape and sealant used on fittings | Yes,N/A
ea4dc0cc-6fc7-54c5-8a15-63572cc12509 | button | Check fitting ferrule orientation and confirm prior to connection | Yes,N/A
64202796-941a-5e4e-b5cf-42640ea5cd78 | button | Tube installation is in compliance with the client specification. (Supports, bracketry, slope, expansion, vibration, access, cables) | Yes,N/A
02fdd7b8-de9d-508b-8c62-666be25bc68e | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
d8efd64a-8454-5fe8-a83e-24bdd64a665c | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
9f80a8b5-837a-50f3-94a7-65b677fc8bb0 | button | Depth insertion tool used; witness mark visible at all stages of process | Yes,N/A
3be9045b-0a42-53df-b373-a0cfc7bca7e9 | button | Tube fitting hexes marked to ensure correct swage tightness | Yes,N/A
6319aca0-2069-53a9-8e62-d3e2549819b0 | button | Random check with No-Go gap gauge | Yes,N/A
3faf2134-eda7-586c-8f80-ff4efdbb25f4 | button | In service leak test performed and passed | Yes,N/A
26373ea2-aa60-53f3-b9af-cc9c96137cab | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
8f041907-06ca-5ac6-8f42-14a1272505f0 | note | Refer to Swagelok book for tube/thread size pressure ratings
1efaef86-5739-490c-a7ac-ad98728ac7f9 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
c92b7ac2-6a8d-4f7c-86ac-4a1b13cf3afe | checklist | ITR-I-03 Instrument Pressure/Leak Test |  | ITR-I-03 Instrument Pressure/Leak Test |  |  | aff28fe9-c304-4178-86e3-1eb82973eb32
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f4d8d21e-a747-4db0-8e0e-68613190187e | checkpoint | Checklist items
29af9b06-db28-5cfc-9e37-3faa3b32b565 | button | Tube identification correct | Yes,N/A
ffa04ea0-0337-511b-8c53-be22c8eac155 | button | Mechanical damage visual check | Yes,N/A
8446b16b-6ec8-5867-a439-3311487b74ec | button | Flow direction and instrument orientation correct | Yes,N/A
77271c24-72dd-5fd4-8d95-c9f8d9450219 | button | Tubing size and installation correct | Yes,N/A
6d0f8c67-42be-42d1-a0f0-d1dbeef5b4f2 | checkpoint | Testing
9bcae28b-41a5-5f45-96bf-49230c06d0ec | note | Verify test pressure and medium is correct per project and manufacture specification prior to test
8e695ed6-5db1-5764-8a51-50820ae97b47 | textbox | Test fluid:
9f199dd9-592f-51ed-9ad0-d8fae0055c64 | textbox | Test pressure:
eb39dffc-c3ec-5758-934a-3a58ee75c599 | textbox | Max design pressure:
f65f4546-28e6-562c-80e7-5568d87e9473 | dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
fe8bb36c-3155-5aa8-a219-19895507f1fe | textbox | Duration: |  |  |  | Minutes
9e6e7c33-8646-5255-a5cf-7d0107066ed8 | button | Confirm all impulse lines have been drained and cleaned | Yes,N/A
495802ce-2843-51f5-91db-461e87c892b7 | button | Confirm any temporary test connections, valve etc. are rated for the intended test. | Yes,N/A
b4e3a5a5-c160-5d3a-9e64-608c02d1e5fe | button | Confirm pneumatic, test gas and aspirator lines have been blown clear. | Yes,N/A
74c3dc63-6a39-512a-9a5a-4464730b5bd9 | button | Check hydraulic lines flushed to project specification. | Yes,N/A
3a1a66d6-e4fe-46bf-a921-6c29976a96e6 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
6dff0826-0455-4bf8-8339-7811b52c752f | checklist | ITR-I-04 Valve & Ancillaries (Pre-Installation) |  | ITR-I-04 Valve & Ancillaries (Pre-Installation) |  |  | 8c11d45c-6832-41e5-a6d8-79773d764b43
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d918794a-8234-4c67-914e-097c71770e28 | checkpoint | Equipment
d783750f-9144-514e-a7d8-b5d9fca1120f | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
9132fc8a-82a3-58b3-8fb8-6bfc616b7c0a | button | Equipment checked for additional items as applicable | Yes,N/A
261050a0-62ff-4d6e-ac29-a0c44b4a295a | checkpoint | Valve
91e15710-c9d1-5d9e-9b17-0b1e8ce5f43e | textbox | Valve Size:
f0fd700f-decb-5742-99fb-821529abf655 | textbox | Flange type:
4b7b5d33-59e3-5456-adab-bcb5fe4dc350 | button | Material certification correct | Yes,N/A
4dcf904b-c604-59b4-b62d-a79bc5246767 | button | Trim material correct | Yes,N/A
ea2a0fb1-3cde-52cb-8f98-cb7d36da7fa7 | textbox | Rating:
b2c24ac3-7ca6-570e-b9d1-160025a7f677 | textbox | Service:
5003c73c-6561-51bb-bf09-0891f6b9bde4 | button | Body material correct | Yes,N/A
8896b5a6-f32a-5740-bac8-385038f3654e | textbox | Leakage class:
66d0aa4c-4ca9-4b02-b00d-6bc507f1f046 | checkpoint | Actuator
7f9973d6-6a20-57cd-bc4f-1e93cd878a4d | textbox | Input range: |  |  |  | kPa
0addbd9c-a08a-5194-bc88-91cc284ce2ea | button | Failure action | Yes,N/A
6926a1f1-f154-5926-b042-670177a2f27e | button | Hand wheel operation correct | Yes,N/A
8d758281-ffc9-4f06-8b44-c3ed5802aeb5 | checkpoint | Positioner
dd2a73c4-94cb-5bc4-a47f-e8bfc3b9ead8 | textbox | Signal range
6fcb5a75-7606-5048-80f6-9f3321406663 | textbox | Output range
1f7bca4b-86ab-4996-b716-273ef149d87d | checkpoint | I/P Converter
acea181e-3a9d-5baf-8035-a5c04afb1b17 | textbox | Signal range
c71cc4ca-dda9-5720-a00f-0310ea4287df | textbox | Output range
f213e6ba-724e-48e7-a09b-dc15887fa1bd | checkpoint | Filter/Regulator/On-Off Valve
f63038e9-1082-5c1a-a7e5-fcdc28c0bd44 | textbox | Range |  |  |  | kPa
4ba132a6-d2f2-5836-9f01-0073938a74f4 | textbox | Pressure setting |  |  |  | kPa
036170fc-af4b-5614-ba96-a78de5e4175f | button | Stroke Time correct | Yes,N/A
8062fc15-7255-58c1-8f61-46011af20170 | textbox | Open |  |  |  | sec
52e3928c-25cf-54a3-af7a-f14d827ea9b2 | textbox | Close |  |  |  | sec
a7864d54-b0f5-53a0-9f64-d4dea7d6b1ef | button | Open/Close times conform to commissioning specifications | Yes,N/A
6c0eab88-991e-4a28-9e25-46adfa4d52d5 | checkpoint | Fail Action
1ddd1587-b667-5c84-a215-85f3f1218519 | dropdown | Electrical Fail Action | FO, FC, FL
61d09ff1-4b94-5c84-b44b-3b81d6e3634e | dropdown | Motive Force | FO, FC, FL
a70c10ba-1ee6-4e93-b483-f1a70423e328 | checkpoint | Valve Field Calibration and Hysteresis Check
a31dd45f-740b-5332-b4ca-42c627cbaf24 | tickbox | Confirm test equipment is within calibration period prior to testing
51da174a-a39f-5fee-92da-d9361bae4caf | note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
0cc82034-d2ae-5d50-bcc6-aaad15735387 | button | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100% | Yes,N/A
45788360-ed5b-4dfc-8fc1-e33e6bbaec2a | checkpoint | Proximity Detectors
3759ff33-4551-5efe-ac87-f50f32f977f6 | button | Open switch set, correct mode setting | Yes,N/A
f57cc0ad-a6d0-5beb-ad67-3e496dac94c2 | button | Closed switch set, correct mode setting | Yes,N/A
1925d13a-af36-53df-8916-38ec2fe043d2 | button | Electrical connections and certification correct | Yes,N/A
2cb7b721-5199-413b-8fb2-bf862c5e84c5 | checkpoint | Solenoid Valve
db34d79b-9209-5ee5-a44c-d3820e535c3e | button | Operation correct | Yes,N/A
9f0c2d4c-8d7a-5639-8c6c-734c82e9db15 | button | Electrical connections correct | Yes,N/A
43f101bc-3e44-580b-9b1c-3045bbaf33ad | button | Electrical certification correct | Yes,N/A
77043595-d414-5041-980a-963bde7030d5 | textbox | Voltage: |  |  |  | V
70fe5354-bb24-5ebd-806d-0e894227d4c0 | button | Pneumatic connections correct | Yes,N/A
1bfb1a06-5782-559b-bb7e-c811c6d60a18 | textbox | Pneumatic pressure |  |  |  | kPa
4c7a4297-9141-4d4d-962c-982d613fb3b4 | checkpoint | Pilot Valve
651f4ce9-34d7-5b14-8e01-047291eef784 | button | Pneumatic connections correct | Yes,N/A
d7024cca-170c-5d0a-8d86-b1b4dd9f916d | button | Operation correct | Yes,N/A
da8efef1-9017-54d7-966a-ba0fd27c6d3f | button | Action/Lockup | Yes,N/A
ea58187c-707e-4b32-a132-55c8bbabf6cf | checkpoint | Hydraulic Actuator
7c906b13-31da-53c3-bc93-1966b124ce24 | textbox | Working pressure
975b18ef-a3db-5b6a-b225-ac74d645dfa9 | textbox | Manifold pressure
9e504aad-a192-58f7-b6b9-1dc379071506 | textbox | Fluid type
6acc186c-b5ca-5e7d-94ca-f9b063aa9cf1 | button | Hydraulic connections correct | Yes,N/A
068794ba-bf5b-56fd-b042-f18e1c7bc939 | textbox | Regulator pressure setting
fe929150-361a-5156-86ef-a0ec2d47072f | button | Pilot operation correct | Yes,N/A
59c7f135-375f-4bdf-b196-f5cd9105f5eb | checkpoint | Accumulator
ea8ce1e5-3d92-5b1b-8918-ce6b3776b251 | button | N2 Charge required | Yes,N/A
a4313a92-c4d2-56ad-a485-3e153944003d | textbox | N2 Pre-charge pressure
3b32867c-fbe7-5dc5-97d1-23a668584b45 | textbox | Pressure switch setting
bf4e6352-97eb-518a-8032-351fb4d015a6 | textbox | Working pressure
85059d6f-bba4-5a9a-8d7b-e137243a46d7 | textbox | Output range
5c6bf8d6-980f-5bba-b389-068e33e15b06 | button | Volume tank & check valve installed correctly | Yes,N/A
2c2ea8c1-614e-48ac-bf6a-c90d5e521047 | checkpoint | Electric Actuator
e58ee991-02fd-5079-86b9-a6420505c888 | textbox | Voltage:
0364a3f0-ada9-574c-8370-0d149defbb01 | button | Electrical certification correct | Yes,N/A
881aa6ad-f0cb-5e59-a9c0-8726e39bc6f6 | button | Electrical connections correct | Yes,N/A
ec9b2798-4085-55b6-88c1-ed19fab85b14 | button | Remote operation correct | Yes,N/A
6810ad7a-f665-5a66-ab51-049b8b839b0a | button | Local hand operation correct | Yes,N/A
815aba2e-0c80-5533-a061-fd958a9bbd80 | button | Torque switches and travel stops set | Yes,N/A
facfa88b-58f4-49fd-8f63-b6f076aa8a28 | checkpoint | Miscellaneous Equipment
de0c820c-cd0b-5a2e-8356-23b7617fb595 | textbox | Description
4dff5fab-4822-5d72-8594-51d2b625a058 | textbox | Manufacturer
21d60b02-b32d-544c-9d8c-161b841ffac8 | textbox | Model No:
6065b1ce-8baa-5248-800e-c09763814df6 | textbox | Serial No:
bb9a0b65-7a66-570f-b775-2a536584923a | textbox | Range:
91146ce2-7872-450b-ac49-64cd814c1d67 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
f4c6212a-8912-475c-9276-25a5c3053bb8 | checklist | ITR-I-06 Instrument Installation |  | ITR-I-06 Instrument Installation |  |  | 4bea3bae-c75d-49b8-9e67-f8bf980edb17
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d6a32dbe-2f5a-41a6-8353-bcfed88d8687 | checkpoint | Instrument Installation
70bfe3f0-9c75-5eaa-8640-42b8477319c8 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
c10d2180-eb34-51a5-b35d-e17ca96387bd | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
24a3bed4-cf49-50a4-bcee-d1376d8048db | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
20d79831-6c2c-50aa-98e9-232f7d48bedf | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
956a3be0-3981-5c57-8a0d-798237c801c2 | button | Vent lines are directed into a safe area. | Yes,N/A
b0634453-debf-5772-8892-ad94488189bc | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
ac2cc897-ce53-5de0-adb6-4e1e79761ab8 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
d69cea9c-2d78-58f7-b078-3ec086b59cbd | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
27ad0057-270b-5803-a1e9-2be2b198bec3 | button | Instrument earthed in accordance with project specification. | Yes,N/A
a46da691-3395-42ba-a098-0fa4c3171525 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
5cfa4415-f79f-4ab3-b33e-2a58bc6c2c61 | checklist | ITR-I-07 Instrument Calibration |  | ITR-I-07 Instrument Calibration |  |  | b92ab4ff-0078-4c12-a80f-1405baa68113
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
01c37575-6d48-4100-93e9-6f442bb68f85 | checkpoint-no-value | Required Data
075d59a8-a405-51ec-b678-532537e459f7 | textbox | Type and Size:
49e45df9-e286-5443-bf3a-ffd44443acd5 | textbox | Make and Model:
e753bef5-c50e-5e16-ad82-cea8456e26a8 | textbox | Serial No:
351549b5-ed76-5f94-888e-0174969499d6 | textbox | Instrument Type:
e425d1f8-9dc5-52f8-9a9c-4d6fc2d9bbf1 | textbox | Instrument designation/equipment no
826ba9dd-12d8-5e3c-bedd-6ada592bff41 | textbox | Calibration interval
410f1caf-8b65-5671-86a6-e5970e473c15 | textbox | Calibration method
5a2240c3-d9f0-532a-b944-dab99706253a | textbox | Calibrated at
04fbe0f0-18d7-49b7-82d0-ac581199bb2b | checkpoint | Instrument Power Supply
5b2173ae-ef15-5380-b56f-bd7844e43ca3 | dropdown | Supply type | VAC, 2 Wire DC, Other, None
3f4b253c-158b-56f8-b3f7-14bece4d793a | textbox | Supply value:
4d577bd3-6d95-5a15-8b10-48cfd1e23f42 | button | Calibration sheet completed and attached below | Yes,N/A
f161f440-b185-4216-98b6-cc9ad8db992d | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
1629ea98-bdcc-489f-9481-435fe12e32c7 | checklist | ITR-I-08 Instrument Pre-Commissioning |  | ITR-I-08 Instrument Pre-Commissioning |  |  | 5ced7639-fa37-445c-8e50-ce57156c25fe
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
9b2abd80-5840-4242-93db-d41c71599f50 | checkpoint | Checklist items
1de93dc0-5a4a-5ecf-96e5-3e3ada82f5b4 | button | Verify transmitter loop connection - Remove wire on transmitter and confirm at Control System interface | Yes,N/A
4f4a87b2-acf0-51b9-9c1a-3fe190a006e1 | button | Relevant individual control system/ESD loops have been checked and test sheets completed | Yes,N/A
9f759255-2361-4b4d-b2ce-a430f0522603 | checkpoint | Analogue Input:
e59c8de5-9a21-4311-b51b-6be7ce40a56a | checkpoint-no-value | Analogue Input:
4164e952-b628-55cd-b75f-aa2c4676d742 | textbox | Input range & units:
d8d5bad2-542c-5cb5-accd-54a1f4bac12b | textbox | Indication range & units:
e9fb9b16-c86f-4d64-9d3d-a4f900805ff2 | checkpoint-no-value | 0% Rising
75970b5d-8105-5da9-a40d-b2cfdbe844af | textbox | Input Signal:
cbc3cab2-d7c4-5b1e-8794-dcc21f38642a | textbox | Control Interface Indication:
02209309-951c-42d9-a2b0-2279ce704abf | checkpoint-no-value | 25% Rising
d6556c18-049e-5403-acfd-c86487991a8e | textbox | Input Signal:
ac08c071-bdf1-54dd-a1d1-54adf56993aa | textbox | Control Interface Indication:
843de891-b802-4680-8866-e0ef077819f6 | checkpoint-no-value | 50% Rising
c55a71c6-d3ab-5fc1-b8ee-239c61b6b325 | textbox | Input Signal:
2a763173-8a1a-5f04-9597-18f03635935e | textbox | Control Interface Indication:
76c1c3a1-3f27-4db0-aa59-2f060e84c71f | checkpoint-no-value | 75% Rising
7f52aa7a-a662-5861-b325-06d09def837b | textbox | Input Signal:
5a8a81cc-e72c-594e-a7da-641a85292857 | textbox | Control Interface Indication:
9f0aaf51-a6fe-4c71-8b8e-8bd798ff1b35 | checkpoint-no-value | 100% Peak
20195e35-4e9f-55cd-9dfb-7fdb03b3c5d8 | textbox | Input Signal:
933476b1-ea08-53e7-b59d-c5ee3a79e55a | textbox | Control Interface Indication:
65034cca-0ce4-4eb2-9022-f5e8c79243a6 | checkpoint-no-value | 75% Falling
51a1e175-3060-5ba0-a565-b94b4881f630 | textbox | Input Signal:
1c2aa0bf-c697-58c0-80ca-1a31378be7d5 | textbox | Control Interface Indication:
b0eb862a-f80c-4faa-8fc5-e501ad51189a | checkpoint-no-value | 50% Falling
4f673392-ba14-5802-a029-58303833b0c8 | textbox | Input Signal:
4b279618-f4a7-5d10-bef6-b17ca2e8871e | textbox | Control Interface Indication:
f9cc3ee4-a274-4580-bb01-c421f9ec9fa3 | checkpoint-no-value | 25% Falling
fa643578-db55-54db-9d57-a34c3f5bafb6 | textbox | Input Signal:
39080333-48fc-5885-876b-674f091042dd | textbox | Control Interface Indication:
69e47036-b6a4-47f7-afc1-7caef5c09693 | checkpoint-no-value | 0% Falling
be470454-ce94-5cfb-b1f5-e0dc8761f535 | textbox | Input Signal:
366eb58a-af13-582d-9736-e1eba26055dc | textbox | Control Interface Indication:
e097e85d-7cfd-4330-903a-bd10d2b03bd1 | checkpoint | Digital Input/Analogue Alarm Trip Points
7ad5e831-7807-4c9d-b8ec-49726264cb6d | checkpoint-no-value | Alarm Lo:
f77b7ecc-54fc-561e-8147-79fac2d96f5a | textbox | Alarm setting
6c11278a-377b-5e8a-bc5a-3789a04a09b2 | textbox | Measured Alarm Point
6eee2af9-b436-54c9-955c-8c767643c523 | textbox | Filter/Time Delay
7b3e022d-effb-578c-8a1d-0b01a7df9ed8 | textbox | Result
2d735702-fabc-442d-adb6-cbda0b8d3399 | checkpoint-no-value | Alarm Lo-Lo:
e6f66d50-c165-5b2a-a41a-fc4f1fbb24bc | textbox | Alarm setting
8733da33-55f1-54f2-8cff-184687bd858c | textbox | Measured Alarm Point
ece75955-1cff-53e5-aad7-2bd5c61bc3a3 | textbox | Filter/Time Delay
b99553e6-c8bc-5561-b491-d8b411051617 | textbox | Result
6be6c957-d6c7-4b45-99b9-51a32d58e050 | checkpoint-no-value | Alarm Hi:
80d99dc1-ebcd-544f-9523-c5d687622b60 | textbox | Alarm setting
430edd6e-5de7-581a-973b-79afc1696762 | textbox | Measured Alarm Point
04e19ddf-202e-5ae6-99be-210f8eb50557 | textbox | Filter/Time Delay
36429f64-5c3b-5e5f-a7a0-372ab744836a | textbox | Result
83cf3fb9-5492-4b7c-aad4-629a12c10bfe | checkpoint-no-value | Alarm Hi-Hi:
c7108dc8-91c5-5449-8727-ad4dcf969f72 | textbox | Alarm setting
e027ebbd-3723-5197-8def-5dbb93a24516 | textbox | Measured Alarm Point
75fd7c8d-c406-5112-a15a-7e82964118fc | textbox | Filter/Time Delay
dadf751e-9b7c-550c-8d56-1a36be82926f | textbox | Result
edd80f6b-38bc-4ec4-86e3-756e0712dc57 | checkpoint-no-value | Control loop set points correct:
eb2594be-ba35-5f00-ba05-219cfba1dfb3 | textbox | Set Point 1:
433fcf49-8f29-5b4d-9b51-e6c9ab5f0b44 | textbox | Set Point 2:
a3d804f6-3084-5c54-845c-afec09f4edbf | textbox | Set Point 3:
78182109-21e4-59fb-aee1-34c8d21c500e | textbox | Set Point 4:
25e6479b-2e80-48d5-be65-2c88a2c20744 | checkpoint | Startup, Shutdown and Override functions
62623f92-3e27-5bbf-b7ca-64cca4738ef3 | button | Control system graphic display | Yes,N/A
92776563-2e22-5318-9875-a9cc5779aa87 | button | Control system point display | Yes,N/A
fb970c56-ebd7-5c63-b50c-c95acc303b18 | button | ESD graphic display | Yes,N/A
33049592-28cf-5745-828b-00a67e1ef762 | button | Alarm Recording and Text | Yes,N/A
0e577e02-0956-41ce-b607-726e8a650bf3 | checkpoint | Additional checks
67617b44-316c-55e1-b491-3673356b4a58 | button | Control system display and alarms are correct as per control functions | Yes,N/A
d81d0e1a-ce16-5165-9f45-b8e2a7974388 | button | Transmitter fail direction and burnout are to spec (Upscale/Downscale) | Yes,N/A
7feed3f2-1e2e-5e30-ad19-43c57e95f617 | button | Switch action verified, including power loss | Yes,N/A
a27b22b9-f951-5c69-91ca-7dce55839236 | button | Drawings, documents and As-Builts scanned and attached | Yes,N/A
5aee35b9-ecc6-4bad-ba10-138cd0a960de | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
1d78fddf-fd2b-46c1-bf3a-25fd9a0f4251 | checklist | ITR-I-09 Commissioning Instruments |  | ITR-I-09 Commissioning Instruments |  |  | 856f95fb-137c-4b63-bf4b-ef2e81461706
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f5e1b227-d30a-4423-a96e-0a10bf869c07 | checkpoint | Required Data
11569a38-46f1-5f78-a29c-5e681b1809cd | textbox | Instrument range:
208cebbb-a864-5db0-b2ae-ce78f5a8ade6 | button | Installation complete | Yes,N/A
475db32d-6c63-563d-aeaa-d74f8681cca9 | button | Point-to-point | Yes,N/A
96c1e3f6-510b-5dde-9f21-6b3f8321014f | button | Haz. Inspected | Yes,N/A
64be49d3-e7a2-53e4-95fd-b247131a9e90 | button | Tag correct | Yes,N/A
07721343-ccc9-5a52-be10-854e8933ab92 | button | Hook-up correct | Yes,N/A
088c749c-660b-470c-921b-7d9d668e2c44 | checkpoint | Alarms & Set points
a9c5e9cc-6bb4-4e59-aba4-2a67bc1fcdf4 | checkpoint-no-value | Alarm Lo
0acf13c2-41e3-533b-9a13-edb016568046 | textbox | Activated:
f6525ac1-6c13-4e6c-8fb2-535028d2a5c2 | checkpoint-no-value | Alarm Lo-Lo
477fc033-a107-54bf-acc5-27c13e880a74 | textbox | Activated:
4a4131f9-c2d1-48bd-885b-ce97f2866b6d | checkpoint-no-value | Alarm Hi
70391dba-f211-50c9-87d0-833df64590ce | textbox | Activated:
9c85d819-6989-4cd9-9ebf-41324e1c835f | checkpoint-no-value | Alarm Hi-Hi
4e3eb6bc-65ad-5870-b2e9-3e7af224c4e4 | textbox | Activated:
dcbc942e-afcb-44a5-82c5-8cefe1fe8136 | checkpoint-no-value | Set Point 1
f0964f5a-801b-5d72-8d1f-cb93e67f8b5c | textbox | Activated:
e1de1ced-efc5-452d-92f4-a0c37f4c5c4f | checkpoint-no-value | Set Point 2
49911ba9-a8d0-54ea-83f2-497bde88431f | textbox | Activated:
f1835b4e-170b-4fd5-bc72-1b33deba1cdd | checkpoint-no-value | Set Point 3
19e304bb-ff98-5e03-b707-8c2469cf781c | textbox | Activated:
e1bfe6ea-3a09-428b-ac6e-d3afe3d3fc83 | checkpoint-no-value | Set Point 4
89ba7c8d-5df9-532c-a4d1-bb7963a303a3 | textbox | Activated:
1fba16f3-4c6b-4b13-9e8c-29b4cc81cc69 | checkpoint | Calibration settings
31eab0d5-40e7-5aad-9c03-021da99a368b | textbox | Zero
7bbcd1a0-9dfc-5fdb-a7aa-e274b86f2b10 | textbox | Range
260038f7-30d8-5e56-b497-8b7cec945021 | textbox | Other (Specify)
001091c4-a5d3-4824-950c-46cac9f2a0fb | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
dfa832f3-b88b-4da6-b1c0-ee102444eb8b | checklist | ITR-I-10 Cone and Thread Tubing Installation |  | ITR-I-10 Cone and Thread Tubing Installation |  |  | 471de089-88c5-4621-980b-2146640f5f27
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
089ff366-8db8-4a2f-a0de-3c836a65deba | checkpoint-no-value | General Data
836862e4-2ee5-5480-be92-2e390beb2c3d | textbox | Location:
f3987e3c-e071-53fe-adef-d6961dc1dd05 | textbox | Duty:
52227d67-48d3-5477-93d4-be69bceb615e | textbox | Reference Drawings/Hook-up drawing:
817b5bcb-636c-5873-8584-d3da6a0f478e | textbox | Related instrument tag no:
67c3a7fa-1af0-5757-a6db-9cf3cdb6bc93 | textbox | Tube diameter and wall thickness:
641085bb-117e-464f-aef6-c16cb3c51a75 | checkpoint | Cone and Thread installation - Stainless fittings
b198dca1-5fe8-5c0e-bde8-ca01afc7022c | button | Correct thread compatibility and engagement | Yes,N/A
5040f0d8-5bbd-56b0-9659-9070f2103d00 | button | Check fitting collar prior to connection - 1 to 2 threads visible at cone | Yes,N/A
5d2f36de-beda-569d-ad2d-87bbc5713d15 | button | Tube installation follows the client specification. (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables) | Yes,N/A
25a037c6-87a9-56f4-a344-905158bbc784 | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
3825cff5-9492-5b90-b0fc-62d6e4a2fcba | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
272724d7-16a8-4bd9-9ce8-17e72511950a | checkpoint | Cone machined face. No defects, lines, bumps etc.
e156b36f-5462-50d1-a4e8-8a4a308cba8a | note | Attach photo of cone and thread.
4c00f4e8-8964-43a7-8ad7-ec59407be98f | checkpoint | Thread cleanly cut, de-burred and cleaned.
7147c5fd-c45f-5907-b92a-324fcfc8f2ca | note | Attach photo of collar.
2ae41ab5-260e-5980-b4ed-81892b0b990d | button | Lubricate collar, cone and gland thread at assembly to prevent galling as required | Yes,N/A
79ed5d6a-5032-5aac-aa19-0019a8086902 | button | Correct Tube nut used for the right sized tube | Yes,N/A
2effeb49-3819-538d-b71c-963916d664a9 | note | Ensure No thread tape or sealant are used on tube nuts
ce29034e-276d-5cae-b28f-fcb5f94165e2 | button | Tube fitting hex torqued to ensure correct tightness, marked with pen | Yes,N/A
3bfd23b0-e15f-5e78-9152-eaa2d2c5611b | button | Ensure Weep hole is unobstructed and clean | Yes,N/A
7495e682-eb45-53d2-a53b-950e4f3b9c38 | button | In service leak test performed and passed | Yes,N/A
5e3c8b4b-74ca-5a06-b759-70347c9eca44 | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
4b98cd58-41d3-4cb9-9489-3945c4e4c18a | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
be1da43d-d508-4495-a76e-2eea57b37bb3 | checklist | ITR-I-12 Telecommunications Equipment Panel |  | ITR-I-12 Telecommunications Equipment Panel |  |  | dcbc2d56-3b12-458d-a0cb-cbd35846eba7
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
48345094-72bb-4b1b-8a46-ab4ebbaa79bd | checkpoint | Telecommunications Equipment Panel
37c3f6fa-c7e3-54b7-851b-9f8084288ee8 | button | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings: | Yes,N/A
6f7b694b-5c62-5036-97a8-52843c4d1f9a | button | Check tag number is in accordance with Telecommunications Equipment List. | Yes,N/A
278fcbde-ff47-5571-a008-fc889d0597e4 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
e20ada87-7a7b-55e8-a8d2-d3e9a9948a3d | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
8645b65c-00f3-5997-b36b-8183745a6826 | button | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified. | Yes,N/A
636fd1fd-6e63-55d5-8793-2749a7f71c6d | button | Check panel air vents are clean and free of dust and dirt. | Yes,N/A
fabb5c44-d645-5715-9481-4d85d352d262 | button | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
8b506adf-59ea-5070-b47f-7f8a9601d9e6 | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
b7b7e247-73fd-53cb-b0f7-d7cdb6bfaeb5 | button | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
413c18d4-968e-5abd-af56-b9749f2abac0 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
7525bf9d-3a4a-53c7-b22e-a73d8ba6d585 | button | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel. | Yes,N/A
b68c1b6b-f6e0-52ea-8303-b61bf60e10f4 | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
d1b9edc9-2800-5b42-aefb-047bf71f0b3f | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
8a2633dc-1acc-4067-8c0e-f875e3f950dc | checklist | ITR-I-13 Temperature Instrument Installation |  | ITR-I-13 Temperature Instrument Installation |  |  | fa90151e-8adb-489c-900d-39185d8ad5cd
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
269d7c43-e589-47b2-ab83-07f96e319221 | checkpoint | Temperature Instrument Installation
6a6bdcdb-494f-599b-9b9f-d89869425c3c | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
715a5f0c-48f7-5f7b-acdd-b254c67ea1c5 | textbox | Type and Size:
60baa098-0025-5341-a219-ea8879e47a50 | textbox | Make and Model:
c74cc3c1-ee96-5f1e-bf78-5bb0d69f379d | textbox | Serial No:
23740f8e-a299-5c2f-92be-2f463fae54ef | textbox | Instrument designation/equipment no
79709bc0-83d2-5a7d-8c45-9b2fe9849f4f | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
8559adf1-a411-52c4-9901-05376f205e1a | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
72f06700-4dcc-5d3c-8eb9-c18f242564e0 | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
571bdeb5-9ddb-5a10-b0c8-7eb0c5c9267f | button | Vent lines are directed into a safe area. | Yes,N/A
f95db7ca-f369-534e-9ab6-bb92a91e228a | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
9815721e-ce0c-5258-8f1c-a10b0509a5e3 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
6f680931-beb1-5da6-8c22-36432028e0cb | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
e03a90c9-d148-5816-8969-8c7f0f6a6795 | button | Instrument earthed in accordance with project specification. | Yes,N/A
2c01a3bd-2cfe-55bf-b4a5-ae6723fdca15 | textbox | Calibration interval
592a2cfd-d829-5964-951a-b00b81b19245 | textbox | Calibration method
804e6ffb-28cb-583f-bc71-adf74899b223 | textbox | Calibrated at
16710066-7743-4181-8802-a7c56d71bb99 | checkpoint | Instrument Power Supply
04d6adec-eb9f-5e98-9d9b-cf37f67d071c | dropdown | Supply type | VAC, 2 Wire DC, Other, None
c7ec3276-dfdf-51b9-b093-6965b353429e | textbox | Supply value:
2255c745-7d00-5c63-b9d7-4ca1b119a296 | button | Calibration sheet completed and attached below | Yes,N/A
0d8a0f2d-dae1-59b9-a94b-19f3a33ee9a6 | dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
f07afaa7-7e0b-5479-b609-335cc96c37af | button | Thermowell details including flange size are correct in accordance with the specifications | Yes,N/A
912625b7-0780-5443-9c6c-8773ce46873f | button | Internal depth of thermowell checked and recorded | Yes,N/A
0d8f6f95-5ee7-51b7-b6a5-ad96e34891df | textbox | Depth:
072d0694-1563-5414-9da7-6e7d2daf6e39 | button | Bar material and tag number stamped on thermowell flange/exposed surface | Yes,N/A
8aaf6f40-21b3-5882-a43e-28fb33a115ab | button | Thermowell CE marked | YES,NO
11270d38-ed63-56b2-b9d6-581d8ce4e39e | button | EOL resistor fitted and correctly rated where applicable | Yes,N/A
c406aeea-d4d1-46db-bbc5-4917115f1e7d | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
8f5b5c42-4253-41b4-b3c7-dbe0c719135e | checklist | ITR-I-14 Flow Meter Installation |  | ITR-I-14 Flow Meter Installation |  |  | 24f19a62-6f0f-4170-8205-2a6e01f88491
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
620241e3-1c47-471b-936f-6df13f1b2994 | checkpoint | Flow Meter Installation
d2d13fc9-3803-54b2-93d6-df97ab3c33ba | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
548badd8-87a3-5dad-a5cd-03f39566d434 | textbox | Type and Size:
11472ea6-2df3-5976-aa68-c498228bf7cc | textbox | Make and Model:
908e16dd-0d2c-51af-8ec5-df2a8cf656d8 | textbox | Serial No:
c555d079-ae50-53a3-9e82-bfab50e58967 | textbox | Instrument designation/equipment no
aa73866e-8a29-54f3-ab21-51edca127972 | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
4564e293-8fa5-5531-8b3b-5cce8db5f0c3 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
353b9521-779c-571d-841d-9c8fb16418f4 | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
2facc962-fd2b-5f9a-b69e-737f9122d2ab | button | Vent lines are directed into a safe area. | Yes,N/A
c70e45c7-a001-5699-8f83-b647d33cc78d | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
b4fabc78-d67d-580a-af72-0e4c2a2496bb | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
959b7e64-d96e-5a73-8173-6f8fa23c60cf | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
8b3056bc-d0d8-511e-9adb-9d40645d78f5 | button | Instrument earthed in accordance with project specification. | Yes,N/A
c3b4f328-5e82-5731-bc7f-8b9f592b1112 | textbox | Calibration interval
64ec83b1-d563-5cab-9f79-1ce6c6d8fc4c | textbox | Calibration method
7098b1f4-f943-53fd-99f6-2eb107aa76d2 | textbox | Calibrated at
f07d7cf5-c643-4b49-8d8c-2556a00343ea | checkpoint | Instrument Power Supply
7bd52285-fc00-5e8d-a5de-61e9106151d2 | dropdown | Supply type | VAC, 2 Wire DC, Other, None
3cfe182c-1ef5-57f4-bdc5-51ff69f8c2f1 | textbox | Supply value:
b4186f24-204d-5272-a2d8-9ea829ceea10 | button | Calibration sheet completed and attached below | Yes,N/A
b9b664e9-58ec-5977-b12c-1d41885046db | button | Ensure location and tapping point is verified as per P&ID & location drawings | Yes,N/A
7759037b-7794-5cee-9615-bde34091a57a | button | Ensure direction of flow is correct with respect to flow meter | Yes,N/A
e55aec1f-c8f3-5784-b8c3-e225154cbfae | button | Check mechanical clearance is adequate for installation of flow meter | Yes,N/A
a50f7f8c-d881-5ce7-8c86-368a2f2e9090 | button | Verify type and size of gasket is correct between process line and measuring unit flange | Yes,N/A
1df40803-fe08-59e5-8bbe-b1cb7bd44874 | button | Ensure correct nut and bolt grade and material for connecting unit to process line | Yes,N/A
6d972da0-e3dd-5ca8-8a25-e68b3843f381 | button | Verify display/cover is oriented for ease of use for operators and access for technicians | Yes,N/A
910c7ab2-36df-4399-b514-1587545cd33d | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
a777718c-a3c9-4b0a-b8c4-58c4649f0861 | checklist | ITR-I-15 Pressure Instrument Installation |  | ITR-I-15 Pressure Instrument Installation |  |  | aad7b6a2-011e-41fd-b70e-6f7fddfd289d
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ddb2fcd0-e046-4404-afe8-4ce03c558f7f | checkpoint | Pressure Instrument Installation
2b746ea0-3d6d-5798-956f-1deddcb166f9 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
ae1eaf31-2cb5-5c75-9f47-ddebda2d2c1d | textbox | Type and Size:
d5394e3c-ab3a-5a07-bfaf-f12403a171c1 | textbox | Make and Model:
d5afc151-2500-5874-9935-92361d79f951 | textbox | Serial No:
6cccb1a4-4c1e-5e20-8687-c517f0bfeab1 | textbox | Instrument designation/equipment no
2a8bff10-0d02-5be4-9545-89a16b264dc0 | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
14883db8-72ae-5a2a-b137-dded47c36d17 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
925a9563-5924-5340-b5ac-fb4f4fa03ba7 | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
f6310c26-ab94-5547-86c6-f694b9e7ca9d | button | Vent lines are directed into a safe area. | Yes,N/A
7e573cc6-68e4-5684-bca3-2dad3f02cbe5 | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
6fec3d3c-2dc6-5fe7-8c06-2c4a96a28924 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
da552dff-d2d7-5f68-8d26-b753bcbd0c94 | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
94657789-e4fe-5c57-b3f6-cc2ccb55f052 | button | Instrument earthed in accordance with project specification. | Yes,N/A
5293e854-1f81-5b3c-8f6c-305a5bfc03fa | textbox | Calibration interval
c0866615-fe84-5730-9710-5681f7ab0935 | textbox | Calibration method
98afce03-a0b1-5664-888c-5718de546875 | textbox | Calibrated at
77ad5b55-6741-4db8-8335-50d2d7dba2c2 | checkpoint | Instrument Power Supply
99ded8a4-8bce-5140-9d21-78c3730e315e | dropdown | Supply type | VAC, 2 Wire DC, Other, None
e1b04bb0-0a75-53de-a7e4-729b40c7f409 | textbox | Supply value:
ed7b055a-0567-5147-a68a-e8fd8a3625b4 | button | Calibration sheet completed and attached below | Yes,N/A
a9270fab-8e53-55e8-99f1-c8ea2fc0fe37 | button | Instrument mounted as per hook-up drawings | Yes,N/A
ebc5b7d7-7ed5-5a3a-a36b-20e9f6e4ddfa | button | Air line/Impulse line are correct material to site specifications | Yes,N/A
e2507f02-836f-5457-b30f-8d35db4fedea | button | Air line/Impulse line are routed tidily and as per hook-up drawings | Yes,N/A
30955280-5bd6-5ae6-8a04-17d70e1df30b | button | Correct bolt size and material/grade used | Yes,N/A
f15d2a76-8895-5c86-9aa4-176c290d53cb | button | Local indicator is mounted and easy to read, easy access for technicians | Yes,N/A
b4969649-ff14-5eb7-b1b0-4ad222e8c47d | button | Instrument and tubing are adequately supported as per drawings | Yes,N/A
01d03224-9ebc-54ed-b088-f0f8e9f73c81 | button | Isolation valve installed | Yes,N/A
6d41ae6f-5122-40e3-8238-029f5eb3ded7 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
a0cf32cd-9bb2-4af9-bf20-037c874f18df | checklist | ITR-I-16 Level Instrument Installation |  | ITR-I-16 Level Instrument Installation |  |  | 220531e1-4822-4c65-b474-bd7de74c2afe
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e369d01c-ba1d-4be8-9bbd-f97f055b1e98 | checkpoint | Level Instrument Installation
4f5632f8-8a40-5293-ac07-ecfdb8b72c83 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
10ba450c-1816-573a-9794-d4718d9cfbe6 | textbox | Type and Size:
c6330cec-42ee-5957-8dce-e9e3e971dd9b | textbox | Make and Model:
cc02d3b6-59a9-5eba-85bf-a7ba8bc9d9fa | textbox | Serial No:
e16f8068-e810-587c-9e80-660ca711a5e2 | textbox | Instrument designation/equipment no
a94a7761-d7cc-5fc1-b553-1885444a2ea7 | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
5bbdd757-9161-5919-84a2-c33dbbfd9f98 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
7b38804c-b656-52fb-ae93-79a50b06b6cf | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
f7ab8c31-e516-5c20-9393-201945b128cb | button | Vent lines are directed into a safe area. | Yes,N/A
61f504a5-8b36-5b41-a758-6cf2217685b2 | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
d143451f-bb26-532a-9337-b3f0a0dfa302 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
65a6137a-b1ff-5ef9-bca8-157f9677a499 | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
34f0b00d-8f3b-54ed-9d8d-d4b7c2b70198 | button | Instrument earthed in accordance with project specification. | Yes,N/A
956bbb10-2219-50b5-851e-89dbcbbcdeea | textbox | Calibration interval
18dc4966-6e9e-5c92-89ca-423accc7b458 | textbox | Calibration method
8de81f63-2e3c-5b56-975d-69f143b114e2 | textbox | Calibrated at
dcec1d94-3129-4c71-be45-1b0dea62c37a | checkpoint | Instrument Power Supply
97581e84-7ac4-5664-a87c-981a244bef35 | dropdown | Supply type | VAC, 2 Wire DC, Other, None
b084c983-b7fc-5bad-930f-2649dabc647b | textbox | Supply value:
10c88007-9913-513a-b5cf-b8551addcffe | button | Calibration sheet completed and attached below | Yes,N/A
b31225a3-9c7f-5bd7-a15b-533f9657e654 | button | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
87ae1bc3-a239-516a-860e-54422c677f8d | button | Level instrument mounting equipment is adequately sturdy and correct materials used | Yes,N/A
84eee38c-3c22-5190-a8eb-74a58f1e37fc | button | Bolts and studs are to site specification | Yes,N/A
1cf16dfe-10e6-557c-aa2f-61eddf1aa74f | button | Ensure location and tapping point is verified per relevant drawings | Yes,N/A
fefb07fc-db0c-5775-bfca-b6f57fe46003 | button | Ensure gasket and studs are used as per specifications | Yes,N/A
430623ad-817e-5f4b-aaa0-1e2cacc7085a | button | Verify contact type sensor probes are installed without any resistance | Yes,N/A
2455155e-73a6-59be-8667-b0673d38ce03 | button | Verify antenna/source are installed correctly | Yes,N/A
0764ce1a-b3c7-5859-9b4c-69ad9d2e5b35 | button | Ensure display is easily readable by operations and access is easy for technicians | Yes,N/A
13a49aab-a168-43e6-a5ec-1c58c5aec42e | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
d7249779-f2dc-4b1f-a3f2-e9fd4bddccff | checklist | JHA - Job Hazard Analysis |  | JHA - Job Hazard Analysis |  |  | d559fd94-7c88-4e7f-89fa-320543db2fbc
367b959a-31c0-486b-9798-c8074ef29bd6 | section | Job details
844716ee-598d-4e93-8098-c5a1b98194db | checkpoint-no-value | Job details
d73afacd-fc5f-53b9-a07d-f675a0b9e31a | date | Date:
cc7d5829-8af6-582a-a833-dc29e4955ba7 | textbox | Permit No.
0209e583-f13d-565d-a8c7-3ea6a1ca436e | textbox | Job No.
ad0ecca4-9f7b-593d-8c73-84473675dd96 | textbox | Site
0421a179-094c-515b-b75c-9029c84465bb | textbox | Activity Location
cbfad55b-10fd-5191-b98b-8378abfa80d4 | textbox | Asset:
e0cc8654-ee08-5185-8a03-a27d395343ec | textbox | Work Details:
4912e8dc-cfe0-4e53-aa01-c3309f10f9a4 | section | Prompts for Hazards - Mark all that apply.
7c8b2a7d-4947-4fd4-84ca-21e2505358ca | checkpoint-no-value | Prompts for Hazards - Mark all that apply.
d861a012-41d8-5336-a006-0601b1e9336d | tickbox | Sparks/Open flame
0006f2e0-1147-56ac-b869-13783cb35735 | tickbox | Disabled safety device(s)
b23664ec-1bf7-5714-af07-a84376bd9740 | tickbox | Uneven surfaces
c8183bb8-9b3f-558c-9cec-17ed696cc6a4 | tickbox | Fatigue, over-exertion
6b6e7932-20a0-5cbd-bfe4-4c2b9a45256a | tickbox | Crane movements
c6734840-900b-52ff-9a98-cfcc11ada84a | tickbox | Moving/Rotating parts
5a745015-b2ae-5e18-a5df-ddcd2350057f | tickbox | Remote area, working alone
e0e71479-32cf-57e1-990a-c8e186abde14 | tickbox | Conflicting work/SIMOPS
61e26cd4-97e2-5d6f-8270-6a10a2a9c8f3 | tickbox | Electrical arc flash
3c4b13e7-3980-5666-8659-e6fccb457644 | tickbox | Sharp objects/materials
1bb7aac1-f5cf-5881-adad-6cca616fef38 | tickbox | Restricted/Difficult Entry/Exit
13909cae-9c7e-5583-93d2-bcdcced8576f | tickbox | Overhead obstacles
64e032c9-2892-54a5-84f9-93cd0676e25b | tickbox | Ignition sources (other)
7d26ef84-f130-5e0f-8b56-aef1502cde24 | tickbox | Access/Egress
b8704016-9150-5d92-830d-ddc551b2ac95 | tickbox | Water body
020ce0f4-b45b-5a7d-acb3-39b14bf06aa4 | tickbox | Live equipment
d1a4dfcb-da0c-5158-94e7-86784ec6a6c7 | tickbox | Slippery surfaces
e9c25dd6-02a3-5cc2-8499-8a6f2b7e7225 | tickbox | Suspended loads
67a205f6-6314-5112-9625-e5585067dccf | tickbox | Hazardous substances (chemicals)
450ef1b1-30c4-5bae-a134-14f6d6b4faa4 | tickbox | Use of non-intrinsically safe equipment
a147d81a-bcdf-570e-b635-4d465d95d593 | tickbox | Weather extremes
b99477f9-fa30-5fcf-b9e1-ddff56a9531f | tickbox | Moving vehicles
a6d727f6-75b6-5b4d-b88e-e4d539f077ab | tickbox | Task related noise
678d2a9c-c647-54f0-b0ba-35c3ee8d9bd8 | tickbox | Engulfment
78b5300f-03cb-5907-a348-92f27654767d | tickbox | General waste
0de12bb5-1ab4-51e0-bcfc-7608c96a062d | tickbox | Hazardous waste
84c782e0-72a5-5ea3-adf5-811e06bece92 | tickbox | Hazardous/toxic substance, fumes, gas
417942ec-1ebe-590e-b693-347aa4adb403 | tickbox | Flammable materials - Gas, liquids, solids
aace0207-0b95-5309-b235-af35918e9575 | tickbox | Reduced visibility, lighting
fac86e44-c910-5401-99ba-c8ab87a551da | tickbox | Electricity
87fa19db-3704-5f97-bc5a-a4e515ad453b | tickbox | Static electricity
6208f132-8822-5832-800e-63afc0b3f656 | tickbox | Work at height
3fe2f8fb-db5d-5973-8cfa-061f978f8989 | tickbox | Underground services
4fb6d000-067e-5077-b2d6-4834b8469f12 | tickbox | O2 Deficiency/Excess
1641a091-59f5-5186-b466-09e3e83133e4 | tickbox | Temperature extremes
25571961-00d0-52bf-b936-8c4edc984165 | tickbox | Heavy objects
b1f4da6b-56bd-587f-ac6b-3a12dfee2876 | tickbox | Radiation
e9ee4ab2-df02-5053-844c-21e2e0c1e9ab | tickbox | Potential energy - Tension/Compression
d8b2bb0a-e364-55f3-a787-6f37aaa00fd7 | tickbox | Flying particles/Dust/Objects
e90f856f-6dc7-5c8a-a930-f2ec427b06fd | tickbox | Vehicle entry
001c08fb-252a-5692-857c-c9895a909900 | tickbox | Exposure to process temperatures.
f2e920b0-d4e4-4c56-aa65-a494ec5e98c7 | section | Prompts for Initial Consequences - Mark all that apply
c8a97056-9986-44da-9318-1dacb4b6bacb | checkpoint-no-value | Prompts for Initial Consequences - Mark all that apply
ada79b0a-b326-5fa2-8f70-9d6092f64061 | tickbox | Falling/Dropped objects
2e66b34d-bd2d-5335-8071-20ea4f2865ac | tickbox | Fall from height
2de6ffd5-32bf-56ca-a019-849d9aa52f1a | tickbox | Trip/Slip/Fall
33372931-1e12-5e55-a4ef-36b5513d7c43 | tickbox | Gas release
23aa8ea6-e0e4-57e5-b0f0-073db18251ca | tickbox | Pressure release
6e32f2c1-06aa-5217-9728-ba384c4f230a | tickbox | Struck by object
05aad929-efd2-54e7-b4ec-634cefd1b623 | tickbox | Exceeding tool limits
3fda1d54-299a-5da7-a1e1-087cb4ce92b8 | tickbox | Overloading people
6bd42cdf-f11d-5537-a962-c13858b9f465 | tickbox | Unplanned shutdown
ca1946df-e546-5caf-8c95-eee042a5ae8d | tickbox | Exposure to O2 deficiency/excess
18e4d98c-62cb-5bdc-9517-10a7231c72c9 | tickbox | Exposure to hazardous substance
114171ae-9b37-596b-981f-1e816cd4c989 | tickbox | Entanglement
c334b135-b764-53f7-8593-404a1305cdb6 | tickbox | Flying objects
86ce07e5-2bdd-5d9f-b17e-f91fc6d6b5f0 | tickbox | Loss of control
71803041-0bb8-50f0-a837-a46e144900d0 | tickbox | Loss of containment
ecc82886-d3d9-59eb-8f7c-9c9dc40b7d1a | tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
86fef76a-ae81-5cf6-92c3-454bb21598a3 | tickbox | Loss of structural integrity
f1a33d27-f430-56e6-8c06-e65cbd74f5b6 | tickbox | Equipment failure
87ae9c7e-c018-55f3-ab02-7ad812185dd5 | tickbox | Uncontrolled ignition source
6730112c-e576-552f-a986-7cad538b1e4d | tickbox | Collision
b5932100-0408-50a7-8b45-fa670d7654eb | tickbox | Ignition/Fire
38d134ed-2ba9-5359-81a3-89f47c08e285 | tickbox | Back strain/Injury
83c22e6c-aa5b-50e7-bb47-73c688ef78a4 | tickbox | Burns
a4c40c53-c415-53ed-8adf-aeb817b2b1d4 | tickbox | Heat exhaustion
52248038-2d25-41e5-b09d-8075ead64394 | section | Initial controls - Mark all that apply.
b56aa456-fb85-4e8a-aef4-d4706d56a553 | checkpoint-no-value | Initial controls - Mark all that apply.
b5f8375f-f7a4-52ae-9e44-82e266da57b4 | note | People controls
40ec1de9-37c0-5c52-8083-100630cc2f63 | tickbox | Safety/Fire watch person
0bb56a3a-4f2f-5989-92e4-86931a0bd06a | tickbox | Barriers/Flagging
6c652daf-043d-53da-9aca-a89985c4d2fb | tickbox | Warning signs
cb795045-8821-5d91-964b-6ac7cefc6f05 | note | Equipment controls
ba172de8-1723-5ca1-bebf-3dfd24efa46c | tickbox | Master tags and locks
8cf662b1-85d7-53ac-b364-13d2aa6d7706 | tickbox | Scaffolding for access
b486d1b5-6711-5a68-b9fc-67df08b45e11 | tickbox | Radio communication
c754a3b2-2aff-50dc-84da-5ba23831ffcf | note | Environmental controls
e7a89826-bfce-5f83-ac38-3eabbf0e8a5a | tickbox | Ventilation
fce464d1-b598-5b66-ae11-263db4aebc6f | tickbox | Lighting
b933bbf9-8111-5e52-9aca-eb7e6832d865 | tickbox | Gas Testing
64d8dfb8-8a88-5ad3-98f7-4232822553b5 | note | High risk controls
03b5a920-941c-5b28-8f65-e46882f34340 | tickbox | WSCS Work permit
f5825dea-75ea-5bfb-a09d-5fd26f9f9f60 | tickbox | WSCS Certificates
ea53838a-de12-5e6c-8b84-c0e3f69a039e | tickbox | Critical lift/Fall protection plan
4c29b0e2-4762-5073-b791-17bf36a16d4e | tickbox | Specialised PPE
6f057333-7556-51c9-904e-4dec9439a180 | tickbox | Spill kit
f631a6b0-cc4a-5ae5-b73f-2ec9abbba9c2 | tickbox | Fire extinguisher
0b42f5c6-b5ac-4e18-9128-b2c2c1796e55 | section | Signatures
28d675b5-d597-454c-b6ff-7feed5edfd07 | checkpoint-no-value | Signatures
58f539bd-a904-4587-90b9-e5df637863bd | signoff | Applicant signature
ec5cd9b2-f61b-47e0-8d72-83777ba90ddf | checklist | JHA - Job Step |  | JHA - Job Step |  |  | ad344645-90c9-4f9b-ad5e-2c2f708a5311
5811ffb5-94b6-455b-9ecb-d504990e1de3 | section | Task Step - add task step for each individual task
01d3089f-c034-408d-9767-2e5d9e3d0b09 | checkpoint-no-value | Task Step - add task step for each individual task
9386b4d6-9569-5447-a7ed-183a2fed9e54 | date | Date:
dbc4f1e5-f9da-5ddc-bb62-3186ba53fc9d | textbox | Task step number (eg. Step 1, Step 2 etc):
54bd3e80-8181-546a-acad-09aa938e4012 | textbox | Task details:
d4efd8ce-ff70-5741-a854-07a3ac049c3b | textbox | Hazards:
ba7e3b31-f0b1-5728-bf3a-a54b8bdc520f | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
e2113dac-a748-5fb5-ba8d-1f0d5943835a | textbox | Potential consequence:
7c491d01-adec-5adc-8091-d4bfcc3b63f0 | textbox | Controls:
88e33cc3-5e88-5cbf-85a7-c6b3fa158aa0 | textbox | Recovery steps:
cbb5bde6-8396-539e-a371-8f0bc93b8566 | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
14b36b3e-da59-4ea5-bb45-f099152c6acf | checklist | MSDS |  | MSDS |  |  | 1033c741-df35-48ad-bd91-6eb6a279b2f3
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6be55d6f-996e-4484-a2be-155f9601b6e8 | checkpoint | Please Upload MSDS Sheets
eae56ce8-f60c-48b3-a1f3-94a5e76eb8f6 | checklist | Record of Inspection (ROI) |  | Record of Inspection (ROI) |  |  | 892de636-adda-4d83-81d3-0d95429de34b
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d20643be-2e4b-4e04-8679-f2860bb4aa45 | checkpoint | Please upload Record of Inspection here when complete (ROI)
bfaa09ee-76ae-4093-bc22-0de62d023e78 | checklist | Test Equipment Details |  | Test Equipment Details |  |  | 8f0d9cb0-2552-454c-aeb8-d0ac0f120918
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7049c5ab-7e9a-4fe6-8e93-3b8888099745 | checkpoint-no-value | Details
c72be79d-3a6d-54d6-b55a-32929cba9523 | textbox | Make
500a2cb1-f22d-5a13-839a-cdf6f614f9d5 | textbox | Model
f0805bdb-05aa-53ca-adde-c0465669dbb4 | textbox | Serial No
559d358d-ff53-552f-ae29-05742d970f31 | textbox | Calibration Expiry Date
103934cf-9252-4c42-8881-ff6d2e1d212e | checklist | Toolbox Meeting |  | Toolbox Meeting |  |  | 4f8e9312-b166-4258-a0c0-11e52446a47f
8e06c923-cd64-417e-a061-6cadda90b587 | section | Toolbox meeting
03b7ee45-9925-4ee4-86c5-e6dc6f27ae99 | checkpoint-no-value | Toolbox meeting
6d0e949e-139b-54bc-ba83-a89b17136bb8 | date | Date:
137e8e51-5225-55dc-a330-2c2862083aa7 | textbox | Meeting location:
495f191a-011f-5006-980d-f33f3d063ae4 | textbox | Meeting conducted by:
500c9feb-5a7a-5823-b477-bd5c14a64efb | textbox | Meeting attendees:
cb21558e-ef12-55dd-8859-cc0660420e3d | textbox | Today's work scope/Hazards
7faa4d02-7838-5234-866d-ec555493f7ea | textbox | Hazard controls:
3aba7a16-51d8-4b21-aa89-5931ec544c31 | signoff | PICWS Signoff

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
6f32d1d7-07ca-42af-88a7-a2d1167c2581 | checklist | (TEST) Checksheet - Version 1 |  | Checksheet |  | 1d64103a-f7b4-43ce-ad9b-d9dc1acc42a0
83f9105f-6662-422c-aeee-17fdd3d69659 | section | Details
1275073e-0aa1-45e5-b263-5d788f45024e | checkpoint | 0%
96c47a0c-6dc0-5460-8529-3e8f3d395774 | textbox | Range
f605261c-f21b-5f56-b9e4-c7a201e0db50 | textbox | Expected mA
c3905969-751f-5b21-8c0b-0f636b9b47a5 | textbox | Local Indication
78ec6ba7-cef9-5fd7-ad22-0ca9d7bc8bc0 | textbox | As-found TX Output mA
34eb8f83-5830-5cd3-b8ff-b5331fdb30e6 | textbox | As-found TX Output
e602c40c-5451-54f4-9ced-d5384e195431 | textbox | As-found TX: Error
f918e7ec-a34f-5102-aa38-a26bdac2176b | textbox | As-left TX Output mA
58e41aa1-6d7f-590b-8618-512fdedc147d | textbox | As-left TX Output
060087d7-0a4b-5c4a-ba7f-f1d6792ed57e | textbox | As-left TX: Error
5052d13d-08f7-49f9-82e7-21779b7c1967 | checkpoint | 25%
c7f1991c-a653-5a88-b2f5-5a43e512e7ea | textbox | Range
970c5da6-a77b-5a89-bc91-84ecd914bb67 | textbox | Expected mA
18e181da-2860-580d-99af-3a8283d9f922 | textbox | Local Indication
8be01080-4085-5fe1-8d89-ab104c610292 | textbox | As-found TX Output mA
17f9fe53-6c41-5714-924a-e04f9ccfaa8b | textbox | As-found TX Output
06725c0d-9ea9-5a52-8109-78e78f2deb00 | textbox | As-found TX: Error
e2094425-b840-5632-b474-afe32724335f | textbox | As-left TX Output mA
fd0f5856-250f-57da-b3c8-c681dbef4035 | textbox | As-left TX Output
c8e91830-9df8-548e-80b9-39ef7f1295ef | textbox | As-left TX: Error
ad0d4e54-73c3-4388-a301-7651c1981333 | checkpoint | 50%
b4b5002f-f2d5-56ed-8cce-dbd0928ce9d5 | textbox | Range
295e3841-2eb9-57e7-aab2-1ee395f89287 | textbox | Expected mA
d0c52b1a-f4e2-59cc-aa22-348b7dbf08d9 | textbox | Local Indication
b1506263-4b27-5407-b5d9-0fcf81dc57b1 | textbox | As-found TX Output mA
7dcf2851-97d3-520f-9b99-810bb06af0bf | textbox | As-found TX Output
9fcbfd8b-39af-50a9-94f6-53a71af21a72 | textbox | As-found TX: Error
64084444-71b5-50cb-86b8-47d48106ea4c | textbox | As-left TX Output mA
449e3200-ae66-5391-b2af-0b6e6562c2d9 | textbox | As-left TX Output
a2b430eb-f64f-5dba-9e78-dc0846587052 | textbox | As-left TX: Error
4eafc647-8a33-4637-9456-a3b1d26ef2db | checkpoint | 75%
d3f268cc-9387-534e-b3f4-173e94bbcbd5 | textbox | Range
30baeadc-eeca-5dce-ba10-3b609dc3e213 | textbox | Expected mA
0d62cfa6-c195-5935-b3d4-5bf38037765c | textbox | Local Indication
14612f70-a9d9-513d-a30c-64b4faa8bbe0 | textbox | As-found TX Output mA
4a77e256-a1a8-57f6-bf87-85e0ada05c0a | textbox | As-found TX Output
18903955-0623-514b-ba89-485b8519f4b4 | textbox | As-found TX: Error
ae06f395-e974-54ae-88ba-6ace6979db03 | textbox | As-left TX Output mA
6cb9fb30-16ce-5a66-b6eb-0d75fa31ca81 | textbox | As-left TX Output
68d10b81-0cd2-5464-bba4-9c61472d9b8d | textbox | As-left TX: Error
b94ec54e-9151-447a-b197-9a0fd52f9d40 | checkpoint | 100%
c838907b-9895-5097-9c07-64a6bccd79b3 | textbox | Range
70de8977-3c3b-578f-ad7e-9f483ede57ae | textbox | Expected mA
de6b5f17-9e46-575e-8591-e8dcb3d441fc | textbox | Local Indication
751e2fc6-d181-51db-a845-c7546a8afa9b | textbox | As-found TX Output mA
e6d617c6-8013-584c-8a1b-6d20fa6a1b4c | textbox | As-found TX Output
c4ca4743-9d2d-5776-aca8-afeac79a0078 | textbox | As-found TX: Error
74c4ae50-abfa-5da8-8d5c-ec1b15ef458d | textbox | As-left TX Output mA
2f036af5-e57d-551e-bfcc-f6c9a4bb077a | textbox | As-left TX Output
189ef0d8-e48b-58e8-bcaa-7b685fdfae67 | textbox | As-left TX: Error
ffda361d-b72c-403c-9043-e2e3c60703c8 | checkpoint | 50%
4df95508-062a-5f99-be42-64393e51ee77 | textbox | Range
846da223-6374-59ef-b1d4-4de40ae06802 | textbox | Expected mA
6d25560d-6726-5c6c-8195-fd689ebe1b29 | textbox | Local Indication
85403d95-cd49-59dd-97d1-e104eb347cc9 | textbox | As-found TX Output mA
a757f707-c1d3-56d3-9dfa-7ae6d785a8b6 | textbox | As-found TX Output
b7f6146d-ba06-5d9a-845c-c1a0f759d1fb | textbox | As-found TX: Error
2acb7b93-aaba-57fb-8b70-89072ce45a19 | textbox | As-left TX Output mA
b1682743-3023-5755-a954-98cc0f10ed54 | textbox | As-left TX Output
a4fc5658-f0c9-5602-a38e-4bf50f5b04e6 | textbox | As-left TX: Error
7e16e2bc-74c9-445c-bd03-3a97fb966db7 | checkpoint | 25%
4482882b-9f1f-5c7b-802a-0d107ee2ae45 | textbox | Range
6c98ef73-e456-5ac5-9432-1106e901ce5c | textbox | Expected mA
adfa453c-46d7-5b22-916b-818cc675f2a2 | textbox | Local Indication
cb19396c-2ba0-519a-91e0-8650962196a7 | textbox | As-found TX Output mA
0bcd12dc-42a8-5110-9ed9-cf722956fa3d | textbox | As-found TX Output
c192fb2a-90ac-5de4-9e45-c86c25fa2a94 | textbox | As-found TX: Error
ee31343f-645a-58ea-9293-094905d13a03 | textbox | As-left TX Output mA
3e9c34af-db74-5149-bc5f-6742aa63aed7 | textbox | As-left TX Output
68e4d8b3-dbeb-5646-866b-9f5f43eeed40 | textbox | As-left TX: Error
2bb64579-142e-4784-ae5a-5fea497a2277 | checkpoint | 0%
7adbb5e2-e53f-514e-a522-ec12295e55e4 | textbox | Range
57cdd67e-4e80-5f60-bf72-30e749ffaf4b | textbox | Expected mA
629bb4fc-9186-5121-9c4d-0fc5a471c5b3 | textbox | Local Indication
2fe1c00d-24a6-5def-b868-56180a12f6d8 | textbox | As-found TX Output mA
204bb146-2f5e-5db3-a4e7-e5d596e50d69 | textbox | As-found TX Output
f7aa6a92-dbe2-52f4-892a-ba093082e88b | textbox | As-found TX: Error
f9f973c0-ac2c-5878-8f99-71da6f936f9c | textbox | As-left TX Output mA
337ee8e1-056d-5fc4-be54-4c2eb07bd009 | textbox | As-left TX Output
79a92e1e-139d-58e0-a198-0994613a6527 | textbox | As-left TX: Error
662ee6ab-446a-44ea-9513-0b08e0496256 | checklist | (TEST) Checksheet - Version 2 |  | Checksheet |  | 7964d075-ddbc-44a7-88c6-7a436ffdfc2a
c2ebbd3e-1fba-40f3-a0d6-ca839a284ea4 | section | Details
72819866-cf3f-40ec-94c2-0711700e4391 | checkpoint | Details
88a39a7e-4db1-5771-bf54-88f644bf2730 | dropdown | % | 0%,25%,50%,75%,100%
26b345bd-9e36-5f8c-97f7-4da3ced9bdfc | textbox | Range
7dedb44a-0e01-5d7f-b7b1-efff929fde6f | textbox | Expected mA
8e0f367f-65da-55ee-974f-5fb25727d6bb | textbox | Local Indication
2f34fd68-645f-5617-bd21-85d8e560e70b | textbox | As-found TX Output mA
fb41007c-dd4f-5eac-90f7-85ca33f8e074 | textbox | As-found TX Output
e0f56a10-12f3-5ce9-a148-a5280460f473 | textbox | As-found TX: Error
93bb44b2-7027-5744-a587-e6c044966ee4 | textbox | As-left TX Output mA
40d0538e-fdb8-56da-918f-bb09664376dc | textbox | As-left TX Output
946a7563-a51c-5d35-9cf4-6bda571972e1 | textbox | As-left TX: Error
| checklist | HV Cable Install |  | HV Cable Install |  | d919a9cc-af4f-47c9-ac5d-d2ced39ad82b
| section | Details
| checkpoint | HV Cable Install
487ddaae-46c2-5065-bc66-78602ebc614a | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
8477b3ab-b11c-5050-8928-265eeb1ed69d | button | Check dressing / cleating, cable undamaged | Yes,N/A
4e2f776d-cf9e-5d33-910f-59909afd22b3 | button | Check cable cores correctly identified and labelled. | Yes,N/A
58536d55-31b2-54fa-aef6-e6d8b219b1ea | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
c16b1dd9-5edb-50f9-a6dc-41f7970159d7 | button | Check Armour / Screen correctly made off. | Yes,N/A
3e412d0a-12c2-5f75-9a63-127759430708 | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
a29713de-bbbe-5127-a07c-57d946cfa343 | button | Glanding / Locknuts correctly installed. | Yes,N/A
6edf48bf-3e82-52c0-9058-a5fde583fda4 | dropdown | Cable Voltage | 11kV,33kV
9e815bb3-d85d-550c-b40b-2889e5657815 | textbox | Temperature:
e395eb8e-cfda-5ae4-b2c6-94e1041417ae | textbox | Cable Point to Point:
| checkpoint-no-value | Electrical Tests
010d2800-3c10-5d1f-a974-2fbc501626a0 | note | Testing for the below should be done at 5kV for 10 minutes. If result is below 1.25GΩ this indicates a low test and will need to be re tested. A brand new cable should have a result above 2GΩ.
9f0fac9c-5a62-5679-9754-9db0036f74ab | textbox | R-WBE |  |  | GΩ
758d221e-df3d-5a99-9b04-df1f33a102fc | textbox | W-RBE |  |  | GΩ
7f434e47-590d-52be-bf10-8bd966f93d69 | textbox | B-RWE |  |  | GΩ
ecff3b43-a061-5c52-9aa6-f966097bc45a | textbox | One Core |  |  | GΩ
| checkpoint-no-value | Sheath Integrity Test
19b7003a-62e1-513a-879e-74674cb20bae | textbox | Test Duration:
29c34ffe-64cd-55f5-8e80-a8a2a85f918d | textbox | Test Voltage: |  |  | GΩ
7ced2f62-6fa1-587e-88e4-3ec6ca45f1c8 | textbox | Result (GΩ):
| checkpoint-no-value | Test Equipment Details
6fb516e7-1915-54aa-b581-70cd33ba98ad | textbox | Make
8da29561-6689-5e3a-a15c-5fdb7288ca29 | textbox | Model
1c4ad141-26ae-5921-afbe-52ac4699f7a9 | textbox | Serial No
75bc13f1-2407-5092-b731-fdd76acde1be | textbox | Calibration Expiry Date
| checkpoint-no-value | Installer Sign-off
| signoff | Installed by:
| checkpoint-no-value | Client Sign-off
| signoff | Client Representative: