## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | CRL-ITR-010 - Crack Unit Installation |  |  |  |  | Yes | CRL-ITR-010 - Crack Unit Installation | 1681b2f6-cc11-443d-919e-ddb5b4e71636
checkpoint-group |  |  | section | Crack Unit
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Correct Unit Model
text | 175f9991-5454-540d-bf44-bc4dd1a7cafc |  | textbox | Model Number
text | 0e7cdd59-6793-5af5-b2a7-4b4bea5ffb1a |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | Check for Damage
checkpoint-status |  |  | checkpoint | Verify Floor is Level
checkpoint-status |  |  | checkpoint | Confirm Fixings as per detail (Seismic)
text | 68fe9f3c-938d-5854-a6b2-ead8a99d5d46 |  | textbox | Drawing Reference Number
checkpoint-group |  |  | section | Crack Second Fix QA
checkpoint-status |  |  | checkpoint | Potable Water connected (by others)
checkpoint-status |  |  | checkpoint | Filters Installed – Check Clearances
checkpoint-status |  |  | checkpoint | Door Clearance checked
checkpoint-status |  |  | checkpoint | Drains Installed – Run to Tundish by Others
checkpoint-status |  |  | checkpoint | Shipping mounts removed
checkpoint-status |  |  | checkpoint | Label to be installed
checkpoint-status |  |  | checkpoint | Location
text | 2a27fca7-ad41-590f-a11c-b3b87fc8ff85 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | c741e9ba-1f9e-588f-a4d7-a3d9d959945e |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 6e2b023b-aed4-5d34-b140-26a0d2904228 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | dc7edf10-d9df-59f5-9d88-cf37ea8ece6c |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | 8e53f063-b122-554a-9b64-3dc340527d29 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | 62633420-df40-5d3f-8d6b-e70b7f30d53c |  | textbox | Add details
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | Location
text | 5fa8d002-082f-5289-b4af-d76ccc743d45 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | 8bede008-011d-5b6b-8698-157a8d8bf14b |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | b986ed32-e89e-56d5-9280-9208681724cd |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | 23c1d94c-e029-5a3b-bc9f-f42ed960ecc8 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | 0746fcdd-a795-5be2-9020-97644af80b5a |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | d3d2f939-c739-536b-a7ec-7f252ecbbd38 |  | textbox | Add details
checklist-sectioned |  |  | checklist | CRL-ITR-002 - Fire Dampers |  |  |  |  | Yes | CRL-ITR-002 - Fire Dampers | 1e39f4ac-1012-4c63-80a6-cc0f230b32c7
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Penetration formed correctly
checkpoint-status |  |  | checkpoint | Correct FD Installed & correct orientation
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Access Panel installed
checkpoint-status |  |  | checkpoint | Drop Tested
checkpoint-status |  |  | checkpoint | Track is Clear
checkpoint-status |  |  | checkpoint | All angles correctly fixed
checkpoint-status |  |  | checkpoint | Label to be installed
checkpoint-status |  |  | checkpoint | Location
text | c2273211-9e1e-5f5b-8cbd-7a1b19d24d85 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | 72de24a0-5ee8-51f0-bf5f-505bc3ca932d |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 87ea4966-4ec1-55c3-a43e-d9867f56cbe3 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | 3c15e468-95a1-595c-bd28-1f59b2911a0e |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | 9b8fbaa2-d803-5994-a267-f652283ffedf |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | d3074725-c8c5-50b6-905f-43b0ccc95a8c |  | textbox | Add details
checklist-flat |  |  | checklist | CRL-ITR-007 - Hydro Pressure Test |  |  |  |  | Yes | CRL-ITR-007 - Hydro Pressure Test | 3781eb03-a06b-47c6-8d66-013a2a171bc8
checkpoint-status |  |  | checkpoint | Details of pressure test
text | 87f0be7a-9acf-520c-9b0f-48c693ee4147 |  | textbox | System Name/No.
text | 88b37616-e8d9-5d65-8961-a4dd973fe474 |  | textbox | Location / Drawing No.
text | 5be0cf38-b612-5b21-9d77-444ea66e9a68 |  | textbox | Test Instrument & Serial Number.
text | a892ee4a-f7ca-5afa-abf2-b129d505aa84 |  | textbox | Normal Working Pressure
text | e4431b42-94b8-50b6-b109-8bc4eae5ebf3 |  | textbox | Start test ambient temperature
text | 75313874-1dd6-5f31-9242-e794754b8cf4 |  | textbox | Start test date
text | f3fcaa39-9cec-5144-a542-145a25c6af43 |  | textbox | Start test time
text | 811a6326-30aa-50e8-861f-e9d9c70842ff |  | textbox | Start test pressure
text | 5521c3e9-8173-50ef-8257-41d7e3d8630d |  | textbox | Finish test ambient temperature
text | 45d1a31c-d8e5-5e5a-9ecf-dc032220d4db |  | textbox | Finish test date
text | b4854204-8c93-559c-b649-2975d949d68a |  | textbox | Finish test time
text | 48a575c5-4a5a-557f-a60d-e51ada134544 |  | textbox | Finish test pressure
text | 45bc749a-dbf5-523d-8f7b-872b7464640f |  | textbox | Corrected pressure at test completion
label | 24c65c6b-5c6e-5f66-b17a-6429012e7ee9 |  | note | Attach photos of the gauges as required
label | 051b8bb0-0f24-56a3-8808-bf6c349d4b06 |  | note | FORMULA:
label | 9916a0a0-16c8-596d-b99f-17ff6a290635 |  | note | Pc = P x (Ts + 273) / (T + 273) kpa
label | 9950f493-5810-581e-8729-d70139023a47 |  | note | Pc = P x (+273 ) / (+ 273) kPa
label | 1c8c6338-acee-56bb-bebd-4c1a4ea91683 |  | note | Pc = kPa
label | b3e25277-f6be-5baf-b574-69a2ff3f90e1 |  | note | WHERE:-
label | e83ed12e-a8b6-5f81-9b3f-84decca24745 |  | note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
label | e9848d81-7303-503b-8987-bc89ecebc583 |  | note | Pc = CORRECTED PRESSURE
label | aabc9f13-92fa-52de-ab7a-d22474c8e02c |  | note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
label | e5bfd5a4-88a6-5c1b-bc58-e02e3e1d789f |  | note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
holdpoint |  |  | signoff | LKA Signature
checklist-flat |  |  | checklist | CRL-ITR-021 - Metal Cladding |  |  |  |  | Yes | CRL-ITR-021 - Metal Cladding | 3985b1fb-aded-4b5b-8a99-10d38c1271e5
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Clad pipework as per drawing
checkpoint-status |  |  | checkpoint | Approved materials have been used
checkpoint-status |  |  | checkpoint | Pipework cladding installation complete and tidy. Check straps, sealant and removable sections
checkpoint-status |  |  | checkpoint | Penetraitons are sealed for gauges, instruments, and drain vents (silicone)
checkpoint-status |  |  | checkpoint | Confirm cladding is free of damages
checklist-sectioned |  |  | checklist | CRL-ITR-005 - Fan Coil Units |  |  |  |  | Yes | CRL-ITR-005 - Fan Coil Units | 3b5b0c67-e589-4a84-956a-4494334b5791
checkpoint-group |  |  | section | Unit First Fix QA
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Correct Unit Installed
text | 5780ca31-f3d9-5da1-93a9-fed4e088671d |  | textbox | Model Number
text | 56a403de-3c21-5146-8dc1-760a7c0233df |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Correct mountings / springs installed and unit confirmed level.
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Unit Plenum Boxes to be installed
checkpoint-status |  |  | checkpoint | Filters installed & clearence checked
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | b79803cf-20ec-51a6-b48a-e69813f016e7 |  | textbox | Drawing Reference Number
checkpoint-status |  |  | checkpoint | P - trap installed if required
checkpoint-status |  |  | checkpoint | Driptray installed if required
checkpoint-status |  |  | checkpoint | Condensate Drains installed
checkpoint-status |  |  | checkpoint | Plug low points and tundish and fill the line. Check water level has not dropped after 30 minutes. Test water flow
checkpoint-status |  |  | checkpoint | Label to be installed
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | Location
text | 39023323-224f-574c-80c3-08277ee49e77 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | b1682822-bfd5-5ac1-8bf9-4d5e20f8319b |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 61fc48a7-19b6-5898-b4d3-d48c3c440de8 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | 3da1d5a7-08f8-5e28-9c1d-c46d1747d376 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | 05c01c8f-1912-54b3-a6b8-96f4165fcf32 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | 2e924921-1903-5240-b4dd-0ca9b4a763ee |  | textbox | Add details
checklist-flat |  |  | checklist | CRL-ITR-006 - Chilled Water Pipe Systems |  |  |  |  | Yes | CRL-ITR-006 - Chilled Water Pipe Systems | 479364f1-e9dc-4a4f-8c20-dd82f195c496
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
text | 5e85c378-0867-5644-a008-0258270e5bfa |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per schematic
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Drains installed at low points
text | c5594e36-fcf2-56b0-bbbd-7bd1de1674e2 |  | textbox | Air vents installed at all high points
checkpoint-status |  |  | checkpoint | The pipe OD and groove dimensions are within tolerance range as per victaulic specification
checkpoint-status |  |  | checkpoint | The correct coupling has been used for the correct joint i.e flexible or rigid
checkpoint-status |  |  | checkpoint | Visual indicators verified - Positive overlap - Joint Square
checkpoint-status |  |  | checkpoint | Steel is primed (two coats) and weld painted after works are completed (PA10)
checkpoint-status |  |  | checkpoint | Confirm all bolts in the system are Galvanised
checkpoint-status |  |  | checkpoint | Pipework Seismic to be installed
text | 128b14fc-7503-54e8-bded-04a9227c092f |  | textbox | Drawing Reference Number
checklist-flat |  |  | checklist | CRL-ITR-003 - Mechanical Board (MSSB) |  |  |  |  | Yes | CRL-ITR-003 - Mechanical Board (MSSB) | 4991d906-3871-451c-bc64-40524ddaf55a
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Switch Board Mounted in correct position and level
checkpoint-status |  |  | checkpoint | Switch Board terminations complete
checkpoint-status |  |  | checkpoint | Board Tested
checkpoint-status |  |  | checkpoint | COC's Complete
checkpoint-status |  |  | checkpoint | Label to be installed
checkpoint-status |  |  | checkpoint | Location
text | dfaa34a0-4f45-5ab6-bc2e-74fd48daa168 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | 7fe2038d-e791-5dba-af3f-5c5d38da6f83 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 44e7f019-76b7-553e-a31d-8b5a5d7d5d84 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | cb017e4c-10c1-5c9d-87ce-4f486f110b13 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | f270e71b-f188-5eea-a4ca-b7b914ff425e |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | 532bde01-5d59-55e0-a41c-478c81c5ee24 |  | textbox | Add details
checklist-flat |  |  | checklist | CRL-ITR-020 - Fire Rated Duct Insulation |  |  |  |  | Yes | CRL-ITR-020 - Fire Rated Duct Insulation | 4adf8ef0-0d22-4096-a20e-9fe3ba6f5e6f
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing and specifications
checkpoint-status |  |  | checkpoint | Ensure all wraps are complete and no gaps ensure
checkpoint-status |  |  | checkpoint | Confirm all joints installed correctly with suitable overlaps
checkpoint-status |  |  | checkpoint | Pins and banding correctly applied
checkpoint-status |  |  | checkpoint | Maxilite board to wall complete and sealed.
checkpoint-status |  |  | checkpoint | Confirm second layer length has been installed as per specification from wall.
checkpoint-status |  |  | checkpoint | Access Panels installed correctly. Confirm fixings, sealant and alignment with internal panel.
checkpoint-status |  |  | checkpoint | Confirm insulation is free of damages
checklist-sectioned |  |  | checklist | CRL-ITR-004 - Fans |  |  |  |  | Yes | CRL-ITR-004 - Fans | 4d627d76-e704-4600-befb-ee5c18078785
checkpoint-group |  |  | section | Fans
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
text | b766db8e-1684-5d1c-b2c7-8205f86d4b22 |  | textbox | Model Number
text | 17d8ba45-8838-5610-9bab-8baae5885d56 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | Correct mountings / springs installed and level checked.
checkpoint-status |  |  | checkpoint | U/S of Fan heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | ba2f8e90-f8fb-5d3c-9bff-ab67c66158a1 |  | textbox | Drawing Reference Number
checkpoint-status |  |  | checkpoint | Label to be installed
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | Location
text | 06429129-fbe3-594c-9d19-daf3691b677e |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | 2a4e03b6-269e-5449-8875-834b5f1aa3fb |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 6a1df7b4-a40e-5a57-91ce-ebcd7c77e9a8 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | f48f15c5-28a0-5fdf-aeac-700c5ced3652 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | d988cd2d-9278-507a-8539-51f6c231bab6 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | 6c793c82-5305-54de-9516-ed5d4bf0c2ec |  | textbox | Add details
checklist-flat |  |  | checklist | CRL-ITR-024 - General floor wide checks |  |  |  |  | Yes | CRL-ITR-024 - General floor wide checks | 51dd725e-d1c0-4f8b-bdfd-a1d7fa036820
checkpoint-status |  |  | checkpoint | Check all equipment and components have smooth edges and are free of sharp surfaces, snags, or points at locations where people may be passing
checkpoint-status |  |  | checkpoint | Check all equipment and components have smooth edges and are free of sharp surfaces, snags, or points at locations where handling is expected
checkpoint-status |  |  | checkpoint | Check any sharp edges are labelled
checkpoint-status |  |  | checkpoint | Check all penetrations through fire-rated are properly sealed
checkpoint-status |  |  | checkpoint | Check NO taped joints are used on ductwork and NO pipe sleeves are used as pipe supports
checkpoint-status |  |  | checkpoint | Check all pressure and temperature test points are insulated
checkpoint-status |  |  | checkpoint | Check semi-rigid ductwork is no longer than 3m
checkpoint-status |  |  | checkpoint | Check all metal components are deburred
checkpoint-status |  |  | checkpoint | Check all joints in metal components are flush
checkpoint-status |  |  | checkpoint | Check all exposed base metal has been treated with a protective coating
checkpoint-status |  |  | checkpoint | Check all welds are painted with zinc chromate paint
checklist-flat |  |  | checklist | CRL-ITR-023 - Air Pressure Test |  |  |  |  | Yes | CRL-ITR-023 - Air Pressure Test | 5817f476-fcd5-4a9d-8066-e38bf7daedb2
checkpoint-status |  |  | checkpoint | Details of pressure test
text | 425454b8-346b-5771-9797-b2172caecf35 |  | textbox | System Name/No.
text | 21855a9f-6601-5868-a3d5-be21fe1676c7 |  | textbox | Location / Drawing No.
text | 8d8f2aee-b761-5cf9-9688-a06b60abee36 |  | textbox | Test Instrument & Serial Number.
text | 9d2d8cea-616c-5399-a6a8-af55fd095158 |  | textbox | Normal Working Pressure
text | ec7474ba-43ea-596e-91e1-67f4beaa61b5 |  | textbox | Start test ambient temperature
text | fa6f8ca3-e147-5967-91ad-3fe77c371179 |  | textbox | Start test date
text | 045bad62-b56a-53af-b40f-ad3d4066b53a |  | textbox | Start test time
text | dfa2b62f-575a-5632-ad87-036dfd627759 |  | textbox | Start test pressure
text | 965eeea1-bac9-541f-8b0b-0e6a4579b8e6 |  | textbox | Finish test ambient temperature
text | a55f3538-c0cf-523b-a160-c871335fcdcb |  | textbox | Finish test date
text | 5b47e25a-d4e2-57a8-ab35-6839fafb9e4a |  | textbox | Finish test time
text | 1ca007f7-f11d-5733-ad56-866002cdc797 |  | textbox | Finish test pressure
text | 0b43bdb7-41a5-5d60-bc29-2bb15d738c7e |  | textbox | Corrected pressure at test completion
label | 9c3f4744-abc9-53e0-a74a-bd9b52f8158b |  | note | Attach photos of the gauges as required
label | 942bf518-f95e-5d14-ba6f-90b6a7660c25 |  | note | FORMULA:
label | 14658dc9-366e-5619-9264-e92deae85417 |  | note | Pc = P x (Ts + 273) / (T + 273) kpa
label | 6a1bd706-3f74-5f2c-9514-bdc861cf8742 |  | note | Pc = P x (+273 ) / (+ 273) kPa
label | 669082c8-c5b6-59e9-bc2f-dc3638ddb560 |  | note | Pc = kPa
label | 91a52124-a21d-5a15-991c-04767920bd0c |  | note | WHERE:-
label | e108f603-946c-5e1c-be26-f3594283db32 |  | note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
label | ea3cbb49-6629-52c0-b534-a6af456d7958 |  | note | Pc = CORRECTED PRESSURE
label | fa4ed202-ff33-5daf-8105-86149a459f08 |  | note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
label | b356cc3c-23d8-5efc-8766-dbeeeb7bcb66 |  | note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
checklist-sectioned |  |  | checklist | CRL-ITR-013 - Radiant Heaters |  |  |  |  | Yes | CRL-ITR-013 - Radiant Heaters | 6763602d-b449-40cd-8974-69fa2b41fe77
checkpoint-group |  |  | section | Radiant Heaters
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
text | c1dce88e-2e6f-579a-817a-60fc7a4273f8 |  | textbox | Model Number
text | 97b4db5f-d91f-5906-9b93-66fc540236f5 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | U/S of Equipment heights correct as per Workshop Drawings
checkpoint-status |  |  | checkpoint | Heater labelled
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | Location
text | cc70e8bb-8fa2-542c-acff-e73af9bfdc8b |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | dba68d1b-57bc-56f2-8777-1197e4ba7800 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 8c618107-0702-5e0c-b23b-e5c51a1fc608 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | e84b0249-9c37-50e2-8b0e-e4e0707f7132 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | cd725ae5-3c7d-555d-ab5c-a6754c276add |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | f0272778-ea0d-54f4-9f1f-8d9af5aaa55e |  | textbox | Add details
checklist-flat |  |  | checklist | External Acoustic Insulation (FCU's) |  |  |  |  | Yes | External Acoustic Insulation (FCU's) | 70a96eeb-56b8-4e67-bacb-4542c39be42c
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Acoustic wrap materials - 50mm Polyester sheet cover with 5kg wave bar
checkpoint-status |  |  | checkpoint | Cover all surface of the FCU units with insulation excluding the Vents and pipe outlet area.
checkpoint-status |  |  | checkpoint | fixing using self adhesive pins and polypropylene Bands with with buckles .
checkpoint-status |  |  | checkpoint | Tape all joints with 50mm width reinforced Aluminium foiled tape.
checklist-flat |  |  | checklist | CRL-ITR-017 - CHW Insulation |  |  |  |  | Yes | CRL-ITR-017 - CHW Insulation | 7299ea09-fcaa-4caf-9f3a-ee67be57a2fd
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specification
checkpoint-status |  |  | checkpoint | Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
checkpoint-status |  |  | checkpoint | Insulation is glued and taped correctly
checkpoint-status |  |  | checkpoint | Confirm insulation is free of damages
checklist-flat |  |  | checklist | CRL-ITR-018 - Condensate Insulation |  |  |  |  | Yes | CRL-ITR-018 - Condensate Insulation | 75cc0929-776c-4e1f-8e13-efde724dbbef
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
checkpoint-status |  |  | checkpoint | Condensate pipework insulated correctly
checkpoint-status |  |  | checkpoint | Confirm insulation is free of damages
checklist-flat |  |  | checklist | CRL-ITR-022 - Motorised Dampers |  |  |  |  | Yes | CRL-ITR-022 - Motorised Dampers | 77d40043-340b-43e2-bbfc-d3c8aa09c5af
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installing
checkpoint-status |  |  | checkpoint | Correct damper installed & correct orientation
checkpoint-status |  |  | checkpoint | Damper is installed open
checkpoint-status |  |  | checkpoint | Check actuator access and clearance for actuator removal.
checklist-flat |  |  | checklist | CRL-ITR-009 - Chillers Installation |  |  |  |  | Yes | CRL-ITR-009 - Chillers Installation | 85a63764-7558-49f6-9f26-ab0a6a429d03
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Check equipment hold down bolts are grouted prior to equipment location
checkpoint-status |  |  | checkpoint | Unit to be aligned, levelled, and pulled down by tightening the nuts of the holding down bolts.
checkpoint-status |  |  | checkpoint | Correct Unit Installed
text | 3e16934a-f0ca-5348-81ab-6b5628c3a463 |  | textbox | Model Number
text | 558a75ab-921c-5104-9fc0-a897039f2c45 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Correct Mounting Springs installed
text | a368ace1-12e1-5b0d-a8a7-782276f86d34 |  | textbox | Drawing Reference Number
checkpoint-status |  |  | checkpoint | Label to be installed
checklist-flat |  |  | checklist | CRL-ITR-014 - Duct / Equipment Cleaning |  |  |  |  | Yes | CRL-ITR-014 - Duct / Equipment Cleaning | 8cf204fb-1a2c-4022-a453-fd0f0de86a12
checkpoint-status |  |  | checkpoint | Duct cleaned in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checklist-flat |  |  | checklist | CRL-ITR-015 - Cowls |  |  |  |  | Yes | CRL-ITR-015 - Cowls | 98da1882-c84a-4314-9e63-64008dc2b2b9
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Outside Air Roof Cowl Installed
checkpoint-status |  |  | checkpoint | Builder - Waterproof and Seal to be installed
checkpoint-status |  |  | checkpoint | Label applied to roof cowl
checklist-sectioned |  |  | checklist | CRL-ITR-012 - Braze Bench Test |  |  |  |  | Yes | CRL-ITR-012 - Braze Bench Test | 9dc1fe71-09b3-4a4a-bb63-7658afe5adf2
checkpoint-group |  |  | section | Test Sheet
checkpoint-status |  |  | checkpoint | Test Sheet Completed
text | 0adae743-ed23-54de-931d-4caf5e336886 |  | textbox | BUILDING:
text | 036c7a07-47e1-5926-ae1a-25be82d3006f |  | textbox | AREA / SYSTEM:
text | e3b3c46f-253b-52dc-aede-b47fbeb34e0b |  | textbox | DRAWING No.
text | d0ed85dd-098c-5a70-a131-a05bf1fe126d |  | textbox | NAME OF WORKER:
text | 72d4378e-c586-59e8-89d9-e9e6747248c3 |  | textbox | ASSIGNED BRAZE ID.
text | 46169e6b-2fd3-56fb-a9d0-c69298ee10b0 |  | textbox | JOINT TYPE INSPECTED:
text | fc5a065e-d259-5aff-a283-a42d6ec50763 |  | textbox | INSPECTING SUPERVISOR
checkpoint-status |  |  | checkpoint | Tube is cut by suitable means, ends are deburred & cleaned of any filings, and surfaces prepared with light grade emery paper.
checkpoint-status |  |  | checkpoint | Joint fit has correct clearance and expanded end of tube (if applicable) is to correct length for pipe size
checkpoint-status |  |  | checkpoint | Heat from Oxy Acetylene torch is being applied uniformly to the fitting, and torch flame is slightly reducing/carburising.
checkpoint-status |  |  | checkpoint | Silfos used is 15% and is being applied so that through capillary action is achieved around the entire joint.
checkpoint-status |  |  | checkpoint | Shoulder build-up of Sipfos is just present around the entire circumference of the brazed joint, and completed joint is left to air cool.
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | e680cfde-17ed-5d48-90bb-d452f38d8189 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 3136f60a-bed3-5ae2-9491-44145af495f1 |  | textbox | Consultant Name
checklist-flat |  |  | checklist | CHW & HHW Insulation |  |  |  |  | Yes | CHW & HHW Insulation | a91cc94e-c555-4548-9e14-e526bc0615f3
checkpoint-status |  |  | checkpoint | Approved material thickness has been used (Thermobreak®).
checkpoint-status |  |  | checkpoint | Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specification
checkpoint-status |  |  | checkpoint | Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
checkpoint-status |  |  | checkpoint | Insulation is glued to the pipe with a 50mm wide band of adhesive (Ados F2®) at both ends of section to form the vapour barrier
checkpoint-status |  |  | checkpoint | Adhesive is applied along all longitudinal and circumferential joints
checkpoint-status |  |  | checkpoint | A 50mm wide strip of pressure sensitive tape reinforced aluminium tape is applied to the insulation facing, along and around all joints
checkpoint-status |  |  | checkpoint | Mitre cut elbows have been used on all bends.
checklist-sectioned |  |  | checklist | CRL-ITR-001 - Mechanical Duct |  |  |  |  | Yes | CRL-ITR-001 - Mechanical Duct | a9de3f00-764a-4d78-acaa-16e97654b8a6
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of duct heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Duct Hangers (is spacing correct, installed level , rods trimmed back etc)
checkpoint-status |  |  | checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint-status |  |  | checkpoint | Orientation of dampers and equipment to be installed correct way
checkpoint-status |  |  | checkpoint | Access panels at low points of ducts
checkpoint-status |  |  | checkpoint | No metallic ducts have taped joints
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | All volume control dampers set fully open.
checkpoint-status |  |  | checkpoint | Seismic bracing installed as per Drawing
text | f6fc64b6-63ad-5161-805c-03bfc24c3c10 |  | textbox | Drawing Reference Number
checkpoint-status |  |  | checkpoint | Flexible duct exceeding 1.5m in length to be supported in the centre using flexible duct supports & nylon banding. Flexibles not to exceed 3m Total length
checkpoint-group |  |  | section | Fit Off QA
checkpoint-status |  |  | checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
checkpoint-status |  |  | checkpoint | Restrained correctly
checkpoint-status |  |  | checkpoint | Flexible connection fixed correctly to grill box
checklist-flat |  |  | checklist | E4M QA |  |  |  |  | Yes | E4M QA | bb3119db-8cac-4a75-99ae-80e858c77332
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Labelling of Equipment |  |  |  |  | Yes | Labelling of Equipment | d03c0589-1475-43b4-9923-6120bdfcad12
checkpoint-status |  |  | checkpoint | Correct label installed as per reference on Equipment / Drawing
checkpoint-status |  |  | checkpoint | Label visible
checkpoint-status |  |  | checkpoint | Correct directional arrows / colour coding installed on system
checklist-flat |  |  | checklist | CHW & HHW Piping ( WELDING ) |  |  |  |  | Yes | CHW & HHW Piping ( WELDING ) | d0b34c4f-f706-40c7-9a6f-82a4099f1765
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
text | 78e198d1-27bb-593c-bffb-8249767c5710 |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing i.e. Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Expansion tank / Dosing Pod
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and Control valve installed correctly
checkpoint-status |  |  | checkpoint | Hose piping installed
checkpoint-status |  |  | checkpoint | Air vents installed at all high points
checkpoint-status |  |  | checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint-status |  |  | checkpoint | Welding procedure specification to be applied as per attached
checkpoint-status |  |  | checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint-status |  |  | checkpoint | Welding of pipework
checkpoint-status |  |  | checkpoint | Pipework Seismic to be installed ( Expansion joints , loops etc. )
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | b6292bea-fb26-5059-b35e-acd533bfbf28 |  | textbox | Drawing Reference Number
checklist-flat |  |  | checklist | CRL-ITR-011 - Pump Installation |  |  |  |  | Yes | CRL-ITR-011 - Pump Installation | d338dfb0-7fc5-49e9-8be7-e66350240a9b
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Corrrect Mounting Springs installed
text | dc7d5d2b-e105-5ebd-8a4f-95651224766e |  | textbox | Drawing Reference Number
checkpoint-status |  |  | checkpoint | Label to be installed
checkpoint-status |  |  | checkpoint | Location
text | f9a1d478-bc55-5518-884d-63e8082cc729 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | d7c6121f-b6ac-51df-85a3-dddf349715f2 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 62d5414e-311f-5096-b88a-3740f0a54147 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | 39bf0efb-5637-5d5c-9668-2d09630a5518 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | 805a5875-1380-590d-ad37-3ea8b1443e04 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | 0d251137-a331-5eee-b235-676cae8f2c44 |  | textbox | Add details
checklist-sectioned |  |  | checklist | CRL-ITR-008 - AHU Installation |  |  |  |  | Yes | CRL-ITR-008 - AHU Installation | d84ce57b-b3e4-4583-96fb-4a9f0ad5cae6
checkpoint-group |  |  | section | AHU's
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Check plinth size and location
checkpoint-status |  |  | checkpoint | Check equipment hold down bolts are grouted prior to equipment location
checkpoint-status |  |  | checkpoint | Unit to be aligned, levelled, and pulled down by tightening the nuts of the holding down bolts.
checkpoint-status |  |  | checkpoint | Correct Unit Installed
text | 04fc395f-dc49-5dce-bc50-35b16d3aeba1 |  | textbox | Model Number
text | 9b80f128-5ec0-5158-9286-84a688404d11 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | Condensate Piping installed
checkpoint-status |  |  | checkpoint | Unit correctly anchored and Isolation Pads installed
text | 8df03626-f237-57de-a99c-b529e734e282 |  | textbox | Drawing Reference Number
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Filters Installed
checkpoint-status |  |  | checkpoint | Label to be installed
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | Location
text | 0fb7a30d-b748-5186-94f6-d2f550776f76 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | 387a2df6-19c4-5b01-a1fb-41a11975c9c8 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 1ca4cd89-4792-55a9-b8c5-b0f5a718a5cb |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | b1e9f8de-338d-5b46-86a0-104727ee85af |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | 246b492b-3c5f-5bfd-94f8-fcfbd3d4eaa9 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | e85cb3cb-1062-55c4-a885-8f16feda2075 |  | textbox | Add details
checklist-sectioned |  |  | checklist | CRL-ITR-022 - General Area Check |  |  |  |  | Yes | CRL-ITR-022 - General Area Check | ec5421c3-8546-4130-bbbe-de4492b9134b
checkpoint-group |  |  | section | General Area Check
checkpoint-status |  |  | checkpoint | Area Inspected
text | 76782235-36ac-5ebc-8730-51543d5cac0e |  | textbox | Level
text | d4ad7a30-2fda-5356-be5c-99ba0e25d506 |  | textbox | Zone
checkpoint-status |  |  | checkpoint | All materials and equipment of "new" origin.
checkpoint-status |  |  | checkpoint | Installation has no sharp edges
checkpoint-status |  |  | checkpoint | Installation has all required labelling completed.
checkpoint-status |  |  | checkpoint | Any damaged or corroded materials repaired or replaced
checklist-flat |  |  | checklist | Internal Duct Work Insulation |  |  |  |  | Yes | Internal Duct Work Insulation | ecccbfa9-3ea5-453a-b009-d4588197da7c
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Duct materials - Fibreglass
checkpoint-status |  |  | checkpoint | Fixed with Adhesive weld pins and speed clips located not more than 75mm from the edges of the ducts and spaced not more than 300mm centres.
checkpoint-status |  |  | checkpoint | Longitudinal corner joints fixed with:
checkpoint-status |  |  | checkpoint | duct dimensions less than 300mm -25mmx25mm angles
checkpoint-status |  |  | checkpoint | duct dimensions 300mm and greater -50mmx50mm angles
checkpoint-status |  |  | checkpoint | Joints taped between adjacent of insulation with a 75mm wide strip of reinforced aluminium foil laminate tape.
checkpoint-status |  |  | checkpoint | Tape joints protected with 75mm wide sheet metal cover strip, pop riveted to the corner angles.
checklist-flat |  |  | checklist | CRL-ITR-019 - External Duct Work Insulation |  |  |  |  | Yes | CRL-ITR-019 - External Duct Work Insulation | f0b3b5e6-81f8-4d55-9043-bf22f3afbeb7
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing and specifications
checkpoint-status |  |  | checkpoint | Provide 50mm over lapping at all joints.
checkpoint-status |  |  | checkpoint | Confirm pins are installed and spacing is correct
checkpoint-status |  |  | checkpoint | Confirm bands at 600mm centres.
checkpoint-status |  |  | checkpoint | Confirm all overlaps and joints are complete
checkpoint-status |  |  | checkpoint | Confirm insulation is free of damages
checklist-sectioned |  |  | checklist | CRL-ITR-016 - DX Units |  |  |  |  | Yes | CRL-ITR-016 - DX Units | fae97e9a-2e24-410e-826d-a3dcad9a786f
checkpoint-group |  |  | section | DX Units
checkpoint-status |  |  | checkpoint | Pre-check equipment for damage prior to installation
checkpoint-status |  |  | checkpoint | Correct Unit Installed
text | 6ff0ba8e-3d35-5395-a334-1d8265b3be16 |  | textbox | Model Number
text | 990af873-350e-50ed-bbd0-023d264da2b9 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | Out door Unit Installed
checkpoint-status |  |  | checkpoint | U/S of Unit at correct height and unit level
checkpoint-status |  |  | checkpoint | Refrigeration Pipework installed as per drawings
text | c8dc3dbb-18b3-589f-a2dd-0719711237c2 |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | Pipework Installed from DX unit box to Outdoor unit
label | 31c4eaa1-e771-543d-95d5-34e6a0671c36 |  | note | Schematic markups drawings
checkpoint-status |  |  | checkpoint | Condensate Piping installed
checkpoint-status |  |  | checkpoint | Pressure Tested
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
text | 09ad8b37-5963-577c-9c1c-1970707fd2c4 |  | textbox | Name of person
text | d60c1800-f87a-5445-8632-f398618d7d31 |  | textbox | Date
checkpoint-status |  |  | checkpoint | Photo's of Pressure test
text | eda2e65d-3719-5b3c-ab07-499b2581de1d |  | textbox | Start of Pressure test
text | 402b070c-e1d2-5513-bbad-c91c59cd245b |  | textbox | Time / Date
text | 83e4260a-2a7d-5545-8f6f-6f8761384363 |  | textbox | Pressure test after recored Duration
text | 75f57f11-f2ee-54b8-b597-37c05644d4df |  | textbox | Time / Date
checkpoint-status |  |  | checkpoint | Triple Evacuation procedure to be done.Final below 500 Microns
checkpoint-status |  |  | checkpoint | Refrigeration (Scale) charge unit completed - According to Calculation for Pipe Size & Length
checkpoint-status |  |  | checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | 6a0460d3-36cf-5dac-8d35-a86da5490267 |  | textbox | Drawing Reference Number
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Filters Installed
checkpoint-status |  |  | checkpoint | Unit Labelled
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | Location
text | 02bea7e5-7510-5a09-9775-423376ca965c |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Level
text | a640e7d5-0755-53b3-b427-27b28e26ca8f |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Room Number
text | 96330074-406b-57f3-8c59-11bbc62c5f31 |  | textbox | Add details
checkpoint-status |  |  | checkpoint | BIM Tag ID #
text | 316af04b-5f43-5a99-b4a5-8d0697a3949c |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Asset #
text | 63129ee9-cdac-50ea-9fc5-2c7e6504703e |  | textbox | Add details
checkpoint-status |  |  | checkpoint | Serial #
text | e691c93d-7be5-5974-b79c-10eeaac63899 |  | textbox | Add details