## Project Structure
Folder Structure |  |  | Checklists
Site QA
|  | Site plan cabling | ITR 33. Installing Underground Services (Electrical)
ITR 33C. Installing Underground Services (Comms)
ITR No.0 5 Rough in
ITP No.07 Structured Cabling Rough In
ITR No. 34 Installing Light Pole Cages
Temp Boards
|  | ZONE 1 | ITP No. 19 Installation of Temporary Power Board
|  | ZONE 2 | ITP No. 19 Installation of Temporary Power Board
|  | ZONE 3 | ITP No. 19 Installation of Temporary Power Board
|  | ZONE 4 | ITP No. 19 Installation of Temporary Power Board
Temp Lighting
|  | ZONE 1 | ITP No. 14 Installation of Temp Lights/Power
|  | ZONE 2 | ITP No. 14 Installation of Temp Lights/Power
|  | ZONE 3 | ITP No. 14 Installation of Temp Lights/Power
|  | ZONE 4 | ITP No. 14 Installation of Temp Lights/Power
Rough In
ZONE 1
ITR No. 10 Cable Tray Installation
ITR No.09 Ground In Slab Conduits
ITR No.14 Mains and Sub Mains
ITR No.0 5 Rough in
ITP No.07 Structured Cabling Rough In
|  | ZONE 2 | ITR No. 10 Cable Tray Installation
ITR No.09 Ground In Slab Conduits
ITR No.14 Mains and Sub Mains
ITR No.0 5 Rough in
ITP No.07 Structured Cabling Rough In
|  | ZONE 3 | ITR No. 10 Cable Tray Installation
ITR No.09 Ground In Slab Conduits
ITR No.14 Mains and Sub Mains
ITR No.0 5 Rough in
ITP No.07 Structured Cabling Rough In
ITR No. 10 Cable Tray Installation
|  | ZONE 4 | ITR No.09 Ground In Slab Conduits
ITR No.14 Mains and Sub Mains
ITR No.0 5 Rough in
ITP No.07 Structured Cabling Rough In
| WOOLWORTHS |  | S
SAME AS ABOVE
S
ITP No.07 Structured Cabling Rough In
Cut Out
|  | ZONE 1 | ITR No.02 Cutout of Ceilings & Walls
|  | ZONE 2 | ITR No.02 Cutout of Ceilings & Walls
|  | ZONE 3 | ITR No.02 Cutout of Ceilings & Walls
|  | ZONE 4 | ITR No.02 Cutout of Ceilings & Walls
| WOOLWORTHS |  | SAME AS ABOVE
Fit Off
|  | ZONE 1 | ITR No. 18 Light and Power Fit Off
ITR No. 16 Switchboard Installation and Terminate Submains
ITP No. 13 SUB-CIRCUIT CABLING FIT OFF
ITP No. 16 EXIT & EMERGENCY INSTALLATION & TESTING
ITP No. 08 STRUCTURED CABLING FIT OFF
|  | ZONE 2 | ITR No. 18 Light and Power Fit Off
ITR No. 16 Switchboard Installation and Terminate Submains
ITP No. 13 SUB-CIRCUIT CABLING FIT OFF
ITP No. 16 EXIT & EMERGENCY INSTALLATION & TESTING
ITP No. 08 STRUCTURED CABLING FIT OFF
|  | ZONE 3 | ITR No. 18 Light and Power Fit Off
ITR No. 16 Switchboard Installation and Terminate Submains
ITP No. 13 SUB-CIRCUIT CABLING FIT OFF
ITP No. 16 EXIT & EMERGENCY INSTALLATION & TESTING
ITP No. 08 STRUCTURED CABLING FIT OFF
|  | ZONE 4 | ITR No. 18 Light and Power Fit Off
ITR No. 16 Switchboard Installation and Terminate Submains
ITP No. 13 SUB-CIRCUIT CABLING FIT OFF
ITP No. 16 EXIT & EMERGENCY INSTALLATION & TESTING
ITP No. 08 STRUCTURED CABLING FIT OFF
| WOOLWORTHS |  | SAME AS ABOVE
Commissioning
|  | ZONE 1 | ITR. 12 Switchboard Commissioning
ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM
|  | ZONE 2 | ITR. 12 Switchboard Commissioning
ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM
|  | ZONE 3 | ITR. 12 Switchboard Commissioning
ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM
|  | ZONE 4 | ITR. 12 Switchboard Commissioning
ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM
ITR. 12 Switchboard Commissioning
ITP No. 09 STRUCTURED CABLING TESTING CERTIFIED SYSTEM
| WOOLWORTHS |  | SAME AS ABOVE
Temp Boards (Decommission)
ZONE 1
ITP No. 20 Decommission Temporary Power Board
|  | ZONE 2 | ITP No. 20 Decommission Temporary Power Board
|  | ZONE 3 | ITP No. 20 Decommission Temporary Power Board
|  | ZONE 4 | ITP No. 20 Decommission Temporary Power Board
DLP
| Preventative Maintenance Checklist |  | PMC 6 Month
PMC 12 Month
| Exit & Emergency | Initial/PC
Exits
Emergencies
6 Month
Exits
Emergencies
12 Month
Exits
Emergencies
Site Induction

## Resources
type | name | value
checklist | ITR No.0 5 Rough in
checkpoint | Area clear, tidy and accessible
checkpoint | Rough in of all lighting circuits- inc Emg/Exits and sensors fed from demoltion zone
checkpoint | Rough in of all external lights fed from demolition zone
checkpoint | Rough in of all power circuits Fed from demolition Zone
checkpoint | Rough in all lighting feeds and label on plan that are fed from demoiltion zone
checkpoint | Rough in all power feeds and label on plan that are fed from demolition zone
checkpoint | Check for clashes with other services
checkpoint | Level fire caulked by contractor
checkpoint | Ensure area is left clean
checklist | ITR No.7 - Ground Fit Off
checkpoint | Area clear, tidy and accessible
checkpoint | Fit off all Lights
checkpoint | Fit off of 4 pin plug
checkpoint | Fit off all Sensors and SET TIME TO MINIMUM
checkpoint | Fit off all EX/EMG’s
checkpoint | Label all EX/EMG’s as per plan number
checkpoint | Fit off all GPOs
checkpoint | Fit off of all isolators (signs, hand dryers, hws)
checkpoint | Ensure all fit off has been ticked off on plans once completed
checkpoint | Ensure area is left clean
checklist-flat | ITR. 12 Switchboard Commissioning
checkpoint | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure And All Steps Undertaken To Ensurecompliance With This Procedure
checkpoint | Refer To As Installed Drawings
checkpoint | Obtain Copy Of Switchboard Schedule And Schematic Drawings
checkpoint | Mark Up Any Additions Or Deletions Found Whilst Commissioing
checkpoint | Complete Visual Checks
checkpoint | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below
checkpoint | Complete Mandatory Tests Using Metrel Tester, Save And Log Results On Tester
checkpoint | Any Failed Results To Be Rectified Saved And Logged On Tester
checkpoint | Ensure Correct Opertation Of All Control/Equipment Installed In Switchboard
checkpoint | Ensure Vast Witness Test Has Been Completed
checkpoint | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated
checkpoint | Ensure No Access To Live Parts
checkpoint | Complete Switchboard Schedules On Vast Template, Install And Fix To Allocated Postion In Switchboard
checkpoint | Download Test Results From Metrel Tester And Save To Project Folder
checkpoint | Complete Certificate Of Electrical Safety And Save To Project Folder
checklist | ITR No.02 Cutout of Ceilings & Walls
checkpoint | Confirm sizes off all fittings prior to cut out
checkpoint | Cut out for all sensors, EX/EMG, light fittings
checkpoint | Cut out smoke detectors
checkpoint | Cut out kitchen to kitchen plan
checkpoint | Cut out switches, GPO's & Comms Riser GPO’s
checkpoint | Cut out Bathroom and Study Led Strips Fig 8
checkpoint | Cut out any CCTV cameras
checkpoint | Ensure AC isolator is in correct position
checkpoint | Ensure Wall light is in correct position
checkpoint | Ensure kitchen outlets are in correct position (where applicable)
checkpoint | Ensure Electric Strike cable is inside the pressed metal frame cut out
checkpoint | Locate all cables ( including Smoke Detectors & Pendants )
checkpoint | Install Fire Boxes and hit all 4 tabs in
checkpoint | Fire caulk kitchen cables ( if applicable )
checklist | ITP No. 20 Decommission Temporary Power Board
checkpoint | Determine what the temporary board is controlling and confirm what action is required before board can be decommissioned.
label | De-commission form issued to builder, 48 hours notice to be given
checkpoint | Sign off builders checklist
checkpoint | Safety Committee Inspection
checkpoint | Final approval to be given by builder
checkpoint | Perform voltage test to ensure power supply has been isolated
checkpoint | Disconnect supply cables
checkpoint | Fire sealing of penetrations
checkpoint | Remove temporary board
checkpoint | Update temporary power board register
checklist | ITP No. 29 Installion of Electrical & Communication Pits
checkpoint | Inspect pits for any damage on arrival to site
checkpoint | Mark out pit locations and alignment/arrangement
checkpoint | Check finished heights of pits against civil drawings/finished floor height
checkpoint | Erect pedestrian barricading
checkpoint | Excavate ground around pits as required
checkpoint | Place bedding material as per pit installation requirements
checkpoint | Cut out pit entry as required
checkpoint | Install puts in ground (using correct lifting equipment)
checkpoint | Check finished heights of pits against civil drawings
checkpoint | Install relevant conduits
checkpoint | Backfill and reinstatement of ground
checkpoint | Check stabilised FCR backfill 200mm below proposed road level, compacted FCR above that
checklist | ITP No. 19 Installation of Temporary Power Board
checkpoint | Area accessible & ready
checkpoint | Locate & fix into position, bolt temporary board down with at least 2 fixings
checkpoint | Install submains cabling as appropriate eg: glands/tray/duct
checkpoint | Install lugs and terminate
checkpoint | Any cables not terminated prior to energisation must be removed from cubicle at origin and have ends covered in heat shrink. At destination cables must be covered in heat shrink and be contrained in a junction box
checkpoint | Clearly identify services
checkpoint | When ready to energise proceed in accordance with energisation procedure
checkpoint | Energise & record results on Vast RCD test sheet
checkpoint | Install A3 laminated sign on face of temp board with floor plan and where the board is fed from
checkpoint | Update Temporary Power Board register & save to project folder/design control/temp const.
label | Lodge non prescribed certificate of electrical safety
label | RCBO'S must be fully tested initially and then tested every month with results recorded and c/b’s labelled
checklist | ITP No. 14 Construction Wiring, Installation, Test and Tag & Removal
checkpoint | Area accessible & ready
checkpoint | Refer to temporary wiring setout plan
label | CABLING MUST BE SUPPORTED AND PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES. TEMPORARY WIRING MUST NOT BE INSTALLED WITH PERMANENT CABLING
checkpoint | Fit off plug base and or powerpoint/isolator
checkpoint | Install light fitting, exit/emg, power
checkpoint | Terminate cable to temp board. Ensure temp board is isolated! Test Test Test
checkpoint | Test & commission
label | Lodge non prescribed certificate of electrical safety
checklist | ITR No.09 Ground In Slab Conduits
checkpoint | Determine origin and destination
checkpoint | Check clear of other services, penetrations etc
checkpoint | Check cable size to verify conduit size
checkpoint | Check if expansion joints are required
checkpoint | Mark out positions of junction boxes and penerations whee necessary
checkpoint | Install bar chairs where necessary
checkpoint | Install junction boxes and penetrations where necessary
checkpoint | Install junction boxes and conduits glue
checkpoint | Tie conduits securely at all joints and midpoints
checkpoint | Ensure all conduits are 50mm above deck
checkpoint | Mark up drawing of conduit runs (if required)
checkpoint | Observe conduits when concrete is being poured
checklist | ITR 33. Installing Underground Services
checkpoint | Inspect conduit material to check that it meets material specifications
checkpoint | Check conduit alignment as per plans
checkpoint | Set out marked, and all services located
checkpoint | Erect pedestrian barricading as per plan
checkpoint | Check excavation depth against proposed road level
checkpoint | Excavate to the trench as per plan
checkpoint | Place specified bedding material in trench
checkpoint | Placement of conduit of specified size in accordance with specifications/drawings
checkpoint | Backfill over conduit to 300mm
checkpoint | Install cover slabs over conduit
checklist | ITR No.14 Mains and Sub Mains
checkpoint | Measure cable runs with appropriate accurate measuring instrument eg: tape measure, wheel, rope in conduit
checkpoint | Confirm length of cable
checkpoint | Install cable in applicable method eg: cable stands, electric winch, pulleys etc
label | Any cable not terminated immediately must have the end taped covering the bare copper
checkpoint | Trefoil (refer to details on back for all options) cables and tie cables to support system
checkpoint | Check cable requirements for cable identification and install