## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 942065cb-d777-4656-8aff-4e2afaf9f151 |  | checklist | ITP No. 05 Switchboard Delivery |  |  |  |  | Yes | ITP No. 05 Switchboard Delivery | 0f95d412-e08b-4cf8-b3d4-7f4b6c9b2d80
checkpoint-status | 097a4350-1741-4d06-9542-6ff17576711f |  | checkpoint | Prior to delivery visual inspection by foreman to coordinate delivery on site
label | fe0ee135-358a-5bcc-baf0-2ff33ea6314c |  | note | Determine method of unloading eg. crane, forklift, man power, specialist subcontractor & arrange
label | cacf7da2-49ea-5a1d-b43c-b3f4a3b27899 |  | note | Coordinate time of delivery
label | 7931900e-2fb9-5af6-bf49-4d4634b3d643 |  | note | Positioning into place eg. crane, forklift, rollers, manual, specialist subcontractor. if vast electrical vic are positioning main switchboard, maneuvering kit is to be delivered with the main switchboard. Distribution boards require lifting trolley
checklist-flat | a7020310-b59f-40ca-8a15-18180a407d65 |  | checklist | Toolbox Meeting |  |  |  |  | Yes | zSYS - Toolbox Meeting Checklist V1 | 11d215b6-0199-4404-953b-8fc914e2218f
checkpoint-status | f1ea0fc8-6885-4170-ae64-b23847a468a2 |  | checkpoint | Details
text | 5f1a7e7a-ab8c-5e4a-a16f-00a5e98c6c27 |  | textbox | Supervisor
boolean | e013d24b-ba44-549e-bdc8-b2faeeb72859 |  | tickbox | David Interligi
boolean | 35e0b83d-ad8a-5f42-84c4-cd4275673277 |  | tickbox | Michael Borg
boolean | 6590847e-6909-5752-b67c-ed3a338ca5d0 |  | tickbox | Rob Pellegrino
boolean | 02f88a85-ee3d-582a-b90e-398c41bbca6b |  | tickbox | Adrian Sibbing
boolean | 3365848b-5ce7-58c6-87fd-db7439599ccc |  | tickbox | John Wolosz
boolean | 1efa7ac7-3ea8-5812-b07e-b8e42236f0b9 |  | tickbox | Lochy Brannelly
boolean | db630244-097f-5cc8-bd2c-ce39e092c2f4 |  | tickbox | Damon Guy
boolean | 57876400-8f5e-5378-bed4-38173cca9798 |  | tickbox | Jake Condon
boolean | 8194a72b-f11c-5f75-ac94-bd21da5ddf58 |  | tickbox | Julian Cannata
boolean | 743bfe77-618c-5d1d-90db-57ef42f27dd2 |  | tickbox | Devilliers Duvenage
boolean | 439bb08a-ec4d-501f-8fb1-2c93ee8a1382 |  | tickbox | David Currie
boolean | 01e81fc1-29a3-58c7-a367-21ebffa7c374 |  | tickbox | Steve Price
label | a151a57c-688b-5752-b9ad-e7d8a7d6c5bc |  | note | Topics discussed
boolean | fd26b6e5-18dc-5d9d-9f97-baeb70cf8def |  | tickbox | Injuries, near misses & incidents
boolean | 90306640-533e-5893-9db4-9b4e24ee2fdf |  | tickbox | Management of major hazards
boolean | 1a6d58d8-7c73-5d9c-b5d5-6e3de2966006 |  | tickbox | Compliance with Vast SWMS
boolean | 008e5c6d-0007-5e77-ac45-feb378a05c0b |  | tickbox | Safety
boolean | 9ea08a2a-9117-572b-b537-4c104905cd49 |  | tickbox | Housekeeping
boolean | 97d2983b-8bbc-5c67-9739-a579f2f9be1c |  | tickbox | PPE (Glasses & Hard Hat's on at all times)
text | 620e95c0-0275-51b7-9b94-0b1cb15ebc03 |  | textbox | Actions from last meeting:
text | c21ee053-2296-57a7-bc41-00c22d24aeba |  | textbox | Injuries, Near Misses and Incidents since last meeting:
text | 37fd2546-d75b-509e-b6bb-d7875daef3b5 |  | textbox | Management of major Hazards and High Risk Activities:
text | 5bc28950-37e0-5828-a6b3-57139c439173 |  | textbox | Compliance with SWMS & Risk Assessment Booklets or Forms:
text | fcd798cd-28ac-5d47-a096-a06ecf963478 |  | textbox | Reviews of any Safety Forms, SWMS, Policies, etc
text | 9881fae8-4878-5a90-a37f-edc3ed203d07 |  | textbox | Comments/issues from the floor:
checkpoint-status | fb24dae8-5cab-46ea-abf9-868490e15a09 |  | checkpoint | Signed off by Supervisor
text | c8dac144-8c18-5978-b666-e698bb6792d6 |  | textbox | Corrective actions
checklist-flat | 01b5e3fb-9585-450a-adb5-d421f69dc932 |  | checklist | ITP. No 04 Conduit / Cable Tray |  |  |  |  | Yes | ITP No. 04 Conduit / Cable Tray | 145e1517-9123-43e1-8347-6704d5f65cbb
checkpoint-status | 7d52b28a-d232-478e-a233-a416449746ef |  | checkpoint | Coordinate with other services
checkpoint-status | 00021ec4-05fe-4b2b-97d9-cf3f5c34be30 |  | checkpoint | Ensure segregation from comms / data services
text | 03c7caeb-4c2a-5713-9d67-83afa233bcb8 |  | textbox | Size and type of conduit
checkpoint-status | cbf58bd3-1d0c-4936-a00e-7c7284cb4602 |  | checkpoint | Install conduit fittings
text | c356a9ec-d944-5fa6-b1e8-ba47d6f22867 |  | textbox | Size of cable tray
checkpoint-status | 3498c484-3223-4348-b681-00efe89629fa |  | checkpoint | Install fittings
checklist-sectioned | 45e1ab3b-55e7-45ca-a9c8-2a2b2771cb91 |  | checklist | Vast Employee Induction |  |  |  |  | Yes | Vast Employee Induction | 1723aaf5-ce48-4bfa-b011-50f228fc410a
checkpoint-group | 6b09ba1d-c864-4d67-9d64-e892bb076618 |  | section | I have been provided an explanation about
checkpoint-status | 3a7b69e9-5a38-47bd-affc-039df76b629c |  | checkpoint | Provide to your new employee an explanation about:
boolean | 6c08b783-aeef-5449-b01d-72c5dfbefb98 |  | tickbox | The industry, nature and structure of your business
boolean | 48ce53f8-8cbb-5991-a912-64c4933739a6 |  | tickbox | Roles of key people in your business
boolean | 3f2bc942-d04f-5ea3-b10d-8ede362d2efb |  | tickbox | Job, tasks and responsibilities position description
checkpoint-group | c2c72d55-3a73-4728-ab3b-4990e366f725 |  | section | The following conditions have been explained
checkpoint-status | ef7674c0-9dd1-4131-8ea8-054f93c18ba6 |  | checkpoint | Explain to your new employee about:
boolean | 52d56fd0-f8a4-58b0-bd1d-2bfed3fed7f0 |  | tickbox | Work times and meal breaks
boolean | b6006371-9c5a-5be4-935d-307edf22ee72 |  | tickbox | Notification of sick leave or absences Timesheets
boolean | cabd38cf-9faf-53bd-ad4b-a98ade44aee2 |  | tickbox | Timesheets
boolean | 4feb3fad-71a9-5f57-be41-495b15e05474 |  | tickbox | Network Drives (if applicable)
boolean | ebbe8b8c-9bd2-5b62-a0be-41554908a88e |  | tickbox | Apprenticeship Contract (if applicable)
checkpoint-group | 018d38fc-b7ec-4b0c-97b0-d34455f2b744 |  | section | I have read and acknowledge the HSEQ induction
checkpoint-status | fa54bf68-bce1-4834-914e-78296f8537d1 |  | checkpoint | Please review health and safety
boolean | 890205f2-a99b-5c6e-887e-09e75eb16d52 |  | tickbox | Safety Policy, Environmental Policy and Quality Policy
boolean | 55e795b6-3854-58ce-ad0e-8835b61540e0 |  | tickbox | Site Safety Instructions and Work Instructions
boolean | ea27e644-94c6-502d-a25c-51aa990d0941 |  | tickbox | High Risk Activities and SWMS
boolean | eedd5f35-4540-5afb-86f3-b630f6637a3f |  | tickbox | Consultation & communication
boolean | 3fb20f2d-2553-58d4-9c9c-cdcf8b605b83 |  | tickbox | WHS responsibilities & Environmental responsibilities
boolean | 1b609027-2c03-5f8e-adb9-f80688a30dbe |  | tickbox | Emergency procedures
boolean | 3c9b72a7-e7bd-54bd-baf8-1b4bf9b0ee25 |  | tickbox | Reporting hazards (Risk Assessment Booklet)
boolean | adbed5e4-1199-54c2-beff-1569f2687541 |  | tickbox | Reporting safety & environmental incidents (Injury/Incident/Accident Report)
boolean | 1aa3ce58-a689-52ba-93e7-7044f51c87b9 |  | tickbox | Location of exits, equipment and First Aid Kit
boolean | 96cd86dd-1971-500e-8dde-b105d3e910f3 |  | tickbox | How they will be kept informed about health and safety issues
checkpoint-status | 96bd5764-33bd-48a0-929b-a1b769ec0c82 |  | checkpoint | Have your new employee complete and sign all necessary documents including:
boolean | bd80fe8d-c7a1-5a4c-9873-34eb49caba95 |  | tickbox | Personal Data Sheet
boolean | 31b7577b-502a-56e9-872f-64c7dc0c3e84 |  | tickbox | Contract Signed & Returned
boolean | 0bde50aa-2ede-5e32-a5bd-28b683199c16 |  | tickbox | Company Policy Statement
boolean | f943f740-8001-5583-80db-ffc7c75da9d0 |  | tickbox | Taxation (include filling out required forms) Superannuation Contribution Form/Super Choice Form
boolean | 41a15473-3013-5e39-9be0-a2830d38cc9f |  | tickbox | Superannuation Contribution Form/Super Choice Form
boolean | b59e9d04-ab65-57e6-b406-4a242db52dcf |  | tickbox | Uniform Form
boolean | aa57fea1-abeb-5ab7-91e9-cdf83885e063 |  | tickbox | Copy of Drivers Licence
boolean | 8706dfc5-1d2f-57df-ba29-e56f727fba96 |  | tickbox | Fairwork Statement
boolean | eb3e7d9c-0494-5e0e-8726-4d04b1b9f823 |  | tickbox | NECA Red Book (Apprentices)
checkpoint-group | ffb1dcdc-f985-406f-a303-8b6a1f3bcb32 |  | section | Induction Sign Off
checkpoint-status | 15947634-eec2-4909-9e11-115dc8d378eb |  | checkpoint | Induction completed, please type name & position, please sign on screen
label | bfb3d9ac-763c-59b6-a2ed-404f0e5d31a7 |  | note | I hereby acknowledge receipt of Vast Electrical Services Pty Ltd induction booklet and I have read and understood the company induction & agree to comply with these Rules and any Statutory or Site Requirements.
label | 4d7a5366-a130-5723-85c1-fda32b6e6d49 |  | note | Should I have any safety concerns whilst working Vast Electrical Services Pty Ltd I agree to seek clarification from my immediate supervisor
checklist-flat | a79d5182-4b77-453e-aa8c-6f16f5f695ad |  | checklist | Pre Start Meeting |  |  |  |  | Yes | Add Pre Start Meeting Checklist | 172a2f7d-a310-48de-a4ff-4ed1d919c6e6
checkpoint-status | 2bcda5fd-e342-46c6-9d75-1ca983557bf6 |  | checkpoint | Details
text | 108d9c54-fa00-58d9-aad6-55a00435e049 |  | textbox | Conducted by
text | 11f7eced-d7c4-5634-9a5b-42f40edbf45b |  | textbox | Area
checkpoint-status | 2a772b97-a2e6-407f-ac1c-352712648302 |  | checkpoint | Any Safety Concerns from last meeting - add comments if required
text | 68b55c49-bcfc-5353-b223-3ea6c2bbb94c |  | textbox | Today's weather
text | ff44e96d-6d1d-57ad-905b-ae776dc13388 |  | textbox | Today's work is
text | 82614f96-d108-5771-ab4d-517bc6edebe9 |  | textbox | Newly Identified Hazards Are
text | 0285b4c0-52cd-543e-9c11-6619e7279637 |  | textbox | Control measures are
checkpoint-status | cc4ab476-a5fd-452c-9d61-7beb3f3b485e |  | checkpoint | Scope of work for the day was discussed and understood
checkpoint-status | 27f95047-d008-45ce-ac8f-1522c08a3214 |  | checkpoint | Major High Risk Activities are understood and controlled in a SWMS
checkpoint-status | 1b535f32-f037-4929-b81f-a3ea2a3f0a0a |  | checkpoint | Relevant SWMS were reviewed, understood and signed by all workers
checkpoint-status | 27f0b807-bea5-4dd2-a088-c840880ca08e |  | checkpoint | Relevant Permits to Work are in place and understood
checkpoint-status | f63cc9d6-0565-4af1-9229-148bdbc6c3b3 |  | checkpoint | Tools and equipment are in good working order
checkpoint-status | 22dda3f1-b6af-40dd-822c-b61355ae23ec |  | checkpoint | All electrical equipment displays current test tags
checkpoint-status | bdf7bf5f-a9b8-4c6c-9130-0cdedfe05ddd |  | checkpoint | Appropriate PPE for tasks is understood and available
checkpoint-status | b2a04cc9-de5d-41ea-a7a3-7944cbe44b25 |  | checkpoint | Housekeeping and clean-up has been discussed and is understood
boolean | 8bb10d80-163b-5f69-bb6f-caca3f26139e |  | tickbox | David Interligi
boolean | ec73d7df-388f-59f0-a2c7-1e243e52ac28 |  | tickbox | Michael Borg
boolean | 917c3df5-0a15-53d4-95f3-fc073c5919c4 |  | tickbox | Rob Pellegrino
boolean | 6fb2ddfc-a104-5f1c-a2c4-8eb13d082fd3 |  | tickbox | Adrian Sibbing
boolean | 447990f2-a013-5b7f-b6a7-5d6eabdf724b |  | tickbox | John Wolosz
boolean | a8c1cdd2-7ab8-5da5-a1d3-bd7614a0a4db |  | tickbox | Lochy Brannelly
boolean | 8388cee1-2dbe-5fa3-a3c0-7ea71429b08f |  | tickbox | Damon Guy
boolean | 95076296-e4b4-5521-84a0-1515b90d463f |  | tickbox | Jake Condon
boolean | 0a10a9af-0730-5f8c-91b0-5bda05a74329 |  | tickbox | Julian Cannata
boolean | 355b6eb0-45c2-5194-bc72-3d7c2a3d4521 |  | tickbox | Devilliers Duvenage
boolean | 41f83a5d-ec84-5a4d-8f53-c1cd532fee3d |  | tickbox | David Currie
boolean | b6eae548-8509-554e-9e1f-5b27a8e36ee5 |  | tickbox | Steve Price
checkpoint-status | 79a176fe-5859-4023-a0ad-5027fc7f7424 |  | checkpoint | Signed off by Supervisor
checklist-flat | 2e46cbb3-a806-4cb7-af7c-b57d550971f1 |  | checklist | ITR No.3 Apartment - Electrical Fit Off |  |  |  |  | Yes | ITR No. 03 Apartment - Electrical Fit Off | 1a1b5e78-f6dd-4b23-8eb9-f08c8bdbd881
checkpoint-status | 03cdc7c8-9d4a-4177-a197-b85b1a4e49d0 |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | ba93f141-e489-4bab-b9e9-b8921b959f10 |  | checkpoint | Drawing Rev No.
text | c52cb059-6814-5f32-9340-165b50c2da36 |  | textbox | Drawing Rev No.
checkpoint-status | c666638a-5c36-456a-bec1-f7b633127609 |  | checkpoint | Fit Off Downlights
checkpoint-status | 306244d9-c534-4940-9c0a-b709f763f1be |  | checkpoint | Fit Off Smoke Detectors ( leave tab & dust cover on )
checkpoint-status | 54337a4d-0a7d-48c3-b10f-75c739a87901 |  | checkpoint | Fit off joinery GPO's & install cover plates.
checkpoint-status | 9c1ea594-9ea8-4374-ac7c-8b0e9cd4dad9 |  | checkpoint | Fit off Laundry GPO & switch
checkpoint-status | ed33bd2c-518a-43e4-bdb5-1f0384268a17 |  | checkpoint | Fit off TV Point
checkpoint-status | 3945e303-9148-4186-9671-26e7c0fa4753 |  | checkpoint | Fit Off Data Points
checkpoint-status | 419ce6df-5864-48e1-b256-e4a27af90239 |  | checkpoint | Fit off Balcony Light
checkpoint-status | f5b8986c-7dff-4652-b70c-7934aa41eed5 |  | checkpoint | Fit off AC Isolator
checkpoint-status | 70ca5d79-867b-497c-9dc1-9d60f12edd5c |  | checkpoint | Fit Off WP GPO ( if applicable )
checkpoint-status | f4e00515-357d-42a9-a922-5f9abf8d5ccc |  | checkpoint | Fit Off LED Strips
checkpoint-status | 1e6b9c3e-a45f-47de-8999-5283fc2cc6a0 |  | checkpoint | Fit Off Pendent
checkpoint-status | 421fc25c-53e4-477d-b45e-f13152cbcb0a |  | checkpoint | Install Oven
checkpoint-status | bccdfe94-e156-4528-ae3c-93e4e74b265e |  | checkpoint | Ensure area is left clean
checklist-flat | fed9f1c7-a62d-4dee-b65a-793cf69e39b9 |  | checklist | ITP. No 09 Communications - Data & Voice Cabling |  |  |  |  | Yes | ITP No. 09 Communications - Data & Voice Cabling | 1ddc9921-9d52-4e44-a53a-9091e21a3212
checkpoint-status | 33921c4c-e097-46ba-8897-38fa50cc3f0a |  | checkpoint | Obtain the relevant and most recent drawings and specification
checkpoint-status | 23e0d5f1-0477-4193-99f3-f42ba4ff5849 |  | checkpoint | Install cable support or conduit where required
label | cdf68592-f9e7-5ebc-ab25-96fb4498beae |  | note | Verify correct cable type
label | 4fc0f77e-dfaf-54a3-9c8e-c531d482ae97 |  | note | Decide appropriate cable numbering sequence relevant to final fit off sequence
checkpoint-status | 681ff54c-5594-40a5-8eed-c24f0dc3d5a2 |  | checkpoint | Install cable within or on cable support system as appropriate
checkpoint-status | 15db011e-ff2a-435c-835e-f98cd1e48ddc |  | checkpoint | Form cables into relevant fit-off groups at the cabinet end
checklist-sectioned | 26fb743b-68ce-44e1-b059-701257c41c91 |  | checklist | ITP No. 01 Conduit in Slab |  |  |  |  | Yes | ITP No. 01 Conduit in Slab | 1df8eec7-235e-4491-be94-b986d3ab9a5f
checkpoint-group | 3a50a0f2-e275-4b70-865e-c014d6f35030 |  | section | Preparation
checkpoint-status | 14d4a8de-3f6d-4470-9041-465ee22433ab |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | 072ff780-ed0f-4b6d-b122-5994d023c81f |  | checkpoint | Drawing Rev No.
text | a84fff2c-e61f-501a-9c13-2576ab3318ae |  | textbox | Drawing Rev No.
checkpoint-status | e1e875b4-c224-4cf2-bd2f-7a53c2858a86 |  | checkpoint | Determine origin and destination of riser cupboards
checkpoint-status | 93af1630-0567-4d10-9c97-9f3de8344a3b |  | checkpoint | Check clear of other services, penetrations etc
checkpoint-status | ba3e3853-5e5c-4093-ada8-a4dac519a7dd |  | checkpoint | Check cable size to verify conduit size
checkpoint-status | 694db822-a65a-4c1b-bda3-4d2b79c5918c |  | checkpoint | Mark out positions of junction boxes, orange flanges and penetrations where necessary
checkpoint-status | 98b78427-b565-4bf1-acec-2b183babfff9 |  | checkpoint | Check if expansion joints are required
checkpoint-group | 764255f5-c510-47cd-8423-fc7e92bba69b |  | section | Installation
checkpoint-status | 909bfdb0-abee-4aec-9ab0-84da20494d4a |  | checkpoint | Installation of sleeves for stair lights
checkpoint-status | 12bd26c7-a513-40ab-a4f3-686b3352877a |  | checkpoint | Installation of sleeves through the core
checkpoint-status | 868f91c4-6e70-4dcf-b308-1b3b8c7e0b47 |  | checkpoint | Installation of foam at riser cupboards if applicable. Foam to be duct taped and secured down to deck.
checkpoint-status | 8c4b3963-d68f-4c2a-8161-433182aeb2ce |  | checkpoint | Install junction boxes, flanges and conduits with glue
checkpoint-status | ef1813cb-39a8-411f-a3db-deb045194c0a |  | checkpoint | Install reo turned up in riser cupboard for earthing of the slab
checkpoint-status | eb6492ed-0d21-4f2f-b660-e11afe195ebc |  | checkpoint | Install any temp conduits where necessary for alimak lighting and temp toilets
checkpoint-status | 97cfb283-e758-4a71-976f-6710f7a04603 |  | checkpoint | Ensure all conduits are 50mm above deck
checkpoint-status | 14d931fc-2442-4e2b-bc9d-06146f7376ed |  | checkpoint | Ensure all conduits are tied and secured
checkpoint-status | a8b1730f-2d64-4b62-a8b6-c5e0bd2b6d6f |  | checkpoint | Ensure all conduits for the next pour are through to the next deck
checkpoint-status | fcf1544e-6520-4abc-8aab-d54c1de3a119 |  | checkpoint | Clean any mess left on deck
checkpoint-status | d805fb6b-c29b-4d44-a1b7-6a76fd10234e |  | checkpoint | Final walk through and mark up plan of conduit runs for as builts.
checklist-flat | 2d76e466-3ee6-4377-9e29-f369e9aba0d7 |  | checklist | ITP No. 14 DB Test Results |  |  |  |  | Yes | ITP No. 14 DB Test Results | 1e07405c-53ec-4731-9e07-5ca0800dbe95
checkpoint-status | 43ab57f8-2f73-4253-b2ea-cfdec91083a0 |  | checkpoint | Visual inspection
text | 5f4abc1e-9c8e-53a3-af66-c037c7b9bff1 |  | textbox | Vast testing device number
text | 4343d93f-6209-53b3-902e-4e561131cf72 |  | textbox | Cert. electrical safety number
text | 6fe21856-11f0-5d51-a4d1-8562313e9ace |  | textbox | Number of Lights
text | 562d4d8e-0c31-572e-a247-3793a1fb55f8 |  | textbox | Number of GPO's
text | d9ebd074-7303-5e34-b4e0-8f0779dd4f43 |  | textbox | Earth & continuity resistance
text | a91b6147-4cb1-5d8e-86ca-3156915405b5 |  | textbox | Insulation resistance
checkpoint-status | 8b0d93ff-697e-4ba3-bb45-17386e8bd9d7 |  | checkpoint | Polarity / correct connections
text | b49d999c-afa7-5af4-b39e-7779798c65b0 |  | textbox | Earth loop impedance
checkpoint-status | 3fcc6f83-86d3-4250-8360-b6da4b75b2a1 |  | checkpoint | RCD testing contractual requirement
checklist-flat | 43840691-3640-42d7-81f1-4e45c6824dbc |  | checklist | Documents |  |  |  |  | Yes | Documents | 28c8a995-52f6-46dc-8914-179d2de80131
checkpoint-status | 0d32b920-3b40-4aac-aa40-13e45a1c0c35 |  | checkpoint | Attach Document
checklist-flat | 4133d766-35cd-4267-8a26-b7393b02e007 |  | checklist | ITP. No 08 Communications - Data & Voice Termination |  |  |  |  | Yes | ITP No. 08 Communications - Data & Voice Termination | 2e69ac13-dbbc-419d-a812-103bdbd34e31
checkpoint-status | 18d10b04-ea9c-4e2e-bdc1-cd295a6b5b7d |  | checkpoint | Visual check ensuring cable to be fitted off in correct position
checkpoint-status | 43e54b12-18c6-4234-87e5-45b7d8d3c4fc |  | checkpoint | Selection of correct tool to be used for termination type
checkpoint-status | 2ffad2a4-bc50-48ab-9bee-77784e837a7a |  | checkpoint | Ensure cables are stripped no more than the specified distance
checkpoint-status | 6e3a5eff-3a2e-4fb1-b49b-5ec158062560 |  | checkpoint | Check terminations at completion for colour code and sequence
checkpoint-status | d594dc94-3843-4361-9cf9-4bc1d019cac1 |  | checkpoint | Label outlets
checkpoint-status | 78f0e962-06ac-47fa-8c7d-18669ea45b9e |  | checkpoint | Patch outlets to hardware devices where applicable and check for correct operation
checkpoint-status | c1b64272-031e-4954-b384-c42377eaecef |  | checkpoint | Complete certification if required
checklist-flat | 620ba6be-2e76-4d5d-90de-10b325d33a89 |  | checklist | VAST Site Induction |  |  |  |  | Yes | zSYS - Add VAST Site Induction (old version) | 3891b90f-7517-4df5-a580-4b6fd0f19254
checkpoint-status | 78797650-19f0-43cf-b4a3-feda22bbf131 |  | checkpoint | VAST Employee
text | ef74e485-6a60-587c-91bb-5c8969fbfee1 |  | textbox | Name
text | 9cbdae28-8873-55e4-9b48-f613b92b6948 |  | textbox | Contact Number
text | c03f7700-3d89-55e2-b36d-44cfa4924019 |  | textbox | Date of Induction
label | 4179b79a-f4cc-5d6b-9621-779e9451d4f1 |  | note | Tick if the following are understood:
boolean | a6603cb7-de4a-586c-9840-9cf936e5b258 |  | tickbox | How to report to the site and who you report to
boolean | 5acc0dbb-4977-5efc-98ea-d27c97c1c006 |  | tickbox | The working hours on site
boolean | e0061ff0-a503-5afd-983b-501d8f1ef83f |  | tickbox | Who the managers and supervisors are on site
boolean | cf3a09cf-eea8-58da-a6d4-f326f6558737 |  | tickbox | The correct minimum PPE for site
boolean | 7b62aa78-7329-5b55-88b1-d44d71815d9a |  | tickbox | How safety is communicated on site
boolean | 767aa5a5-529c-5d09-9dd8-a051bd3aaa4b |  | tickbox | Where to have lunch and where the toilets are
boolean | 1db68ef8-8ff9-50ac-b619-e11d48926d2e |  | tickbox | Where the First Aid Kit is kept and who is the First Aider
boolean | cc3bab0d-d53d-5e5c-b894-4aaa905e69cc |  | tickbox | The Emergency Plan and the Assembly Area for Emergency Evacuation
boolean | 22bb7ed0-419f-5e7c-be65-47c5cf1c4693 |  | tickbox | What the high risk activities and hazards are on site
boolean | 6efbf997-d08c-524e-8859-4dfecb9151f5 |  | tickbox | How to report WHS & Environmental hazards & issues
boolean | 0a541d72-e908-5493-bec7-1ac8b689323f |  | tickbox | How to report a safety or environmental accident or incident
boolean | 1cd4a1bd-c92c-5ac6-bda2-7212900a7b7f |  | tickbox | Housekeeping responsibilities
checkpoint-status | 49b26424-df06-4d35-8341-fe9f3b34475b |  | checkpoint | EWP Licence - Please take a photo
checkpoint-status | a49ed8ba-8d46-46b3-8d01-d25d2af6e863 |  | checkpoint | Current Certificates Sighted - Please take a photo & comment on each attached certificate
checkpoint-status | 11efe7be-16b2-4617-8803-44a8f3257358 |  | checkpoint | VAST Employee Signature
checkpoint-status | 9ffdb14a-d6de-458c-919b-41344d26fd18 |  | checkpoint | VAST Supervisor Signature
checklist-flat | ad5d0519-ce8d-4bf9-8825-621a934990f0 |  | checklist | ITR No.8 Hallway – Commissioning Electrical & Permanent Power |  |  |  |  | Yes | ITR No. 08 Hallway – Commissioning Electrical & Permanent Power | 3eb388f0-1ae8-446e-a5ed-417a61b83e8e
checkpoint-status | 5f7aad87-c19c-41cc-81f2-d6838a466bf0 |  | checkpoint | Energisation permit completed prior to energisation
checkpoint-status | 97f811b1-8e8f-4843-86b2-2313eb59f805 |  | checkpoint | Visual Check (against most current plan)
checkpoint-status | cd3893c7-108f-4b8a-b4a3-03918b4cdffe |  | checkpoint | Dead Testing
checkpoint-status | b6f6c237-1622-4da6-86dd-482b3f1d1493 |  | checkpoint | Live Testing
text | 188a68be-3a36-5272-9aa4-24e7749cc5c9 |  | textbox | Record Metrel Results
checkpoint-status | e44b8a11-7e8b-4927-877b-f1a5ed53972e |  | checkpoint | Check operation of all sensors (individually on minimum time setting )
checkpoint-status | e0b2b443-bd26-4ca4-876b-e720d2264105 |  | checkpoint | Check sensors are set to specified time and lux
checkpoint-status | bcb7a16a-b67e-44d6-a0c3-45ce6206ae78 |  | checkpoint | Check operation of all EX/EMG, perform 120 min test ( initial )
checkpoint-status | 4830e798-9894-41f8-92db-1b9df84d15f7 |  | checkpoint | Fit cover plates to all GPOs & exit signs
checkpoint-status | 5330ff0f-9c5c-49f5-a451-a563ec0187fa |  | checkpoint | Ensure area is left clean
checklist-flat | 6d004513-4020-4462-9768-a87fb51ea049 |  | checklist | Vast Employee Induction - Personal Details |  |  |  |  | Yes | Vast Employee Induction - Personal Details | 4520cbf0-f99f-48a4-95d6-435f8ebef94e
checkpoint-status | 4ff25597-c71a-40da-a2db-0c4b2765be92 |  | checkpoint | Attach Document
boolean | 6b53572d-ae71-59b5-87fd-c5b75f8fc0a2 |  | tickbox | A Grade
boolean | dd0aaf82-01f8-5934-b490-9822b5f75ef7 |  | tickbox | White Card
boolean | 4eda26b9-a95b-58fe-8715-4832e6d0af71 |  | tickbox | Vacc Cert
checklist-flat | 51696e7c-68f2-42fa-8e56-6b02127c66bc |  | checklist | ITP. No 12 Install DB's - Terminate Sub Main Cables |  |  |  |  | Yes | ITP No. 12 Install DB's - Terminate Sub Main Cables | 468dda79-495c-40d8-aaa2-b0ee05bf1542
checkpoint-status | 6474acb6-ef3f-41a3-afa8-9a27eaa70d14 |  | checkpoint | Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
checkpoint-no-status | dc0db123-0f30-41df-bad9-f0e017699d48 |  | checkpoint | Drawing Rev No.
text | 9098cbdf-962b-5e25-89c6-b88f56fef674 |  | textbox | Drawing Rev No.
checkpoint-status | b3371122-e41c-4261-afec-1f92256f1fb6 |  | checkpoint | Locate & fix into position
checkpoint-status | 1ab18953-87dd-4821-b5aa-0c8efb2d345a |  | checkpoint | Install sub mains cabling as appropriate eg. glands, tray, duct
checkpoint-status | 4ceb3aa3-55d4-4d50-a566-8273916eab32 |  | checkpoint | Install lugs and terminate
label | 8da70f7d-c29b-5b2e-a9e4-202fd03974a0 |  | note | Any cables not terminated prior to energisation must be removed from the cubicle at origin and have ends covered in heatshrink
label | 654cef54-d8a8-59e7-956f-91100264854d |  | note | At destination cables must be covered in heat shrink and be contained in a junction box
checklist-flat | 1de66e1b-6a26-4bd8-a098-580f5ab1f5b0 |  | checklist | ITP No. 10 Comms: Data Jack Termination |  |  |  |  | Yes | ITP No. 10 Comms: Data Jack Termination | 778c7b49-3367-4606-88c4-a9c96f478c40
checkpoint-status | 02d0f776-e28a-4ed7-b3a9-f6460e529268 |  | checkpoint | Visual check ensuring cable to be fitted off in correct position
label | 193b1493-ce90-502c-81f5-eaf8a9f89b69 |  | note | Selection of correct tool to be used for termination type
checkpoint-status | a5080e27-b7db-46e6-9aef-0484322f499b |  | checkpoint | Ensure cables are stripped no more than the specified distance
label | 3b6da24a-3c8e-500b-98f8-c1d56f0781c1 |  | note | Check terminations at completion for colour code and sequence
checkpoint-status | 68053fa1-4b0c-45b1-974a-6eb6309ad3d6 |  | checkpoint | Put stuffer cap onto jack
checkpoint-status | 20a7b812-301f-4782-881e-26f3497a1de0 |  | checkpoint | Attach wrap around label to cable no more than 60mm from the jack. Ensuring correct number sequence
checkpoint-status | ac6fcf31-7418-4141-b857-c21d24f1e621 |  | checkpoint | Install jack into workstation or wall outlet
checkpoint-status | 1708e288-ca26-41a6-b18b-98c6c246fcfe |  | checkpoint | Label outlet ensuring correct number sequence
checklist-flat | 144b06d4-e496-46dd-b7b2-0548ffce70ab |  | checklist | Toolbox Meeting |  |  |  |  | Yes | zSYS - Toolbox Meeting | 77ac75ef-f569-4101-9bce-dc8a6ebb9a67
checkpoint-status | c35130b3-ada3-4374-bdf7-1f55527e9682 |  | checkpoint | VAST toolbox meeting completed
text | 63b1bc2f-b2c6-5f9f-85b0-d9be5fe0d10f |  | textbox | Supervisor
text | 49371db3-49a1-5fc9-bd9c-69d6c828d45b |  | textbox | Persons present
boolean | edf9ec6c-d8a7-51d5-bcb7-9d26d271643f |  | tickbox | Injuries, near misses and incidents
boolean | 12355a90-5ef8-5a3d-b111-5ada48b4d141 |  | tickbox | Management of major hazards
boolean | b0282e9a-d78f-5258-abfe-2c804b60938c |  | tickbox | Compliance with our Vast SWMS
boolean | 591f07d7-d2c3-5a19-9f22-ec6f4e80ef18 |  | tickbox | Safety
boolean | 26d38d4f-b3f4-532a-a3d2-8284d19055bc |  | tickbox | House Keeping
boolean | 6abb5fe9-d1c5-5ade-8083-8675caeb600f |  | tickbox | PPE (HARD HATS & GLASSES ON AT ALL TIMES)
text | c4e1127c-e005-5711-9ffc-c9e600081598 |  | textbox | Comments
checklist-flat | 0a8dc72a-bbe3-47b8-bd2a-a408c7bc6ca0 |  | checklist | Exit & Emergency Testing |  |  |  |  | Yes | Exit & Emergency Testing Checklist | 7bdc8829-b802-46d9-9ac8-bd3f10435231
checkpoint-status | 2e3dada8-fe5a-4540-ab78-8b07cc1a6a67 |  | checkpoint | Details entered below
text | 760c235a-cac1-5615-b517-b494cec98465 |  | textbox | Start time / Finish time
select | 281669c3-0fa8-5768-be60-9d22ad7106f7 |  | dropdown | Lamp duration | 120 mins, 90 mins
boolean | c0341b15-8baf-5768-a566-3b3351ccabc2 |  | tickbox | Starter switch
boolean | 9b87ca32-59ce-57fd-bb74-c96bb1e95ad2 |  | tickbox | Charge indicator
boolean | 936c0f3d-b91a-515b-ab44-0e09e02e952e |  | tickbox | Test switch
boolean | dff84c27-ec90-509d-815e-2b4c583b8304 |  | tickbox | Circuit board
boolean | e06eba67-34ca-5b1d-b433-56514dd5eaad |  | tickbox | Clean diffuser
checkpoint-status | 0b05a618-65a6-4c70-aa80-e5530840b93a |  | checkpoint | Overall fitting
label | 96f1335e-2f32-5dcb-9ce7-5cd58b4ab6cc |  | note | Please add comments if additional action taken / other details
checklist-flat | c636586b-56f6-4f89-93e6-b6553997a105 |  | checklist | ITR No.0 5 Hallway Rough In |  |  |  |  | Yes | ITR No. 05 Hallway Rough In | 872c60e0-8c83-4c65-8d19-3d7ba581ede5
checkpoint-status | ee09223d-59f4-42f7-a1fc-0516bda54fd2 |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | 309da757-6081-40f2-b9f1-c6cd6ced24d2 |  | checkpoint | Drawing Rev No.
text | 26762b3e-2c8f-54d4-ab64-8e609f655f5b |  | textbox | Drawing Rev No.
checkpoint-status | 645c7dfc-a32e-4e7b-8cb5-84901f8e9e67 |  | checkpoint | Mark out all public L+P in hallway
checkpoint-status | 41c4e9ef-4623-4791-95bd-2265770a6453 |  | checkpoint | Rough in lighting, Emg/Exits and sensors
checkpoint-status | 73a48591-db91-472a-b1d2-b1a2bd1b6a7a |  | checkpoint | Rough in cleaners power, water meter power, window louver (CS) if applicable
checkpoint-status | d52b4524-6d63-4af3-8bd8-0130795e34ab |  | checkpoint | Rough in comms riser power
checkpoint-status | c8619ecd-e57d-4105-802b-5d1867d0fdf8 |  | checkpoint | Rough in lighting feed to first lighting point near elec riser
checkpoint-status | f45c477f-fd67-4289-886b-87c8bc0f619c |  | checkpoint | Rough in power feed to first cleaners point near elec riser
checkpoint-status | a53564ae-a1b5-4b4f-ada9-5b0d25b9b2c6 |  | checkpoint | String all comms conduits
checkpoint-status | 28ecbc50-6b77-453c-85a3-b91874a495c2 |  | checkpoint | Rough in all apartment sub mains from riser to apartment DBs and LABEL
checkpoint-status | ba472013-b644-40c6-a8af-3b13fd092b21 |  | checkpoint | Rough in stair doors access control
checkpoint-status | 281314a7-ea99-44a3-980c-307cc1fd8002 |  | checkpoint | Rough in any relevant comms/access control from one floor to another ( Backbone )
checkpoint-status | 94e15d95-4f6e-4b57-b35f-f487054560e1 |  | checkpoint | Check for clashes with other services
checkpoint-status | 10f319dc-478a-4ad0-9f20-047115c2655f |  | checkpoint | Fire caulk riser cupboard door headers ( smoke seal only )
checkpoint-status | 55814cd7-c479-4dc3-828c-ac7d0fdde817 |  | checkpoint | Fire caulk apartment door headers
checkpoint-status | 2229ef90-f680-4412-a5d4-b206d617adde |  | checkpoint | Ensure area is left clean
checklist-flat | ab2b8282-4852-4b6c-92e8-f069429878d8 |  | checklist | WHS Policies |  |  |  |  | Yes | WHS Policies | 8cf4f66d-8b5b-43dc-a07e-ad91026503cf
checkpoint-status | 52072f4c-6068-4894-b8cd-b061e97f8c90 |  | checkpoint | Attach Document
checklist-flat | 429e1490-8f9a-4b01-a394-55b4ac721fe7 |  | checklist | ITP No. 17 Construction Wiring Installation, Test & Inspection and Removal |  |  |  |  | Yes | ITP No. 17 Construction Wiring Installation, Test & Inspection and Removal | 8d1fdeb0-3890-4363-a54b-2013013323a6
checkpoint-status | 4409a74c-ba69-41af-9734-75820277a22c |  | checkpoint | Area accessible & ready
label | 13434c82-7f0b-5be2-9bba-1d71c9100ed3 |  | note | Prepare single line diagram of proposed distribution system
checkpoint-status | 93063a87-f48a-466b-bdcf-a26ab9ca0b88 |  | checkpoint | Request power distribution to conduct fault discrimination study to verify correct functionality.
checkpoint-status | 09fcd871-d6c8-481d-a407-fa6f3587ffd7 |  | checkpoint | Adjust circuit breaker sizes if required
checkpoint-status | c156ce92-e73d-4a6b-896f-4e7944753fd3 |  | checkpoint | Position and fix switchboard
checkpoint-status | 1173e092-832f-4975-a6d8-95624952e0a1 |  | checkpoint | Cabling must be supported and protected from damage. construction wiring tape must be fitted at every 5 metres.
checkpoint-status | 51147331-78e3-4aed-bdb8-27fd7d9cd7a1 |  | checkpoint | Terminate sub circuits and Sub Mains
checkpoint-status | 5439df64-5ccb-4707-abe1-493cf40859f3 |  | checkpoint | Test & commission
label | 8a8705c1-dbb5-5bd6-b4ba-6b752fdefefd |  | note | Lodge prescribed/non prescribed (as applicable) certificate of electrical safety. organise inspector (if required).
checkpoint-status | e5b6c9b7-6530-43ca-a7e2-19f48e50dfa2 |  | checkpoint | Earth leakage circuit breakers are to be used for circuit protection lights and sheds, 30 ma maximum outlets 30ma maximum
checkpoint-status | c8a65080-33aa-4c58-bb80-b7f35ec4d124 |  | checkpoint | Elcb’s must be fully tested initially and then tested every month with results recorded and c/b’s tagged
checklist-flat | ac09b392-d20e-49e5-b436-32521501b4e9 |  | checklist | ITP No. 06 Soft Wiring |  |  |  |  | Yes | ITP No. 06 Soft Wiring | 8e7db7f3-a81b-4785-8ab4-5ee771d4af8d
checkpoint-status | 704fa199-53b3-41ea-bbab-8e3a7ed0ddcb |  | checkpoint | Delivery check for damage
checkpoint-status | 271c5a6e-1f7e-44e8-8979-a7155d32f263 |  | checkpoint | Install hard wiring termination point
checkpoint-status | a407acdc-4994-4fa5-9b93-3f17091c3456 |  | checkpoint | Terminate cable at termination box
checkpoint-status | 0039a6e9-da63-4a2f-b5d9-3b91b0c3630d |  | checkpoint | Loop flexible lead from termination box to light switch, sensor or outlet as required
checkpoint-status | c2bca54e-33d1-47e7-8eed-0878dc8c9fae |  | checkpoint | Test and commission
checklist-flat | 8357bc08-7a93-42fc-8363-27db83d5107b |  | checklist | Exit & Emergency Testing checklist V2 |  |  |  |  | Yes | Exit & Emergency Testing checklist V2 | 8f3c8c7a-2ed3-44de-8b33-837a82e7b390
checkpoint-no-status | 7c4721cc-8085-4877-b328-026e44751adb |  | checkpoint | Details entered below
select | b2b44129-dc61-5316-b2b8-dc148015882f |  | dropdown | Start time | 07:00AM, 07:30AM, 08:00AM, 08:30AM, 09:00AM, 09:30AM, 10:00AM, 10:30AM, 11:00AM, 11:30AM, 12:00PM, 12:30PM, 01:00PM, 01:30PM, 02:00PM, 02:30PM, 03:00PM, 03:30PM, 04:00PM, 04:30PM, 05:00PM, 05:30PM, 06:00PM, 06:30PM
select | f9d3f7cd-5143-5388-9e11-b2d6fe86e8fb |  | dropdown | Lamp duration | 120 mins, 90 mins
boolean | 7cbbb13c-dea9-5135-bd54-824606b4dd22 |  | tickbox | Starter switch
boolean | 74169403-30f6-51ea-a9ec-550b68e0b3d4 |  | tickbox | Charge indicator
boolean | 342c7048-55d0-5c65-a077-86c7e221d820 |  | tickbox | Test switch
boolean | eed44d7b-a3c2-5e1a-b50d-33cf330aabe9 |  | tickbox | Circuit board
boolean | c3726a26-db59-51e7-a491-c7d77dc86e56 |  | tickbox | Clean diffuser
checkpoint-status | 29ada6a1-7711-4d4c-a15e-3f1a1c76f48f |  | checkpoint | Overall fitting
label | 6ed39e09-35f7-58b8-b800-a7f3ed88c642 |  | note | Please add comments if additional action taken / other details
checklist-flat | e505717a-25ea-4a3f-adb6-feba9e65f6b1 |  | checklist | Apprentice Contract of employment |  |  |  |  | Yes | Apprentice Contract of employment | 9083711f-7efa-45a6-b4a5-7fe580bdec86
checkpoint-status | e7732d71-6869-4b0e-a903-185684fbe6d0 |  | checkpoint | Attach Document
checklist-flat | 9f5bb4f2-b534-41a5-959b-c8e6b1df5dd0 |  | checklist | Preventative Maintenance Checklist |  |  |  |  | Yes | Preventative Maintenance Checklist | 95e7616b-8ad2-443d-9e0a-366ab471ffd1
checkpoint-status | e1b8eb24-22a6-4ff1-a530-cd343cdf51ac |  | checkpoint | Visual Inspection of Electrical Installation
label | 8d90ab72-6272-5e16-bd16-689f807a6e0b |  | note | Lights are operational
label | f3ea1f35-1fd8-5042-8b60-13afdd7a0908 |  | note | Light fittings correctly installed and not hanging down
label | 9f3b9727-71ea-5a43-86dd-68b7e167b930 |  | note | Switches and Power outlets securely fixed and cover plates not missing
label | cd394615-f34b-5068-a477-88423dc29055 |  | note | Switchboards not missing pole fillers
label | 537c3bc3-c423-5fff-bb4f-dd7a0553106b |  | note | Any surface conduit or tray work is securely fixed
label | ca15487d-ff72-5f88-9e36-32355bd22b46 |  | note | Diffusers, fittings, switchboard cupboards free from obvious debris
checkpoint-status | 71835161-2cf2-438e-91b7-b005b4c4736f |  | checkpoint | Exit & Emergency Lighting Testing Carried Out & Logbook Completed
checkpoint-status | fc671b03-29c5-4960-9e4c-5fd83ab1db84 |  | checkpoint | Operation of Switchboards Checked
label | d34d33bd-c590-5816-84c0-6322624e5131 |  | note | Performed at 12 months only unless otherwise advised by Builder
checkpoint-status | 7f1fcb07-f9bf-4c1c-8522-47e7d0c2d312 |  | checkpoint | Operation of Lighting Control Checked
checkpoint-status | 5c8584e2-f6ed-48db-a9d6-24862c706076 |  | checkpoint | Check & Replace Fault Lamps
checkpoint-status | de2eb51a-94a0-46d5-83f7-ef18fb56ae9f |  | checkpoint | Fire Detection System Test carried Out
checkpoint-status | 613bd411-54dc-47c3-86f7-bff63d8c60b5 |  | checkpoint | Fire Detection System Test Results Issued
checkpoint-status | b45c4fd6-0e18-47d0-8a6a-19ad27a072ef |  | checkpoint | Switchboard Thermal Imaging Test Carried Out & Report Completed
label | fdd04c4c-7145-5650-9e30-f331df1e5d0d |  | note | Performed at 12 months
checkpoint-status | 1f8bef0c-664a-48c8-8370-e2e058f14a0f |  | checkpoint | Solar
checkpoint-status | bc9c9e8a-b936-4103-990a-9eb145da61f5 |  | checkpoint | UPS
checkpoint-status | 40b5c8ba-8d32-4c8d-8970-01c512f93ede |  | checkpoint | Data & Communications
checklist-flat | f0ba16b4-d079-4ccc-b136-4df460931e48 |  | checklist | ITP. No 13 Commissioning of DB's |  |  |  |  | Yes | ITP No. 13 Commissioning of DB's | 960a58c9-886b-48a0-ac5f-7e1934a0ad89
checkpoint-status | f4e69526-d7ab-414c-b141-ac65128e8f9e |  | checkpoint | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
label | 3b00e467-8738-5fdc-b6b7-c0560bfef13d |  | note | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
label | 7e89bbb9-77b6-5809-bad0-9b4a4fd041a9 |  | note | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
label | c3667d10-83f5-5591-a785-8e170e016a49 |  | note | Collect material from office and have correct db structure downloaded.
checkpoint-status | 00759227-aa49-4821-8796-e46d9d8a3fc1 |  | checkpoint | Commence commissioning
checklist-flat | 8f4dae53-9b75-4ebb-bd6e-f7abeca2d093 |  | checklist | ITP. No 02 Rough In Sub Circuting Cabling |  |  |  |  | Yes | ITP No. 02 Rough In Sub Circuting Cabling | 96805835-b0a1-49cf-86f5-5824eac0ca03
checkpoint-status | 35785279-8b3f-44a3-8a80-edbe9162a193 |  | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
checkpoint-no-status | ecac6e40-2f80-4f20-92ff-b1d331c15f6d |  | checkpoint | Drawing Rev No.
text | 006fdcff-9a53-5dc7-ac54-2aa52c203c13 |  | textbox | Drawing Rev No.
label | 9fe04e58-0b70-5f12-88ce-79272569e884 |  | note | Determine cable size as per itp 30 selection of cables for subcircuit wiring etc
text | 8bc227d5-f75d-5284-9dd1-d56c273b40fe |  | textbox | Cable size / max length
label | c30f8d92-4ff7-5c64-b876-0df8ae19413f |  | note | Determine cable support system ie. catinary, cable tray, fix to structure, ducting
checkpoint-status | f03e7280-87d1-41da-8c90-84f8304b767c |  | checkpoint | Install cable support system
checkpoint-status | 183066a5-99eb-4948-b75f-19c5a62fc87e |  | checkpoint | Check cable size/type
label | 7c9af774-15dd-587d-a425-915d96b77a11 |  | note | Black sheath for power, white sheath for light: 4mm to be used for runs over 90 metres (unless specified differently)
checkpoint-status | 64f5fa5b-2c7f-4900-a0f9-99549b86b18a |  | checkpoint | Install and identify cables
label | fc646844-a6d8-5a90-a3d9-43b4e5015bc8 |  | note | Any cable not terminated immediately must have the ends taped covering the bare copper
checkpoint-status | f3a82761-856b-423e-8472-63fad255f875 |  | checkpoint | Fix cables to support system
checkpoint-status | 8751adde-6b09-4098-b926-64ead8ccd277 |  | checkpoint | Fit-off outlets, plug bases etc. (if necessary)
label | 512d571a-4604-52a3-9344-24d9790b4a1a |  | note | Each circuit to be fitted off completely & clean up area
checklist-flat | ec1ffdc7-0630-4232-a140-f3e7c4eb1a26 |  | checklist | ITP. No 18 Light Fitting Installation |  |  |  |  | Yes | ITP No. 18 Light Fitting Installation | 9e5b29f5-2778-4636-af3e-f6696dc899b1
checkpoint-status | 34db5686-f2b8-4de9-a2c9-27c56ed525f2 |  | checkpoint | Delivery check for damage and correct quantities
checkpoint-status | cf0fc51c-2996-4c0f-8a7e-1abd92dbcf87 |  | checkpoint | Locations coordinate with other services
label | f6ad06cc-0bec-5eaf-92f5-c353e16483b9 |  | note | Marking out if required - refer to reflected ceiling plan for set out
checkpoint-no-status | 999627b2-7909-4a3b-8916-a4615d5d9abe |  | checkpoint | Drawing Rev No.
text | 53a1d37a-4328-5275-8993-2c7919dd005a |  | textbox | Drawing Rev No.
checkpoint-status | a58a2dcf-28f7-48be-8456-de436816c1da |  | checkpoint | Plug in or fit off light / plug base
checkpoint-status | f05db11a-7418-4f7b-8ec5-0ac69a8320fe |  | checkpoint | Install light fitting
checkpoint-status | aca4daa4-6636-45d4-bbfe-5d2c43be617f |  | checkpoint | Install lamps and diffuser
checkpoint-status | bd8d3b01-7555-4d9b-8215-e975db4d6da7 |  | checkpoint | Clean fitting, lamp diffuser
checklist-flat | 7085805e-42f9-4474-a336-773714ef10a4 |  | checklist | Drawings / Documents |  |  |  |  | Yes | Drawings / Documents | 9fd9e1d0-e43e-408e-801c-3f040def3faf
checkpoint-status | 571c2731-68da-4b3a-8f3c-1b8846d05b5c |  | checkpoint | Attach Drawings / Document
checklist-flat | 1d0607f6-e23d-4dbb-a6d7-39b78fae82fb |  | checklist | ITR No.7 Hallway - Fit Off Electrical (High Level & Walls) |  |  |  |  | Yes | ITR No. 07 Hallway - Fit Off Electrical (High Level & Walls) | aada9389-b46f-4cd9-82be-f8baee979a64
checkpoint-status | 3417a6fd-5260-4392-bd0d-cb550c293532 |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | ecd66f75-3f57-4eef-82fc-8f45f9b9051f |  | checkpoint | Drawing Rev No.
text | ab98b686-3bd7-5e3b-901c-a66d3c95a867 |  | textbox | Drawing Rev No.
checkpoint-status | 2d697abe-5a87-4e3c-b7b0-8de1725ddde4 |  | checkpoint | Fit off all Lights
checkpoint-status | 641caac3-3401-4b45-bd12-71d14107d61d |  | checkpoint | Fit off all Sensors and SET TIME TO MINIMUM
checkpoint-status | 0422e5bc-851a-4cd9-905c-f0310cf6a13f |  | checkpoint | Fit off all EX/EMG’s
checkpoint-status | cad330e8-3679-4fea-8d55-a5d0e25b2b4c |  | checkpoint | Label all EX/EMG’s as per plan number
checkpoint-status | b5db37e0-8f66-4882-aa4a-99f036ae291b |  | checkpoint | Fit off all Cleaners GPO’s
checkpoint-status | db2cecbf-ce2a-4dd8-afc8-a2f92d2119d5 |  | checkpoint | Fit off all Comms Riser GPO’s
checkpoint-status | e53d1b49-ad82-4506-b51a-c53cdcf1b118 |  | checkpoint | Ensure area is left clean
checklist-flat | ec3690c4-db79-49dc-a2b3-8734a59fe0fe |  | checklist | ITP No. 19 Copper Data & Voice Testing |  |  |  |  | Yes | ITP No. 19 Copper Data & Voice Testing | bd7a6963-ddb2-4fdf-bf3e-06b5683b12b5
checkpoint-status | fa9eda02-3dc4-461d-b546-d379ec942a2c |  | checkpoint | Area accessible & ready
checklist-flat | fe52c65b-8d1c-4e80-9a15-9e65adcd6a42 |  | checklist | ITP. No 22 Bakelite & Power Installation |  |  |  |  | Yes | ITP No. 22 Bakelite & Power Installation | c1d01c9a-5b08-439d-adbf-b4a49fe8aecd
checkpoint-status | e4929978-a1cc-4202-83c6-437e50ee7ac0 |  | checkpoint | Check drawings for quantity, brand type and colour location/compliance wet areas, hazards etc. mounting heights
checkpoint-no-status | dd9a0482-6b10-4f37-98b3-1368458357d7 |  | checkpoint | Drawing Rev No.
text | 754e0e84-4058-52cc-9034-b74457451d2b |  | textbox | Drawing Rev No.
checkpoint-status | 5d5a5723-f226-45b9-9211-935048952724 |  | checkpoint | Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch
label | 754e0e84-4058-52cc-9034-b74457451d2b |  | note | Each circuit must be fitted off completely
checkpoint-status | 1f4f04f7-9247-4094-9a91-a6ad09d0156e |  | checkpoint | Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use shroud
label | 7a925405-60f3-5315-99fb-ed1c49650686 |  | note | Each circuit must be fitted off completely
checkpoint-status | 536c8cdc-e5c7-4493-8c13-d4b0c46cfa99 |  | checkpoint | Fit off final appliances
button | 98a06d06-5915-5f63-a064-2a5e51af0a6f |  | button | Cover plates (if required) | Yes, No, N/A
button | 34e5bad3-e62b-55cf-837a-9f205bb720db |  | button | Install label (if a specified requirement) | Yes, No, N/A
checklist-flat | 811c840b-78a8-4329-8918-cee6eb680702 |  | checklist | Toolbox Meeting |  |  |  |  | Yes | zSYS - Toolbox Meeting Checklist | c238acba-9ed7-49c6-8c42-848b5fcb03a9
checkpoint-status | 8b4ceea1-7963-432f-adce-fb01d475faae |  | checkpoint | Details
text | 717e797c-ec3e-5270-8c89-047a545f89c4 |  | textbox | Supervisor
boolean | 084abdf9-7275-5cc8-872d-b71cc0f02072 |  | tickbox | David Interligi
boolean | 16ad7117-78c2-5ff5-9e03-b6e523e6e623 |  | tickbox | Michael Borg
boolean | ad5b68a6-7896-5504-9a18-fe75f69179aa |  | tickbox | Rob Pellegrino
boolean | 3840916b-b875-5b7b-823d-04efed1533d8 |  | tickbox | Adrian Sibbing
boolean | 4ed1757c-7afc-5c7a-a8f5-319da8879243 |  | tickbox | John Wolosz
boolean | b3428edf-69b6-5913-9655-7e6d6407aabe |  | tickbox | Lochy Brannelly
boolean | c66ef8b4-a66e-5fd3-8dc1-7bc768aadc6f |  | tickbox | Damon Guy
boolean | 2ae9425c-e118-5e77-bece-56820172cbd7 |  | tickbox | Jake Condon
boolean | b3c31838-fab1-5909-8022-9a940c4e81e3 |  | tickbox | Julian Cannata
boolean | 8df36e14-bf39-5b66-b708-1c0174149986 |  | tickbox | Devilliers Duvenage
boolean | 2b9c1296-314e-5c94-b12b-825814849440 |  | tickbox | David Currie
boolean | 29aa1daf-bc6a-5993-8725-0306b3b893e9 |  | tickbox | Steve Price
text | a0748d01-1664-590d-a1f3-a4afde9b158b |  | textbox | Actions from last meeting:
text | a06b5651-2e24-55dc-997a-092e7aefa51b |  | textbox | Injuries, Near Misses and Incidents since last meeting:
text | 0910a513-4810-5d56-98aa-b2b8ea4cc394 |  | textbox | Management of major Hazards and High Risk Activities:
text | 683b8ba0-c0ed-52ed-94ad-adfd5580745e |  | textbox | Compliance with SWMS & Risk Assessment Booklets or Forms:
text | 1eecf130-63d3-5614-909f-1e3dfa11c741 |  | textbox | Reviews of any Safety Forms, SWMS, Policies, etc
text | c67c4405-3916-567b-bf59-cd655c224d47 |  | textbox | Comments/issues from the floor:
checkpoint-status | b363e52f-2861-4952-b0a4-7b7f4d42d8b3 |  | checkpoint | Signed off by Supervisor
text | a9242d9b-0578-5ce5-9cd2-0532e1de907a |  | textbox | Corrective actions
checklist-flat | 7cce01ba-08e9-46b7-a0ab-dff71413ed57 |  | checklist | VAST Site Induction |  |  |  |  | Yes | zSYS - VAST Site Induction | c2b295b8-5d54-46f3-b542-8cc4fca1d0ca
checkpoint-status | f37e2b03-a5ca-42d5-8dc0-216bc3399dc0 |  | checkpoint | VAST Employee
text | e001aba4-7d8e-5638-b09f-36a6ab5c1e2a |  | textbox | Name
text | fda3113f-4e4a-57e5-bc72-33ae17bbb780 |  | textbox | Contact Number
text | 04ca305f-26f2-5191-8074-295cbf85cc88 |  | textbox | Date of Induction
label | 12841d34-6b99-5a84-8928-4eeb0c7dfabf |  | note | Tick if the following are understood:
boolean | bee90432-7150-5cdb-8c35-782536e9e065 |  | tickbox | How to report to the site and who you report to
boolean | ad88561d-16a3-5089-bad8-591bc956a4ea |  | tickbox | The working hours on site
boolean | f2c37a1a-9b22-5c0b-a965-f405a5886200 |  | tickbox | Who the managers and supervisors are on site
boolean | 3cc0d559-232f-50fb-b911-e4a32f61fd74 |  | tickbox | The correct minimum PPE for site
boolean | 73efbd53-e540-5575-b344-e6f4b02122af |  | tickbox | How safety is communicated on site
boolean | 8737230f-1428-5ae9-a49d-f663f25faee6 |  | tickbox | Where to have lunch and where the toilets are
boolean | 6b90f2fc-d229-5cde-baa8-3f90a5cbb4a7 |  | tickbox | Where the First Aid Kit is kept and who is the First Aider
boolean | d1e59acd-4173-533e-ac3d-920000204a9f |  | tickbox | The Emergency Plan and the Assembly Area for Emergency Evacuation
boolean | 552f82e3-54a5-5b02-9a16-9bb2aac54c57 |  | tickbox | What the high risk activities and hazards are on site
boolean | 885d2490-8994-5df9-9a69-76fca2671d14 |  | tickbox | How to report WHS & Environmental hazards & issues
boolean | 6ac47ca0-b962-570c-867f-9703ca95dd54 |  | tickbox | How to report a safety or environmental accident or incident
boolean | 1c39aa80-6829-5deb-bfcf-6120043181fe |  | tickbox | Housekeeping responsibilities
checkpoint-status | f34af980-b34a-419c-9df7-6608754b1084 |  | checkpoint | EWP Licence - Please take a photo
checkpoint-status | d57dfccf-f777-4de2-8e35-1f26d72839ea |  | checkpoint | Current Certificates Sighted - Please take a photo & comment on each attached certificate
checkpoint-status | ecac10de-4cf3-431d-9796-3e45269c1293 |  | checkpoint | VAST Employee Signature
checkpoint-status | ad9a2e21-0148-41e5-a4f5-bd500271acd3 |  | checkpoint | VAST Supervisor Signature
checklist-flat | 0f62d89e-57a0-4260-831a-65fe04aeeb47 |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | c3566541-ee33-4e6e-85c1-d867c71d4832
checkpoint-status | decd8a96-685e-4f28-8e50-47e2bd93d09d |  | checkpoint | Details
text | acd446e9-425e-519b-992d-37c653e93b3a |  | textbox | Location
text | 584c8b07-1952-52fb-96b1-d33f22ebebe2 |  | textbox | Supervisor
text | f2df7993-08bd-55a7-b963-f6a24029d7ac |  | textbox | Date
text | 86bf3f4c-4b87-5460-95df-79f833b3d475 |  | textbox | Time
text | aada1ba2-e42e-522a-ae83-93188c9d606e |  | textbox | Persons present
label | 2edb7a82-9792-5c51-b090-590b130131a1 |  | note | Topics discussed
boolean | 8620ec71-f1d1-5bde-a218-01579e56052b |  | tickbox | - Injuries, near misses and incidents
boolean | dcd8d09c-2b0c-5491-af13-836000890d20 |  | tickbox | - Management of major hazards
boolean | eb62f661-8372-533c-a886-19ced59e43bd |  | tickbox | - Compliance with our Vast SWMS
boolean | 109aba20-cfdb-59df-8651-ead89987567b |  | tickbox | - Safety - E.g., Apply LOTO processes when applicable. When Megger testing ensure that no person is working at the other end of cable being tested.
boolean | f3c0de5c-d953-5538-b42c-851b5412762b |  | tickbox | - Housekeeping
text | a8f4766f-f8aa-5b17-80ae-f20aa19b7cdc |  | textbox | Comments from the floor
checklist-flat | b377adb1-f1ad-48f3-be8c-121139fc5603 |  | checklist | ITR. 12 Switchboard Commissioning |  |  |  |  | Yes | ITR No. 12 Switchboard Commissioning | c7b52640-be78-498e-9269-4a1b04406ea3
checkpoint-status | 0416db91-f1ea-4711-b15a-1799cee5307e |  | checkpoint | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure And All Steps Undertaken To Ensure compliance With This Procedure
checkpoint-status | 9fe60678-49da-4648-b1a2-ed560d2b0b5c |  | checkpoint | Place all required signage and barricading and have LV rescue kit on standby.
checkpoint-status | 9cefc730-0bc8-4d13-83b1-4014520b991c |  | checkpoint | Refer To As Installed Drawings
checkpoint-status | a47b52f2-f6ee-4b00-a1b1-974368014b6e |  | checkpoint | Obtain Copy Of Switchboard Schedule And Schematic Drawings
checkpoint-status | 5f6c10d4-8cd9-4ca7-ab95-702025f85c0e |  | checkpoint | Mark Up Any Additions Or Deletions Found Whilst Commissioing
checkpoint-status | f37194c5-5b42-4506-a773-ac56736bc027 |  | checkpoint | Complete Visual Checks
checkpoint-status | 8ef5fa65-e4d6-4b32-8300-8167c9d83012 |  | checkpoint | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below
checkpoint-status | 9c09c495-2512-4fe5-86a1-191696078591 |  | checkpoint | Complete Mandatory Tests Using Metrel Tester, Save And Log Results On Tester
checkpoint-status | cae2885e-c680-4199-bcc3-d34a1d537547 |  | checkpoint | Any Failed Results To Be Rectified Saved And Logged On Tester
checkpoint-status | a6fb945b-9361-4b9d-8fac-878b27e007aa |  | checkpoint | Ensure Correct Opertation Of All Control/Equipment Installed In Switchboard
checkpoint-status | dac25eb5-8424-41fe-9617-9d79c547c6d3 |  | checkpoint | Ensure Vast Witness Test Has Been Completed
checkpoint-status | bf43c5b9-3c4e-467d-a3d1-630aede1c03f |  | checkpoint | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated
checkpoint-status | e0fb19a0-42fc-410c-b31c-8a7c04a79f60 |  | checkpoint | Ensure No Access To Live Parts
checkpoint-status | d0987c4e-7b93-4b0a-80a4-e766728258e4 |  | checkpoint | Complete Switchboard Schedules On Vast Template, Install And Fix To Allocated Postion In Switchboard
checkpoint-status | 6434ccb7-26d3-441c-989b-5a5642e30b7c |  | checkpoint | Download Test Results From Metrel Tester And Save To Project Folder
checkpoint-status | 344f8e3e-f91f-45b4-8dc0-c777dac38ade |  | checkpoint | Complete Certificate Of Electrical Safety And Save To Project Folder
checkpoint-status | d0df8d09-88fd-4f3b-b2f4-bd4ba7b67725 |  | checkpoint | Take photo's of all Switchboard internals without escutcheon
checklist-flat | b394fd5f-e9b6-423f-821d-cef7cde18096 |  | checklist | ITP. No 11 Data & Patch Panel Termination |  |  |  |  | Yes | ITP No. 11 Data & Patch Panel Termination | c921f125-e8b7-4f2c-916f-c3718a56ab21
checkpoint-status | 304c01bc-55a3-4d18-b619-c4b97b0a8a19 |  | checkpoint | Visual check ensuring cable to be fitted off in correct position
label | 66d643cd-5d79-5315-be93-f2080e5e9a57 |  | note | Selection of correct tool to be used for termination type
checkpoint-status | ccf91404-b865-4244-a460-699ff9be71c0 |  | checkpoint | Install patch panel into cabinet loom cables to the back of the patch panel
label | 24bb835a-d9dd-540e-a1a2-365b1b184833 |  | note | Tie into position using velcro strip and/or cable ties supplied
checkpoint-status | 76728025-9a09-45ff-a203-553cb72b779d |  | checkpoint | Ensure cables are stripped no more than the specified distance
label | 385768cc-2230-5b13-8ced-69c52d92c763 |  | note | Check terminations at completion for colour code and sequence
checklist-flat | 3337042e-01c1-4099-9ef1-a67c71778906 |  | checklist | ITP No. 18 Light Fitting Installation |  |  |  |  | Yes | ITP No. 18 Light Fitting Installation | d0b152e8-da2e-4586-ac19-6181be17b6ed
checkpoint-status | 50456aef-857a-40bd-9ddc-bc9be28b2d68 |  | checkpoint | Area accessible & ready
checkpoint-no-status | 0fe2a060-c475-4f77-9b6e-c63c4cb7a6d6 |  | checkpoint | Drawing Rev No.
text | ca073d91-c1c9-5986-a93e-3b71200e9a52 |  | textbox | Drawing Rev No.
checkpoint-status | eb333df5-7ebd-4f02-bc9d-90337268e9a8 |  | checkpoint | Delivery check for damage and correct quantities
checkpoint-status | 7ede8471-07fa-4617-98c0-277ee868aa74 |  | checkpoint | Locations coordinate with other services
label | 87507f30-79d5-58fa-9ec6-e7e9a3ee56b0 |  | note | Marking out if required - refer to reflected ceiling plan for set out
checkpoint-status | 513f52e6-6a61-454a-8fd5-fa5afdd7b202 |  | checkpoint | Plug in or fit off light / plug base
checkpoint-status | 94ccf444-f08e-41da-bebc-23f71c651054 |  | checkpoint | Install light fitting
checkpoint-status | 75ae8c4d-a86b-4fca-b6db-8ef71a07bcc0 |  | checkpoint | Install lamps and diffuser
checkpoint-status | 3b9c390a-79d8-4763-af01-50f1ee5c4762 |  | checkpoint | Clean fitting, lamp diffuser
checklist-flat | c65fe2cf-5c01-43c8-a89b-546657035424 |  | checklist | ITR. No 4 Commission Electrical & Permanent Power |  |  |  |  | Yes | ITR No. 04 Commission Electrical & Permanent Power | d81a7480-7022-4ff8-9121-41bfde1e9c1c
checkpoint-status | 11440775-4912-4ab8-b7b1-77cc2715d1ab |  | checkpoint | Energisation permit completed prior to energisation
label | e919948c-f1a8-5b84-a1c8-8843fbe69266 |  | note | Visual Check all items
checkpoint-status | f7aa73b9-8214-4c22-9186-39063a7eacdf |  | checkpoint | Dead Testing
checkpoint-status | aceb2b37-20a5-444a-9cff-62b4b99dd60e |  | checkpoint | Live Test
text | 8379ea70-198f-5b02-b52d-9e43c0246050 |  | textbox | Record Metrel Results and log
checkpoint-status | 1d4914a2-94b1-4002-95d9-ce106ec8e86f |  | checkpoint | Test 4 pin plug base for switching
checkpoint-status | 24915b19-b370-4919-ba5a-5313b3ffb96b |  | checkpoint | Check light switches for correct switching functions
checkpoint-status | 9bbc4719-cf38-4cc5-b3da-b6ae62de7493 |  | checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
checkpoint-status | 736a4a6b-1e3f-46d9-a0c1-857db9f52fd3 |  | checkpoint | Install switchboard cover / label (take photos)
checkpoint-status | 79bdf925-1250-4653-82bb-a0914a796eef |  | checkpoint | Remove battery tabs on smoke detectors ( after MFB certification )
checkpoint-status | 7411ed54-44d0-429f-9e3f-32d8b08dc072 |  | checkpoint | Ensure area is left clean
checklist-flat | 243a9ec3-350a-47c1-8e79-9249ba5b3fdf |  | checklist | ITP No. 07 Comms: Backbone Cabling Installation, Termination & Testing |  |  |  |  | Yes | ITP No. 07 Comms: Backbone Cabling Installation, Termination & Testing | defafabb-34d2-4a07-b1a9-89f39277a33e
checkpoint-status | fbce480b-5a69-42b9-a3a6-4cbf9fadd4ca |  | checkpoint | Obtain the most recent drawings and specifications
checkpoint-status | 01c9afe4-2287-457d-8e89-5e1a531a719a |  | checkpoint | Install cable support or conduit where required
checkpoint-status | d464904a-18a3-443e-97a6-888308bdd45b |  | checkpoint | Dress cables to final location, ensure velcro straps for cat 6 cabling
checkpoint-status | a7faf4f4-0d5f-4f63-a593-a61a373da058 |  | checkpoint | Terminate cabling ensuring correct colour code
label | 19e63e99-5d4f-5ce6-9738-56df49c2271f |  | note | Ensure correct termination tool used as per vendor recommendation
checkpoint-status | 1646b3a7-0bc2-438a-b3fa-4fcbb5d0df87 |  | checkpoint | Test terminations using wizard tester for krone block terminations and mod tap tester for patch panel terminations
text | 1fcc9e62-ee66-5b67-b641-83f8d6886056 |  | textbox | Device number
text | 9a175e11-acb7-5499-9a92-ca4355e1c085 |  | textbox | Record results
checkpoint-status | d7a3459c-de88-4234-94a2-0311632440ca |  | checkpoint | Complete telecommunications cabling advice form and attachment if required
checklist-flat | 114ea3e9-7bea-403d-959b-386005422e67 |  | checklist | Uniform Request |  |  |  |  | Yes | Uniform Request | e40ed167-9728-4c7d-8b8f-02efbe614a18
checkpoint-status | 9aa8c895-de62-4186-8616-da8a74e61bbe |  | checkpoint | Attach Document
checklist-flat | 24deff79-877c-47ff-94ac-ef6e6f1b5425 |  | checklist | ITP No. 16 Terminate Sub Circuit Cabling |  |  |  |  | Yes | ITP No. 16 Terminate Sub Circuit Cabling | ed4b6f0a-0e36-4884-9c83-6f010f2769fa
checkpoint-status | 56d2a377-bef5-4582-a40e-3433088dd89c |  | checkpoint | Install sub circuit cabling in accordance with db schedule and terminate
label | 159dba9f-b291-53e9-a141-6d9015d30f72 |  | note | If circuit not complete at the other end, it must not be terminated but placed in a junction box at field end and in connectors at distribution board end
checkpoint-status | 3f3cb747-2c5a-4985-bfec-d7c97f709264 |  | checkpoint | Clean & vacuum
label | 652332a1-e179-5691-afc7-f6fb417bbb0a |  | note | Record relevant information and any changes on db schedule. And return to administrator/office for commissioning team
checklist-flat | 5665f939-b89e-4567-a1c7-76a4b29db642 |  | checklist | ITR No. 02 Apartment Cut Out |  |  |  |  | Yes | ITR No. 02 Apartment Cut Out | fe0fb839-0957-48ab-89f6-1d9d809a1cb0
checkpoint-status | d75e2cc0-e554-41c7-9e65-ab331c6c2fb4 |  | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
checkpoint-no-status | 7350f815-8e22-4018-874f-7ce137a2775d |  | checkpoint | Drawing Rev No.
text | b5b50ffc-b16d-5f87-9cce-d7196f1364f0 |  | textbox | Drawing Rev No.
checkpoint-status | 70bece3d-9c16-4c3b-9587-0fbc651d803f |  | checkpoint | Cut out for light fittings
checkpoint-status | 050be8a1-e6e1-4562-9132-38f5dd4dc1d3 |  | checkpoint | Cut out smoke detectors
checkpoint-status | aa771f97-0ff4-4428-af71-3f6e892d29c5 |  | checkpoint | Cut out kitchen to kitchen plan
checkpoint-status | 00238d24-cf37-46b2-a88f-3c387cf2e02e |  | checkpoint | Cut out switches & GPO’s
checkpoint-status | 4f43ca77-dcbc-47e5-b328-3a38833cfe18 |  | checkpoint | Cut out Bathroom and Study Led Strips Fig 8
checkpoint-status | d862698c-1904-4788-ab8c-82a3599b9f67 |  | checkpoint | Ensure AC isolator is in correct position
checkpoint-status | f306f08e-75ec-4ee3-a42e-de2a5498b23a |  | checkpoint | Ensure Wall light is in correct position
checkpoint-status | 1f9f112a-22d5-49eb-916d-96a444d8f35c |  | checkpoint | Ensure kitchen outlets are in correct position
checkpoint-status | a1e681ff-9225-44a4-9f4d-960f74a47cf3 |  | checkpoint | Locate all cables ( including Smoke Detectors & Pendants )
checkpoint-status | 33660f39-897f-43f3-8efe-0a27e5db7ca3 |  | checkpoint | Install Fire Boxes and hit all 4 tabs in
checkpoint-status | 90bb542e-6ea3-46fb-9f81-b9e2e89d916b |  | checkpoint | Fire caulk kitchen cables ( if applicable )
checkpoint-status | 1887ebad-a57b-4bb5-9145-fbfb733e193e |  | checkpoint | Ensure area is left clean
checklist-flat | 3c645d25-6aa5-449f-9698-d098947be17d |  | checklist | ITR No.1 Apartment Rough In of Electrical Services |  |  |  |  | Yes | ITR No. 01 Apartment Rough In of Electrical Services | fe654a13-1bf9-4b4e-9492-2a15cb2cd6d9
checkpoint-status | a206157c-775e-4da7-9def-bc3759952631 |  | checkpoint | Area clear, tidy and accessible
checkpoint-no-status | 5cadb29b-7679-40cc-aef1-eb0c784b9194 |  | checkpoint | Drawing Rev No.
text | 914cb580-50e8-5f90-9255-18c021bb9842 |  | textbox | Drawing Rev No.
checkpoint-status | 80e64b0d-3302-44cf-83d3-3560dd3e2395 |  | checkpoint | Rough in Hard Actives to all switches
checkpoint-status | c7eedba4-8cc1-4ff4-845c-be8d88aa67e2 |  | checkpoint | Rough in of Switched Actives from switches to lights & Fit off Quick connects whilst on ladder
checkpoint-status | 47a81b8a-85ba-4f0d-aab8-60ee0233db76 |  | checkpoint | Rough in GPOs
checkpoint-status | 16d74f66-3e64-4c8b-b9aa-8a8a92b685bc |  | checkpoint | Rough in of all kitchen general power (including island bench) above bench, gas cooktop, fridge, microwave, rangehood & dishwasher
checkpoint-status | d9547bc9-e6e3-490d-9a09-4287898d3664 |  | checkpoint | Rough in A/C & Oven
checkpoint-status | db676e67-ce90-45c7-b123-3e416a030684 |  | checkpoint | Rough in single tail island bench Pendant to the nearest downlight
checkpoint-status | cc9866eb-b372-4b2a-a3de-a47e98dec2ff |  | checkpoint | Rough in a loop from Pendant to LED strip at rangehood
checkpoint-status | 0a45a744-2394-4817-8159-e88d9e99cc54 |  | checkpoint | Rough in bathroom LED Fig 8 downight location and switch separately
checkpoint-status | f4d57431-837c-4638-8e6b-0296b37297b4 |  | checkpoint | Rough in LED fig 8 to study desk to nearest downlight
checkpoint-status | 0eb7c5c3-9366-462b-ba43-bb9357e1a2d1 |  | checkpoint | Rough in all internal lights
checkpoint-status | 11e0bb13-800e-4aa4-a5ed-91c3e50cf8f7 |  | checkpoint | Rough in Balcony wall light- If 2 lights, bring 2 switch wires back to switch
checkpoint-status | 219a3c67-4152-4f3d-be9e-421b38709db4 |  | checkpoint | Rough in smoke detector and interconnect to other detectors.
checkpoint-status | ee11b574-4ab0-431c-9d0e-6d04bc7fc1c7 |  | checkpoint | Rough in bathroom fans off power circuit and HA loop at fan
checkpoint-status | f7fcbdc0-b1ba-4883-a33c-ed5f95c61ca3 |  | checkpoint | Rough in WM/DR and install SDI from dryer gpo to laundry switch
checkpoint-status | 61ec9e8e-fcaa-48ed-8a6c-65a0ed1b4e26 |  | checkpoint | Rough in WP GPO to balcony if applicable
checkpoint-status | 797bb3fd-3719-4c9f-969a-0e615aa15658 |  | checkpoint | Rough in intercom patch lead to LBNCO hub
checkpoint-status | 09aeb5a1-deef-4770-a6ff-00f5e9db35da |  | checkpoint | Rough in tv points to LBNCO hub
checkpoint-status | a4278a67-83c5-4c87-ba85-571e7c58804e |  | checkpoint | Rough in data points to LBNCO hub
label | 4f454e61-68ae-52ba-ac08-f4f9e5380274 |  | note | Ensure LBNCO draw string is in
label | 8ba03f60-87ab-5ddc-99f7-693a4298a3cd |  | note | Ensure Sub Mains are at Switchboard Location
checkpoint-status | 67b15e39-5c60-4013-a1d0-9cdb9c9f55e6 |  | checkpoint | Install switchboard & fit off
button | 5f5e6f38-a2ff-5d33-8636-17bd3d314476 |  | button | Install 150mm stud protecting sub main and earth with nut & bolt | Yes, No, N/A
button | 7d285a23-1d0d-5068-8bbf-d85ea696f08c |  | button | Install 2.5mm earth tags | Yes, No, N/A
button | 2582625a-4cf7-53e1-9ee0-e4ba93967be3 |  | button | Fire caulk sub main into DB and all cable entries | Yes, No, N/A
button | b30e1a98-645c-5392-a059-b57fb25cb5de |  | button | Fit off 4 pin plug base | Yes, No, N/A
checkpoint-status | 3d38d15d-582a-4e96-bae6-ce3b8e5d1dc5 |  | checkpoint | Ensure all Quick Connects are fit off
button | 03370382-1e15-5196-90cc-35667210ea3b |  | button | Ensure all cables are neat, taped to studs and easily accessible for cut out | Yes, No, N/A
button | 632d220e-669f-53a9-b7f1-a01e3340fa27 |  | button | Ensure all cables are clearly labelled at DB and at party walls | Yes, No, N/A
checkpoint-status | 93efd2d8-e384-4ab6-a3b4-575c052a438f |  | checkpoint | Ensure area is left clean
checklist-flat | 8932aa9b-c907-4043-be68-5bb9ff077dc7 |  | checklist | ITP. No 03 Mains & Substation Installation |  |  |  |  | Yes | ITP No. 03 Mains & Substation Installation | fe774b30-4b55-4d56-b5cc-7f8bd577886c
checkpoint-status | 4705fc2e-a8b0-4e5a-87ef-dfec580b61d6 |  | checkpoint | Measure cable runs with appropriate accurate measuring instrument (eg tape measure, wheel)
checkpoint-status | c56c27a6-1a16-4161-bb5f-e9920f4b4fb2 |  | checkpoint | Check cable sizes resistance of protective earth conductor - shall be low enough to permit passage of current necessary to operate protective device
checkpoint-status | 96f32459-d6f6-433f-afbf-ada8ac7bc289 |  | checkpoint | Confirm length of cable if sub contract item & order
text | 7bd5d7f5-fc89-589d-8593-16a00a4ff6b6 |  | textbox | Record length of cable
checkpoint-status | fed89742-f21c-4d0c-99b6-0ea463bbd9c4 |  | checkpoint | Install cable in applicable method (EG. Cable stands, electric winch, pulleys etc.) - ANY CABLE NOT TERMINATED IMMEDIATELY MUST HAVE THE ENDS TAPED COVERING THE BARE COPPER - please take a photo
checkpoint-status | 0942badc-dcfd-44ae-9b5f-51ee8a9a3518 |  | checkpoint | Trefoil cables & tie cables to support system (ensure spacing)
checkpoint-status | 4cfcfc64-5a39-4111-a4de-eeeabf56801f |  | checkpoint | Check requirements for cable identification & install