## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITR No.34 - Installing Light Pole Cages
section | Details
checkpoint | INSPECT CAGES FOR ANY DAMAGE PROIR TO INSTALLATION
checkpoint | SET OUT LIGHT POLE LOCATION, ALIGNMENT AND HEIGHT AS SPECIFIED
checkpoint | ERECT PEDESTRIAN BARRICADING AS PER PLAN
checkpoint | EXCAVATE AS PER PLAN
checkpoint | PLACE SPECIFIED BEDDING MATERIAL AS PER REQUIREMENT
checkpoint | INSTALL LIGHT POLE CAGES AND CONDUITS AS REQUIRED
checkpoint | RE-CHECK FINSHED HEIGHT AS PER CIVIL DRAWINGS
checkpoint | POUR CONCRETE FOOTING WITH SPECIFIED MPA
checkpoint | CLEAN UP AND BARRICADE WORK AREA
checklist | ITP No.07 - Structured Cabling Rough In
section | Details
checkpoint | Refer approved drawings and specification.
checkpoint | Install cable support or conduit where required.
checkpoint | Verify correct cable type.
checkpoint | Refer to approved drawings for cable numbering sequence relevant to final fit off sequence & record
checkpoint | Install cable within or on cable support systems maintaining min segregations, ensure velcro cable ties are used as per specification
checkpoint | Form cables into relevant fit-off groups at the cabinet end.
checklist | ITR No.18- Light and Power Fit Off
section | Bakelite & Power
checkpoint | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
checkpoint | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS,
checkpoint | FIT OFF AND FIX SWITCHES, WHERE MULTI GANG SWITCHES WITH MULTI CIRCUITS ARE INVOLVED USE SHROUDS ON EACH SWITCH. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
checkpoint | FIT OFF AND FIX GPO’S, WHERE A GPO IS LOCATED WITHIN 150mm OF A METAL STUD, USE SHROUD. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
checkpoint | FIT OFF FINAL APPLIANCES
checkpoint | COVER PLATES (IF REQUIRED)
checkpoint | INSTALL LABEL (IF A SPECIFIED REQUIREMENT)
section | Light Fittings
checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
checkpoint | LOCATIONS CO ORDINATE WITH OTHER SERVICES
checkpoint | MARKING OUT IF REQUIRED - REFER TO REFLECTED CEILING PLAN FOR SET OUT
checkpoint | PLUG IN OR FIT OFF LIGHT / PLUG BASE
checkpoint | INSTALL LIGHT FITTING
checkpoint | INSTALL LAMPS AND DIFFUSER
checkpoint | CLEAN FITTING, LAMP DIFFUSER
checklist | ITR No.16 - Switchboard Installation and Terminate Submains
section | Details
checkpoint | DELIVERY CHECK FOR DAMAGE, PAINT FINISH, DIMENSIONS AND DOORS AGAINST APPROVED SHOP DRAWING
checkpoint | LOCATE & FIX INTO POSITION
checkpoint | INSTALL SUBMAINS CABLING AS APPROPRIATE EG. GLANDS, TRAY, DUCT
checkpoint | INSTALL LUGS AND TERMINATE
checkpoint | ANY CABLES NOT TERMINATED PRIOR TO ENERGISATION MUST BE REMOVED FROM CUBICLE AT ORIGIN AND HAVE ENDS COVERED IN HEATSHRINK. AT DESTINATION CABLES MUST BE COVERED IN HEATSHRINK AND BE CONTAINED IN A JUNCTION BOX
checkpoint | CLEAN & VACUUM
checkpoint | ORGANISE INPECTION BY INSPECTOR. LODGE PRESCRIBED / NON PRESCRIBED (AS APPLICABLE) CERTIFICATE OF ELECTRICAL SAFETY (IF REQUIRED).
checkpoint | CLEARLY IDENTIFY SERVICES
checkpoint | WHEN READY TO ENERGISE PROCEED IN ACCORDANCE WITH ENERGISATION PROCEDURE
checkpoint | ENERGIZE & RECORD RESULTS
checkpoint | CHECK SWITCHBOARD AS INSTALLED MATCHES SHOP DRAWING. IF NECCESARY MODIFY SHOP DRAWING TO MATCH INSTALLED & RETURN TO OFFICE
checkpoint | CLEAN SWITCHBOARD CUPBOARD
checkpoint | INSTALL SUB CIRCUIT CABLING IN ACCORDANCE WITH DB SCHEDULE AND TERMINATE. if circuit not complete at the other end, it must not be terminated BUT PLACED IN A JUNCTION BOX AT FIELD END AND IN CONNECTORS AT dISTRIBUTION BOARD END.
checkpoint | CLEAN & VACUUM
checkpoint | RECORD RELEVANT INFORMATION AND ANY CHANGES ON DB SCHEDULE. AND RETURN TO ADMINISTRATOR/OFFICE FOR COMMISSIONING TEAM
checklist | ITP No.13 - Sub-circuit Cabling Fit Off
section | Details
checkpoint | COMPLETE WALL OR CEILING CUT OUT WHERE REQUIRED
checkpoint | TEST & ENSURE SUB CIRCUIT CABLING IS NOT LIVE PRIOR TO FIT OFF
checkpoint | TERMINATE CABLE TO OUTLET OR PLUG BASE, CHECK CORRECT CONNECTIONS AND FIX TO SURFACE, IF CIRCUIT CAN NOT BE FULLY TERMINATED A JUNCTION BOX MUST BE INSTALLED WHERE REQUIRED
checkpoint | CLEAN AREA AS REQUIRED
checkpoint | RECORD ANY RELEVANT INFORMATION ON DRAWINGS.
checklist | ITP No.16 - Exit & Emergency Installating & Testing
section | Details
checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
checkpoint | COORDINATE LOCATIONS WITH OTHER SERVICES
checkpoint | MARKING OUT (IF REQUIRED) REFER TO DRAWINGS FOR LOCATIONS
checkpoint | PLUG IN OR FIT OFF LIGHT, FIT OFF DATA CABLE IF REQUIRED
checkpoint | INSTALL LAMP & DIFFUSER AND CLEAN FITTING
checkpoint | INSTALL EMERGENCY BARCODE TO FITTING AND TO DRAWINGS (IF REQUIRED) OR,
checkpoint | NUMBER FITTINGS AS PER VAST SHOP DRAWINGS.
checkpoint | UPDATE ANY CHANGES FOR AS BUILTS
checkpoint | COMPLETE LOG BOOK
checkpoint | COMPLETE INITIAL 2 HOUR TEST
checkpoint | RECORD RESULTS
checklist | ITP No.08 - Structured Cabling Fit Off
section | Details
checkpoint | VISUAL CHECK ENSURING CABLE TO BE FITTED OFF IN CORRECT POSITION.
checkpoint | SELECTION OF CORRECT TOOL TO BE USED FOR TERMINATION TYPE.
checkpoint | ENSURE CABLES ARE STRIPPED NO MORE THAN THE SPECIFIED DISTANCE. CHECK TERMINATIONS AT COMPLETION FOR COLOUR CODE AND SEQUENCE.
checkpoint | ATTACH WRAP AROUND LABEL TO CABLE NO MORE THAN 60MM FROM THE JACK. ENSURING CORRECT NUMBER SEQUENCE.
checkpoint | DRESS CABLES TO FINAL LOCATION. ENSURE VELCRO STRAPS FOR CAT 6 CABLING
checkpoint | INSTALL JACK INTO WORKSTATION OR WALL OUTLET.
checkpoint | INSTALL PATCH PANEL INTO CABINET LOOM CABLES TO THE BACK OF THE PATCH PANEL. TIE INTO POSITION USING VELCRO STRIP AND/OR CABLE TIES SUPPLIED.
checkpoint | PATCH OUTLETS TO HARDWARE DEVICES WHERE APPLICABLE AND CHECK FOR CORRECT OPERATION.
checkpoint | LABEL OUTLET ENSURING CORRECT NUMBER SEQUENCE
checkpoint | COMPLETE CERTIFICATION AS REQUIRED
checklist | ITP No.09 - Structured Cabling Testing Certified System
section | Details
checkpoint | REFER TO INSTALLED DRAWINGS
checkpoint | Test terminations using COPPER STRUCTURED CABLING tester AND LOG RESULTS
checkpoint | RECTIFY ANY FAILED RESULTS, RE-TEST AND LOG
checkpoint | LABEL FRAMES AND PATCH PANELS
checkpoint | COMPLETE PATCH PANEL SCHEDULE
checkpoint | DOWNLOAD RESULTS FROM TESTER TO PROJECT FOLDER