## Project Structure
Folder Structure |  |  |  | Checklists
Site QA
Basements
B05
|  |  | Pour 1 | In-Ground Drainage Hydraulic Services ITP
|  |  | Pour 2 | In-Ground Drainage Hydraulic Services ITP
|  |  | Pour 3 | In-Ground Drainage Hydraulic Services ITP
|  |  | Pour 4 | In-Ground Drainage Hydraulic Services ITP
|  |  | Pour 5 | In-Ground Drainage Hydraulic Services ITP
|  |  | Pour 6 | In-Ground Drainage Hydraulic Services ITP
|  |  | Sewer pump station | Sewer Pump Station
|  |  | Storm Water Pump Station | Storm Water Pump Station
|  |  | Aerial drainage | Aerial Drainage
|  |  | Prssure Services | Pressure Services Installation
|  |  | Car park | Car Park Finalisation
B04
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | Car Park Finalisation | Car Park Finalisation
B03
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | Car Park Finalisation | Car Park Finalisation
B02
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | Car Park Finalisation | Car Park Finalisation
B01
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | DDCV fire supply | DDCV for Fire supply
|  |  | Fire Pump room | Fire Hydrant/Sprinkler Pump Room & Tank
|  |  | Pump Cold Water Pump | Cold Water Pressure Pump
|  |  | Recycled Water Pump | Cold Water Pressure Pump
|  |  | Garbage rooms (BIN ROOM) | Garbage Room Work
|  |  | Garbage rooms (RESI WASTE) | Garbage Room Work
|  |  | Male Bathroom | Common Male Bathroom Rough In
|  |  | Female Bathroon | Common Female Bathroom Rough In
|  |  | Disabled Bathroom | Common Disabled bathroom Rough Ins
|  |  | Grease tanks | Grease Tank
|  |  | Car Park Finalisation | Car Park Finalisation
|  |  | LAUNDRY | Laundry
Level 01 (Ground)
|  |  | In-Ground Drainage Hydraulic Services | In-Ground Drainage Hydraulic Services ITP
|  |  | Inground Pressure Services Installation | Inground Pressure Services Installation.
|  |  | Fire water connection | Water Connection
|  |  | Water connection | Water Connection
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 4 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial drainage | Aerial Drainage
|  |  | Pressure services | Pressure Services Installation
|  |  | Water meter | Water Meter Install & RPZD
|  |  | Common Water meter | Water Meter Install & RPZD
|  |  | Retail Meters | Water Meter Install & RPZD
|  |  | Temp Bin Holding Room | Garbage Room Work
|  |  | Retail Waste Room | Garbage Room Work
|  |  | Gas connection | Gas Connection
|  |  | Gas meter for retail tenancies | Gas Meter
|  |  | Gas meter Residential | Gas Meter
|  |  | Retail 01 | Commercial Tenancy
|  |  | Retail 02 | Commercial Tenancy
|  |  | WC | Common Disabled bathroom Rough Ins
|  |  | Stormwater connection 1 | Stormwater Connection
|  |  | Stormwater connection 2 | Stormwater Connection
|  |  | Sewer Connection 1 | Sewer Connection
Level 02
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | Stormwater filter | Water Storage Tank
Level 03
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | Commercial Tenancy | Commercial Tenancy
|  |  | Male Bathroom | Common Male Bathroom Rough In
|  |  | Female Bathroon | Common Female Bathroom Rough In
|  |  | Disabled Bathroom | Common Disabled bathroom Rough Ins
Level 04
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | Commercial Tenancy | Commercial Tenancy
|  |  | Male Bathroom | Common Male Bathroom Rough In
|  |  | Female Bathroon | Common Female Bathroom Rough In
|  |  | Disabled Bathroom | Common Disabled bathroom Rough Ins
Level 05
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | Commercial Tenancy | Commercial Tenancy
|  |  | Male Bathroom | Common Male Bathroom Rough In
|  |  | Female Bathroon | Common Female Bathroom Rough In
|  |  | Disabled Bathroom | Common Disabled bathroom Rough Ins
Level 06
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure Services Installation
|  |  | Commercial Tenancy | Commercial Tenancy
|  |  | Male Bathroom | Common Male Bathroom Rough In
|  |  | Female Bathroon | Common Female Bathroom Rough In
|  |  | Disabled Bathroom | Common Disabled bathroom Rough Ins
|  |  | Hot Water Plant & Return Pumps | Hot Water Plant & Return Pumps
Level 07
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 701 | Apartment / Hotel
|  |  | 702 | Apartment / Hotel
|  |  | 703 | Apartment / Hotel
|  |  | 704 | Apartment / Hotel
|  |  | 705 | Apartment / Hotel
|  |  | 706 | Apartment / Hotel
|  |  | 707 | Apartment / Hotel
|  |  | 708 | Apartment / Hotel
|  |  | 709 | Apartment / Hotel
|  |  | 710 | Apartment / Hotel
Level 08
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 801 | Apartment / Hotel
|  |  | 802 | Apartment / Hotel
|  |  | 803 | Apartment / Hotel
|  |  | 804 | Apartment / Hotel
|  |  | 805 | Apartment / Hotel
|  |  | 806 | Apartment / Hotel
|  |  | 807 | Apartment / Hotel
|  |  | 808 | Apartment / Hotel
|  |  | 809 | Apartment / Hotel
|  |  | 810 | Apartment / Hotel
Level 09
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 901 | Apartment / Hotel
|  |  | 902 | Apartment / Hotel
|  |  | 903 | Apartment / Hotel
|  |  | 904 | Apartment / Hotel
|  |  | 905 | Apartment / Hotel
|  |  | 906 | Apartment / Hotel
|  |  | 907 | Apartment / Hotel
|  |  | 908 | Apartment / Hotel
|  |  | 909 | Apartment / Hotel
|  |  | 910 | Apartment / Hotel
Level 10
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1001 | Apartment / Hotel
|  |  | 1002 | Apartment / Hotel
|  |  | 1003 | Apartment / Hotel
|  |  | 1004 | Apartment / Hotel
|  |  | 1005 | Apartment / Hotel
|  |  | 1006 | Apartment / Hotel
|  |  | 1007 | Apartment / Hotel
|  |  | 1008 | Apartment / Hotel
|  |  | 1009 | Apartment / Hotel
|  |  | 1010 | Apartment / Hotel
|  |  | 1011 | Apartment / Hotel
|  |  | 1012 | Apartment / Hotel
|  |  | 1013 | Apartment / Hotel
Level 11
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1101 | Apartment / Hotel
|  |  | 1102 | Apartment / Hotel
|  |  | 1103 | Apartment / Hotel
|  |  | 1104 | Apartment / Hotel
|  |  | 1105 | Apartment / Hotel
|  |  | 1106 | Apartment / Hotel
|  |  | 1107 | Apartment / Hotel
|  |  | 1108 | Apartment / Hotel
|  |  | 1109 | Apartment / Hotel
|  |  | 1110 | Apartment / Hotel
|  |  | 1111 | Apartment / Hotel
|  |  | 1112 | Apartment / Hotel
|  |  | 1113 | Apartment / Hotel
Level 12
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1201 | Apartment / Hotel
|  |  | 1202 | Apartment / Hotel
|  |  | 1203 | Apartment / Hotel
|  |  | 1204 | Apartment / Hotel
|  |  | 1205 | Apartment / Hotel
|  |  | 1206 | Apartment / Hotel
|  |  | 1207 | Apartment / Hotel
|  |  | 1208 | Apartment / Hotel
|  |  | 1209 | Apartment / Hotel
|  |  | 1210 | Apartment / Hotel
|  |  | 1211 | Apartment / Hotel
Level 13
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | Male Change Room | Common Male Bathroom Rough In
|  |  | Female Changeroom | Common Female Bathroom Rough In
|  |  | Pool and Spa DDA Bathroom 1 | Common Disabled bathroom Rough Ins
|  |  | Pool and Spa DDA Bathroom 2 | Common Disabled bathroom Rough Ins
|  |  | Toilet (Gym) | Common Disabled bathroom Rough Ins
Level 14
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1401 | Apartment / Hotel
|  |  | 1402 | Apartment / Hotel
|  |  | 1403 | Apartment / Hotel
|  |  | 1404 | Apartment / Hotel
|  |  | 1405 | Apartment / Hotel
|  |  | 1406 | Apartment / Hotel
|  |  | 1407 | Apartment / Hotel
Level 15
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1501 | Apartment / Hotel
|  |  | 1502 | Apartment / Hotel
|  |  | 1503 | Apartment / Hotel
|  |  | 1504 | Apartment / Hotel
|  |  | 1505 | Apartment / Hotel
|  |  | 1506 | Apartment / Hotel
|  |  | 1507 | Apartment / Hotel
|  |  | 1508 | Apartment / Hotel
|  |  | 1509 | Apartment / Hotel
|  |  | 1510 | Apartment / Hotel
|  |  | 1511 | Apartment / Hotel
Level 16
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1601 | Apartment / Hotel
|  |  | 1602 | Apartment / Hotel
|  |  | 1603 | Apartment / Hotel
|  |  | 1604 | Apartment / Hotel
|  |  | 1605 | Apartment / Hotel
|  |  | 1606 | Apartment / Hotel
|  |  | 1607 | Apartment / Hotel
|  |  | 1608 | Apartment / Hotel
|  |  | 1609 | Apartment / Hotel
|  |  | 1610 | Apartment / Hotel
|  |  | 1611 | Apartment / Hotel
|  |  | 1612 | Apartment / Hotel
Level 17
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1701 | Apartment / Hotel
|  |  | 1702 | Apartment / Hotel
|  |  | 1703 | Apartment / Hotel
|  |  | 1704 | Apartment / Hotel
|  |  | 1705 | Apartment / Hotel
|  |  | 1706 | Apartment / Hotel
|  |  | 1707 | Apartment / Hotel
|  |  | 1708 | Apartment / Hotel
|  |  | 1709 | Apartment / Hotel
|  |  | 1710 | Apartment / Hotel
|  |  | 1711 | Apartment / Hotel
|  |  | 1712 | Apartment / Hotel
Level 18
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1801 | Apartment / Hotel
|  |  | 1802 | Apartment / Hotel
|  |  | 1803 | Apartment / Hotel
|  |  | 1804 | Apartment / Hotel
|  |  | 1805 | Apartment / Hotel
|  |  | 1806 | Apartment / Hotel
|  |  | 1807 | Apartment / Hotel
|  |  | 1808 | Apartment / Hotel
|  |  | 1809 | Apartment / Hotel
|  |  | 1810 | Apartment / Hotel
|  |  | 1811 | Apartment / Hotel
|  |  | 1812 | Apartment / Hotel
Level 19
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 1901 | Apartment / Hotel
|  |  | 1902 | Apartment / Hotel
|  |  | 1903 | Apartment / Hotel
|  |  | 1904 | Apartment / Hotel
|  |  | 1905 | Apartment / Hotel
|  |  | 1906 | Apartment / Hotel
|  |  | 1907 | Apartment / Hotel
|  |  | 1908 | Apartment / Hotel
|  |  | 1909 | Apartment / Hotel
|  |  | 1910 | Apartment / Hotel
|  |  | 1911 | Apartment / Hotel
Level 20
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2001 | Apartment / Hotel
|  |  | 2002 | Apartment / Hotel
|  |  | 2003 | Apartment / Hotel
|  |  | 2004 | Apartment / Hotel
|  |  | 2005 | Apartment / Hotel
|  |  | 2006 | Apartment / Hotel
|  |  | 2007 | Apartment / Hotel
|  |  | 2008 | Apartment / Hotel
|  |  | 2009 | Apartment / Hotel
|  |  | 2010 | Apartment / Hotel
|  |  | 2011 | Apartment / Hotel
Level 21
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2101 | Apartment / Hotel
|  |  | 2102 | Apartment / Hotel
|  |  | 2103 | Apartment / Hotel
|  |  | 2104 | Apartment / Hotel
|  |  | 2105 | Apartment / Hotel
|  |  | 2106 | Apartment / Hotel
|  |  | 2107 | Apartment / Hotel
|  |  | 2108 | Apartment / Hotel
|  |  | 2109 | Apartment / Hotel
|  |  | 2110 | Apartment / Hotel
|  |  | 2111 | Apartment / Hotel
|  |  | 2112 | Apartment / Hotel
Level 22
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2201 | Apartment / Hotel
|  |  | 2202 | Apartment / Hotel
|  |  | 2203 | Apartment / Hotel
|  |  | 2204 | Apartment / Hotel
|  |  | 2205 | Apartment / Hotel
|  |  | 2206 | Apartment / Hotel
|  |  | 2207 | Apartment / Hotel
|  |  | 2208 | Apartment / Hotel
|  |  | 2209 | Apartment / Hotel
|  |  | 2210 | Apartment / Hotel
|  |  | 2211 | Apartment / Hotel
|  |  | 2212 | Apartment / Hotel
Level 23
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2301 | Apartment / Hotel
|  |  | 2302 | Apartment / Hotel
|  |  | 2303 | Apartment / Hotel
|  |  | 2304 | Apartment / Hotel
|  |  | 2305 | Apartment / Hotel
|  |  | 2306 | Apartment / Hotel
|  |  | 2307 | Apartment / Hotel
|  |  | 2308 | Apartment / Hotel
|  |  | 2309 | Apartment / Hotel
|  |  | 2310 | Apartment / Hotel
|  |  | 2311 | Apartment / Hotel
|  |  | 2312 | Apartment / Hotel
Level 24
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2401 | Apartment / Hotel
|  |  | 2402 | Apartment / Hotel
|  |  | 2403 | Apartment / Hotel
|  |  | 2404 | Apartment / Hotel
|  |  | 2405 | Apartment / Hotel
|  |  | 2406 | Apartment / Hotel
|  |  | 2407 | Apartment / Hotel
|  |  | 2408 | Apartment / Hotel
|  |  | 2409 | Apartment / Hotel
|  |  | 2410 | Apartment / Hotel
|  |  | 2411 | Apartment / Hotel
Level 25
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2501 | Apartment / Hotel
|  |  | 2502 | Apartment / Hotel
|  |  | 2503 | Apartment / Hotel
|  |  | 2504 | Apartment / Hotel
|  |  | 2505 | Apartment / Hotel
|  |  | 2506 | Apartment / Hotel
|  |  | 2507 | Apartment / Hotel
|  |  | 2508 | Apartment / Hotel
|  |  | 2509 | Apartment / Hotel
|  |  | 2510 | Apartment / Hotel
|  |  | 2511 | Apartment / Hotel
Level 26
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2601 | Apartment / Hotel
|  |  | 2602 | Apartment / Hotel
|  |  | 2603 | Apartment / Hotel
|  |  | 2604 | Apartment / Hotel
|  |  | 2605 | Apartment / Hotel
|  |  | 2606 | Apartment / Hotel
|  |  | 2607 | Apartment / Hotel
|  |  | 2608 | Apartment / Hotel
|  |  | 2609 | Apartment / Hotel
|  |  | 2610 | Apartment / Hotel
|  |  | 2611 | Apartment / Hotel
|  |  | 2612 | Apartment / Hotel
Level 27
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2701 | Apartment / Hotel
|  |  | 2702 | Apartment / Hotel
|  |  | 2703 | Apartment / Hotel
|  |  | 2704 | Apartment / Hotel
|  |  | 2705 | Apartment / Hotel
|  |  | 2706 | Apartment / Hotel
|  |  | 2707 | Apartment / Hotel
|  |  | 2708 | Apartment / Hotel
|  |  | 2709 | Apartment / Hotel
|  |  | 2710 | Apartment / Hotel
|  |  | 2711 | Apartment / Hotel
|  |  | 2712 | Apartment / Hotel
Level 28
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2801 | Apartment / Hotel
|  |  | 2802 | Apartment / Hotel
|  |  | 2803 | Apartment / Hotel
|  |  | 2804 | Apartment / Hotel
|  |  | 2805 | Apartment / Hotel
|  |  | 2806 | Apartment / Hotel
|  |  | 2807 | Apartment / Hotel
|  |  | 2808 | Apartment / Hotel
|  |  | 2809 | Apartment / Hotel
|  |  | 2810 | Apartment / Hotel
|  |  | 2811 | Apartment / Hotel
|  |  | 2812 | Apartment / Hotel
Level 29
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 2901 | Apartment / Hotel
|  |  | 2902 | Apartment / Hotel
|  |  | 2903 | Apartment / Hotel
|  |  | 2904 | Apartment / Hotel
|  |  | 2905 | Apartment / Hotel
|  |  | 2906 | Apartment / Hotel
|  |  | 2907 | Apartment / Hotel
|  |  | 2908 | Apartment / Hotel
|  |  | 2909 | Apartment / Hotel
|  |  | 2910 | Apartment / Hotel
|  |  | 2911 | Apartment / Hotel
Level 30
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3001 | Apartment / Hotel
|  |  | 3002 | Apartment / Hotel
|  |  | 3003 | Apartment / Hotel
|  |  | 3004 | Apartment / Hotel
|  |  | 3005 | Apartment / Hotel
|  |  | 3006 | Apartment / Hotel
|  |  | 3007 | Apartment / Hotel
|  |  | 3008 | Apartment / Hotel
|  |  | 3009 | Apartment / Hotel
|  |  | 3010 | Apartment / Hotel
|  |  | 3011 | Apartment / Hotel
Level 31
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3101 | Apartment / Hotel
|  |  | 3102 | Apartment / Hotel
|  |  | 3103 | Apartment / Hotel
|  |  | 3104 | Apartment / Hotel
|  |  | 3105 | Apartment / Hotel
|  |  | 3106 | Apartment / Hotel
|  |  | 3107 | Apartment / Hotel
|  |  | 3108 | Apartment / Hotel
|  |  | 3109 | Apartment / Hotel
|  |  | 3110 | Apartment / Hotel
|  |  | 3111 | Apartment / Hotel
|  |  | 3112 | Apartment / Hotel
Level 32
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3201 | Apartment / Hotel
|  |  | 3202 | Apartment / Hotel
|  |  | 3203 | Apartment / Hotel
|  |  | 3204 | Apartment / Hotel
|  |  | 3205 | Apartment / Hotel
|  |  | 3206 | Apartment / Hotel
|  |  | 3207 | Apartment / Hotel
|  |  | 3208 | Apartment / Hotel
|  |  | 3209 | Apartment / Hotel
|  |  | 3210 | Apartment / Hotel
|  |  | 3211 | Apartment / Hotel
|  |  | 3212 | Apartment / Hotel
Level 33
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3301 | Apartment / Hotel
|  |  | 3302 | Apartment / Hotel
|  |  | 3303 | Apartment / Hotel
|  |  | 3304 | Apartment / Hotel
|  |  | 3305 | Apartment / Hotel
|  |  | 3306 | Apartment / Hotel
|  |  | 3307 | Apartment / Hotel
|  |  | 3308 | Apartment / Hotel
|  |  | 3309 | Apartment / Hotel
|  |  | 3310 | Apartment / Hotel
|  |  | 3311 | Apartment / Hotel
|  |  | 3312 | Apartment / Hotel
Level 34
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3401 | Apartment / Hotel
|  |  | 3402 | Apartment / Hotel
|  |  | 3403 | Apartment / Hotel
|  |  | 3404 | Apartment / Hotel
|  |  | 3405 | Apartment / Hotel
|  |  | 3406 | Apartment / Hotel
|  |  | 3407 | Apartment / Hotel
|  |  | 3408 | Apartment / Hotel
|  |  | 3409 | Apartment / Hotel
|  |  | 3410 | Apartment / Hotel
|  |  | 3411 | Apartment / Hotel
Level 35
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3501 | Apartment / Hotel
|  |  | 3502 | Apartment / Hotel
|  |  | 3503 | Apartment / Hotel
|  |  | 3504 | Apartment / Hotel
|  |  | 3505 | Apartment / Hotel
|  |  | 3506 | Apartment / Hotel
|  |  | 3507 | Apartment / Hotel
|  |  | 3508 | Apartment / Hotel
|  |  | 3509 | Apartment / Hotel
|  |  | 3510 | Apartment / Hotel
|  |  | 3511 | Apartment / Hotel
Level 36
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3601 | Apartment / Hotel
|  |  | 3602 | Apartment / Hotel
|  |  | 3603 | Apartment / Hotel
|  |  | 3604 | Apartment / Hotel
|  |  | 3605 | Apartment / Hotel
|  |  | 3606 | Apartment / Hotel
|  |  | 3607 | Apartment / Hotel
|  |  | 3608 | Apartment / Hotel
|  |  | 3609 | Apartment / Hotel
|  |  | 3610 | Apartment / Hotel
|  |  | 3611 | Apartment / Hotel
|  |  | 3612 | Apartment / Hotel
Level 37
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3701 | Apartment / Hotel
|  |  | 3702 | Apartment / Hotel
|  |  | 3703 | Apartment / Hotel
|  |  | 3704 | Apartment / Hotel
|  |  | 3705 | Apartment / Hotel
|  |  | 3706 | Apartment / Hotel
|  |  | 3707 | Apartment / Hotel
|  |  | 3708 | Apartment / Hotel
|  |  | 3709 | Apartment / Hotel
|  |  | 3710 | Apartment / Hotel
|  |  | 3711 | Apartment / Hotel
|  |  | 3712 | Apartment / Hotel
Level 38
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3801 | Apartment / Hotel
|  |  | 3802 | Apartment / Hotel
|  |  | 3803 | Apartment / Hotel
|  |  | 3804 | Apartment / Hotel
|  |  | 3805 | Apartment / Hotel
|  |  | 3806 | Apartment / Hotel
|  |  | 3807 | Apartment / Hotel
|  |  | 3808 | Apartment / Hotel
|  |  | 3809 | Apartment / Hotel
|  |  | 3810 | Apartment / Hotel
|  |  | 3811 | Apartment / Hotel
|  |  | 3812 | Apartment / Hotel
Level 39
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 3901 | Apartment / Hotel
|  |  | 3902 | Apartment / Hotel
|  |  | 3903 | Apartment / Hotel
|  |  | 3904 | Apartment / Hotel
|  |  | 3905 | Apartment / Hotel
|  |  | 3906 | Apartment / Hotel
|  |  | 3907 | Apartment / Hotel
|  |  | Disabled Bathroom | Common Disabled bathroom Rough Ins
Level 40
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 4001 | Apartment / Hotel
|  |  | 4002 | Apartment / Hotel
|  |  | 4003 | Apartment / Hotel
|  |  | 4004 | Apartment / Hotel
|  |  | 4005 | Apartment / Hotel
|  |  | 4006 | Apartment / Hotel
|  |  | 4007 | Apartment / Hotel
|  |  | 4008 | Apartment / Hotel
Level 41
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 4101 | Apartment / Hotel
|  |  | 4102 | Apartment / Hotel
|  |  | 4103 | Apartment / Hotel
|  |  | 4104 | Apartment / Hotel
|  |  | 4105 | Apartment / Hotel
|  |  | 4106 | Apartment / Hotel
|  |  | 4107 | Apartment / Hotel
|  |  | 4108 | Apartment / Hotel
|  |  | 4109 | Apartment / Hotel
Level 42
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 4201 | Apartment / Hotel
|  |  | 4202 | Apartment / Hotel
|  |  | 4203 | Apartment / Hotel
|  |  | 4204 | Apartment / Hotel
|  |  | 4205 | Apartment / Hotel
|  |  | 4206 | Apartment / Hotel
|  |  | 4207 | Apartment / Hotel
|  |  | 4208 | Apartment / Hotel
|  |  | 4209 | Apartment / Hotel
Level 43
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 4301 | Apartment / Hotel
|  |  | 4302 | Apartment / Hotel
|  |  | 4303 | Apartment / Hotel
|  |  | 4304 | Apartment / Hotel
|  |  | 4305 | Apartment / Hotel
|  |  | 4306 | Apartment / Hotel
|  |  | 4307 | Apartment / Hotel
|  |  | 4308 | Apartment / Hotel
|  |  | 4309 | Apartment / Hotel
Level 44
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 4401 | Apartment / Hotel
|  |  | 4402 | Apartment / Hotel
|  |  | 4403 | Apartment / Hotel
|  |  | 4404 | Apartment / Hotel
|  |  | 4405 | Apartment / Hotel
|  |  | 4406 | Apartment / Hotel
|  |  | 4407 | Apartment / Hotel
|  |  | 4408 | Apartment / Hotel
|  |  | 4409 | Apartment / Hotel
Level 45
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 4501 | Apartment / Hotel
|  |  | 4502 | Apartment / Hotel
|  |  | 4503 | Apartment / Hotel
|  |  | 4504 | Apartment / Hotel
|  |  | 4505 | Apartment / Hotel
|  |  | 4506 | Apartment / Hotel
|  |  | 4507 | Apartment / Hotel
Level 46
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 4601 | Apartment / Hotel
|  |  | 4602 | Apartment / Hotel
|  |  | 4603 | Apartment / Hotel
|  |  | 4604 | Apartment / Hotel
|  |  | 4605 | Apartment / Hotel
|  |  | 4606 | Apartment / Hotel
|  |  | 4607 | Apartment / Hotel
Level 47
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services | Pressure services on apartments/ Hotel or commercial floors.
|  |  | 4701 | Apartment / Hotel
|  |  | 4702 | Apartment / Hotel
|  |  | 4703 | Apartment / Hotel
|  |  | 4704 | Apartment / Hotel
|  |  | 4705 | Apartment / Hotel
|  |  | 4706 | Apartment / Hotel
|  |  | 4707 | Apartment / Hotel
Level 48 (ROOF)
|  |  | Pour 1 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 2 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Pour 3 | Set out and Penetration installation (Retail, Commercial and car park areas)
|  |  | Hot Water Plant & Return Pumps | Hot Water Plant & Return Pumps
|  |  | Roof Work | Roof work
|  |  | Aerial Drainage | Aerial Drainage
|  |  | Pressure Services Installation | Pressure Services Installation
|  |  | DRINKING COLD WATER TANK | Water Storage Tank
|  |  | COMBINED FIRE HYDRANT/SPRINKLER STORAGE TANK | Fire Hydrant/Sprinkler Pump Room & Tank
|  |  | Pump Cold Water Pump | Cold Water Pressure Pump
|  |  | Recycled Water Pump | Cold Water Pressure Pump
|  |  | Rain water tank | Water Storage Tank
Project finalisation |  |  |  | Project finalisation

## Resources
type | name | values
checklist | In-Ground Drainage Hydraulic Services ITP
section | Sewer/ Trade Waste
checkpoint | Sewer drainage, Trade Waste drainage and vents installed as per workshop drawings.
button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
button | Pipework risers labelled, pink primer and blue glue used only. | Yes,No
checkpoint | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults.
checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
checkpoint | Inspection by Fair Trading for sewer drainage to be done & other inspections if required by others.
label | Photograph inspection booking.
checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
label | Ensure compaction of fill materials is to specifications & Australian Standards.
button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
checkpoint | All works completed to specification/drawings & Area left clean/tidy & excess material stored away.
section | Stormwater
checkpoint | Stormwater drainage installed as per workshop drawings.
button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
checkpoint | Installation of pits to the correct levels.
button | Ensure correct grates & lids used with appropriate load ratings for locations to traffic movements. | Yes,No
button | Pits to be sparged - Made water tight to inlet & outlet pipework. | Yes,No
checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
checkpoint | HOLD POINT - Inspections if required by relevant authorised persons .
label | Attach inspection reports below.
checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
label | Ensure compaction of fill materials is to specifications & Australian Standards.
button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
checkpoint | All Stormwater Work completed to specification/drawings & Area left clean/tidy & excess material stored away.
section | Handover
checkpoint | Update As Built drawing immediately - Confirm IL of pipework. Attach with ITP submission.
checkpoint | CCTV completed pipework to ensure no defects before concrete Pour to prevent future problems.
checkpoint | Pictures of works completed - Attached below.
text | Concrete Pour date.
checklist | Inground Pressure Services Installation.
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check working pressures & ensure material can cater for those pressures.
checkpoint | Calibration of crimp tools, welding equipment & deburring machine ready for use..
checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
label | Ensure to keep separation between NPCW & other services as per Australian Standards.
button | Witness marks on all press Fittings checked. | Yes,No
checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any.
label | Photograph inspection booking.
checkpoint | Fire services installed correctly as per workshop drawings.
checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
label | Ensure trace tape is installed
label | Ensure compaction of fill materials is to specifications & Australian Standards.
button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
label | All services left under pressure during construction.
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Set out and Penetration installation (Retail, Commercial and car park areas)
checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
checkpoint | Wall Penetrations for pressure and drainage services complete? Installed at correct Invert levels?
checkpoint | Downpipes with columns installed and capped off with DWV caps ONLY.
checkpoint | Sewer, stormwater and pressure penetration points installed. Check off Hydraulic plans.
checkpoint | Cast in services installed at correct grades (as per AS3500) and locations. Check off Hydraulic plans.
checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in.
label | Photograph inspection booking.
checkpoint | Correct fire collars installed with test reports on file.
label | Hour rating to meet slab FRL.
checkpoint | Puddle flanges installed for floor wastes and balconies at minimum concrete height stated on structural drawings.
checkpoint | Car park drains,RWO's , trench drains and risers installed. Trafficable grates to be class D only.
label | Correct grade of drain to be installed.
checkpoint | Miscellaneous penetrations installed.
checkpoint | All pipe risers to be protected with pipe caps and or duck tape.
checkpoint | Top up water on the morning prior concrete Pour for major casting.
checkpoint | Pictures of works completed.
text | Concrete Pour date:
label | All Penetration Work completed to specification/drawings & Area left clean/tidy.
type | name
checklist | Concrete Pour Checklist (Apartment and hotel floors)
checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
checkpoint | Wall Penetrations for pressure & drainage services complete & Installed at correct Invert levels.
checkpoint | Downpipes with columns installed & capped off.
checkpoint | Correct fire collars installed with test reports on file.
label | Integrity and insulation hour rating to meet slab FRL.
checkpoint | All hydraulic service penetrations points installed.
label | Cast in services installed at correct grades (as per AS3500) & locations.
checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in.
label | Photograph inspection booking.
checkpoint | Balcony, Bathroom, Kitchen & Laundry Layouts Checked.
checkpoint | Puddle flanges installed for floor wastes and balcony drains at minimum concrete height stated on structural drawings.
label | Car Park Drains Checked.
label | Correct grates, Planter box drains or RWO installed.
checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
checkpoint | Top up water on the morning prior concrete Pour for major casting.
checkpoint | Cold water, Hot water and gas service conduits installed from lobby to apartment/hotel.
button | Cold water, Hot water and gas service conduits loops to balconies and kitchen islands installed. | Yes,No
checkpoint | Pictures of works completed.
text | Concrete Pour date:
label | All Penetration Work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Aerial Drainage
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Fire collars cleared of concrete slurry & replaced if damaged.
checkpoint | Sewer, Stormwater, Trade Waste and vent services installed correctly as per workshop drawings and schematics.
button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
button | Check for cross connections. | Yes,No
label | Pink primer and Blue glue used only on UPVC.
checkpoint | Syphonics installed as per manufacturer's recommendation
button | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults. | Yes,No
checkpoint | Hydrostatic test filled with water to a height not less than 1m above sofFit level of highest pipe for a minimum of 30min.
checkpoint | RetroFit fire collars installed.
button | Fire penetration stickers installed and photographed. High top collars to be smoke sealed. | Yes,No
checkpoint | Pipes labelled as per AS3500.
checkpoint | Acoustic lagging as per project requirements.
checkpoint | All points capped off to ensure no builders debri enters system.
button | Floor waste protected with sponge. | Yes,No
checkpoint | Update As Built drawing immediately. Confirm IL of pipework.
checkpoint | All Drainage works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Pressure Services Installation
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check scope of works/specification & ensure all documents are current.
label | Check working pressures & ensure material can cater for those pressures.
checkpoint | Calibration of crimp tools & deburring machine onsite complete.
checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
label | Ensure to keep separation between NPCW & other services as per Australian Standards.
button | Witness marks on all press Fittings checked. | Yes,No
checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any.
label | Photograph inspection booking.
checkpoint | Fire services installed correctly as per workshop drawings.
button | Gal pipe grooves checked with a groove tape. | Yes,No
checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
button | Pipe spacers installed to avoid electrofusion. | Yes,No
checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
label | All services left under pressure during construction.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | Pipes labelled as per AS3500.
checkpoint | Thermal lagging as per project requirements & AS3500.
checkpoint | Fire hose reel installed as pe Australian standards and tested.
checkpoint | Fire hose reel tagged.
checkpoint | RPZD valve installed as per AS3500.
button | RPZD drain installed & tested. | Yes,No
label | Please attach photo of serial number and valve.
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Pressure services on apartments/ Hotel or commercial floors.
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check scope of works/specification & ensure all documents are current.
label | Check working pressures & ensure material can cater for those pressures.
checkpoint | Calibration of crimp tools & deburring machine onsite complete.
checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
label | Ensure to keep separation between NPCW & other services as per Australian Standards.
button | Witness marks on all press Fittings checked. | Yes,No
checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
button | Pipe spacers installed to avoid electrofusion. | Yes,No
checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
label | All services left under pressure during construction.
checkpoint | Isolation lever shut off valves and PRV,s installed.
button | Tempering valve or Thermostatic mixing valve installed in the correct orientation. | Yes,No
button | Cold water, Hot water and or meter bars installed and labelled. | Yes,No
button | Connection of all reticulated cold, hot, Gas & NPCW PEX pipes to points of connections from manifold setups. | Yes,No
checkpoint | Floor waste grate installed.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | Pipes labelled as per AS3500.
checkpoint | Thermal lagging as per project requirements & AS3500.
checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE).
checkpoint | Garbage Chute RPZD installed and tested. (IF APPLICABLE).
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary).
checklist | Apartment / Hotel
section | Rough In
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
checkpoint | Check for any cross connections.
checkpoint | Balcony gas bayonet or water taps installed as per AS5601 and AS3500. Check foothold requirements
checkpoint | Basin wastes and toilet waste offset and tested with water if required.
checkpoint | Internal cistern installed and tested. Ensure cistern is installed as far forward.
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
button | separation of services as per AS3500 | Yes,No
checkpoint | All setouts ok and run eyes over crimps
checkpoint | HOLD POINT - Inspections if required by relevant authorised persons .
label | Photograph inspection booking.
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy
label | Pictures of works completed if applicable.
section | Apartment Commissioning
checkpoint | Bathroom, Kitchen and Laundry set out off current Architectural drawings.
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED, Laundry,bathroom, ensuite and balcony.
checkpoint | Kitchen mixer and sink installation complete.
button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexi & trap and check mini cock for leaks. | Yes,No
button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
checkpoint | Dishwasher installed with hoses, Power lead not kinked and dishwasher plum. (cover plate for hoses must be installed)
button | Run full dishwashing cycle and inspect for faults. | Yes,No
checkpoint | Cooktop installed and power plugged in.
button | Once gas is on, purge gas safely and ignite cooktop for its operation. Confirm yes once complete. | Yes,No
text | Hot water delivery to kitchen sink.
checkpoint | Laundry tub and mixer installed?
label | Tub door to swing the correct way.
button | Clean aerator, Remove Trap & Clean Out (Tighten Trap) & Test Floor Waste - Clean Out | Yes,No
button | Laundry mixer solid, check for cross connection, run tap, tighten flexi & trap and check mini cock and trap for leaks. | Yes,No
button | A/C Tundish(Cap if there is no Tundish by AC). Ensure 25mm air gap achieved. | Yes,No
button | Washing Machine taps Installed Under Tub/Opp Tub, cover plates installed and AAV installed if applicable. | Yes,No
checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
checkpoint | Basin mixer and basin installed. (photo)
button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
text | Hot water delivery to Shower.
checkpoint | Bath installed, Cement grouted in, fill tested and water tested for any pipe or plug and waste leaks.
checkpoint | Bath mixer cover plate/handle and bath spout installed.
button | Bath fill test and water run test, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
checkpoint | Balcony drains clear, overflows in place?
checkpoint | Balcony gas bayonet and or water taps installed as per AS5601 and AS3500. Test for leaks and operation.
checkpoint | Gas valves tagged, CW meter installed and tagged, Hw meter installed and tagged and NPCW installed if applicable.
checkpoint | Gas Tested with Manometer - on hold for 10 minutes. Ensure absolutely no leaks!
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
label | General photos, comments & observations during Fit out stage (Add below).
checklist | Roof work
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Builder has overflows installed.
checkpoint | Sewer vents terminated as per AS3500.
button | CCTV of sewer completed | Yes,No
checkpoint | RWO cleared of debri and CCTV completed.
checkpoint | RWO grates installed and secured.
label | Ensure protection screen installed so no pebbles block drains
checkpoint | Pressure services installed.
checkpoint | Provisions for other services installed. (IF APPLICABLE)
checkpoint | UV thermal lagging installed.
checkpoint | All hydraulic works completed to specification/drawings & Area left clean/tidy.
label | Pictures of works completed if applicable.
checklist | Hot Water Plant & Return Pumps
section | Hot water plant
checkpoint | Installation – refer to installation checklist for hot and cold water.
checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
checkpoint | Flue installed as per manufacturer's specification.
button | Power flue turned on. | Yes,No
checkpoint | Temp relief points ran to tundishes.
checkpoint | Temperature probe from control box installed into storage tanks.
checkpoint | Check that an adequate water supply is available to the hot water system.
checkpoint | Water supply pressure shall not exceed the maximum pressure stated by manufacturer.
checkpoint | Open cold water inlet valve, hot water outlet valve
checkpoint | Exercise all valves and ensure correct operation. Ensure all valves are in open position prior turning power on.
checkpoint | Check the system is fully charged & all air is bled from the system & no leaks are evident
checkpoint | Ensure hot water heaters and storage tanks are full of water and all valves are open.
checkpoint | Ensure pressures are not greater than 750Kpa to the heaters or storage tanks.
checkpoint | Open all individual gas isolation valves & purge gas lines.
checkpoint | Test gas pipe work for leaks.
checkpoint | Check the gas supply pressure at the inlet to the water heater with the water heater and all
checkpoint | range is NG: 1.13Kpa - 3.5Kpa & LPG: 2.75Kpa - 3.5Kpa
button | Clean filters and strainers once after 4 hours of use. | Yes,No
checkpoint | Set temperature to 65 degrees.
section | Hot Water Return Pumps
checkpoint | Hot Water Return Pumps - Installation – refer to installation checklist for hot and cold water.
checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
checkpoint | Ensure there is water supply to the pumps.
checkpoint | Clean filters and strainers once after 4 hours of use.
checkpoint | Turn on power to the pumps. Set the pumps to alternate.
checkpoint | Purge pumps of air. Ensure water is visible from the purging points.
checkpoint | Set balancing valves.
checkpoint | Inspect system for any leaks or faults.
checklist | Common Male Bathroom Rough In
section | Rough In
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
checkpoint | Check for any cross connections.
checkpoint | Basin wastes and toilet waste offset and tested with water if required.
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
button | separation of services as per AS3500 | Yes,No
checkpoint | All setouts ok and run eyes over crimps
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
section | Fit out and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
checkpoint | Basin mixer and basin installed.
button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
checkpoint | Urinals installed and connected to solenoid and waste.
button | Flush Urinal 3 Times (check that sensor is working fine). | Yes,No
checkpoint | HW heater installed as per drawings and specification, purged and tested.
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
label | General photos, comments & observations during Fit out stage (Add below).
checklist | Common Female Bathroom Rough In
section | Rough In
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
checkpoint | Check for any cross connections.
checkpoint | Basin wastes and toilet waste offset and tested with water if required.
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
button | separation of services as per AS3500 | Yes,No
checkpoint | All setouts ok and run eyes over crimps
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
section | Fit out and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
checkpoint | Basin mixer and basin installed.
button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
checkpoint | HW heater installed as per drawings and specification, purged and tested.
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
label | General photos, comments & observations during Fit out stage (Add below).
checklist | Common Disabled bathroom Rough Ins
section | Rough In
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
checkpoint | Check for any cross connections.
checkpoint | Basin wastes and toilet waste offset and tested with water if required.
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
button | separation of services as per AS3500 | Yes,No
checkpoint | All setouts ok and run eyes over crimps
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
section | Fit out and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
checkpoint | Basin mixer and basin installed.
button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
checkpoint | HW heater installed as per drawings and specification, purged and tested.
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
label | General photos, comments & observations during Fit out stage (Add below).
checklist | Garbage Room Work
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
button | Thermal lagging as per project requirements. | Yes,No
checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
checkpoint | Hose taps installed at correct heights.
checkpoint | Bucket trap wastes installed and grate secured.
checkpoint | Clear out debris from bucket trap floor wastes.
checkpoint | Tundish points installed as required.
checkpoint | HW heater installed as per drawings and specification, purged and tested.
checkpoint | RPZD valve installed as per AS3500.
button | RPZD drain installed and tested. | Yes,No
label | Please attach photo of serial number and valve.
checkpoint | All tests completed as per AS3500.
checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Cleaners Rooms
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
button | Thermal lagging as per project requirements. | Yes,No
checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
checkpoint | Hose taps installed at correct heights.
checkpoint | Bucket trap or floor wastes installed and grate secured.
checkpoint | Clear out debris from bucket trap or floor wastes.
checkpoint | Tundish points installed as required.
checkpoint | Fit out of cleaners room hydraulic PC items
button | Commision PC items and set Temp valve to 49 degrees | Yes,No
checkpoint | All tests completed as per AS3500.
checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Laundry
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
button | Thermal lagging as per project requirements. | Yes,No
checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
checkpoint | Hose taps installed at correct heights.
checkpoint | Bucket trap or floor wastes installed and grate secured.
checkpoint | Clear out debris from bucket trap or floor wastes.
checkpoint | Tundish points installed as required.
checkpoint | Fit out of cleaners room hydraulic PC items
button | Commision PC items and set Temp valve to 49 degrees | Yes,No
checkpoint | All tests completed as per AS3500.
checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Parents Room Rough In
section | Rough In
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
checkpoint | Check for any cross connections.
checkpoint | Basin wastes and toilet waste offset and tested with water if required.
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
button | separation of services as per AS3500 | Yes,No
checkpoint | All setouts ok and run eyes over crimps
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
section | Fit out and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
checkpoint | Basin mixer and basin installed.
button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
checkpoint | HW heater installed as per drawings and specification, purged and tested.
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
label | General photos, comments & observations during Fit out stage (Add below).
checklist | Managers Office Work - Bathroom
section | Rough In
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
checkpoint | Check for any cross connections.
checkpoint | Basin wastes and toilet waste offset and tested with water if required.
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
button | separation of services as per AS3500 | Yes,No
checkpoint | All setouts ok and run eyes over crimps
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
section | Fit out and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
checkpoint | Basin mixer and basin installed.
button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
checkpoint | HW heater installed as per drawings and specification, purged and tested.
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
label | General photos, comments & observations during Fit out stage (Add below).
checklist | Commercial Tenancy
section | Rough In
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
checkpoint | Check for any cross connections.
button | separation of services as per AS3500 | Yes,No
checkpoint | All setouts ok and run eyes over crimps
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
button | Smoke seal applied to all penetrations required. | Yes,No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
section | Fit out and Commissioning
checkpoint | Kitchen mixer and sink installation complete.
button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes,No
button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
checkpoint | Tundish point installed as required.
checkpoint | HW heater installed as per drawings and specification, purged and tested.
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
label | General photos, comments & observations during Fit out stage (Add below).
checklist | Tenancy Works
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
checkpoint | Sewer and trade waste Provisions installed in correct locations and capped off.
checkpoint | Vent provisions and AAVS installed as per documentation and AS3500.
checkpoint | Cold Water Gas Point Provision Installed in correct locations and capped off.
button | Sydney water meter installed if applicable. | Yes,No
checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE)
checkpoint | CCTV all lines to ensure clear
checklist | Water Connection
checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
checkpoint | Services scan within area completed
checkpoint | Opening permits from authorities complete. Traffic control booked in.
checkpoint | Non destructive excavation if many services are within the footpath or road.
checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
checklist | Sewer Connection
checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
checkpoint | Services scan within area completed
checkpoint | Opening permits from authorities complete. Traffic control booked in.
checkpoint | Non destructive excavation if many services are within the footpath or road.
checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
checkpoint | Fair trading inspection complete.
checklist | Stormwater Connection
checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
checkpoint | Services scan within area completed
checkpoint | Opening permits from authorities complete. Traffic control booked in.
checkpoint | Non destructive excavation if many services are within the footpath or road.
checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
checkpoint | Council inspection complete.
checklist | Gas Connection
checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
checkpoint | Services scan within area completed
checkpoint | Opening permits from authorities complete. Traffic control booked in.
checkpoint | Non destructive excavation if many services are within the footpath or road.
checkpoint | Works installed as per drawings and Tested as per Jemena requirements (attach photos if necessary)
checklist | DDCV for Fire supply
checkpoint | DDCV installed as per Sydney water guidelines.
checkpoint | check for leaks and also bracketing as per AS3500.
checkpoint | DDCV valve installed as per AS3500. For fire supply.
button | DDCV drain installed and tested. | Yes,No
label | Please attach photo of serial number and valve.
checklist | Water Meter Install & RPZD
checkpoint | Water meter installed as per Sydney water guidelines.
checkpoint | check for leaks and also bracketing as per AS3500.
checkpoint | Take photos of device & ensure to get all serial numbers
checkpoint | Test & commission device as required by certified persons
checkpoint | RPZD valve installed as per AS3500.
button | RPZD drain installed & tested. | Yes,No
label | Please attach photo of serial number and valve.
checklist | Gas Meter
checkpoint | Arrange gas inspector for inspection and requirements.
checkpoint | Gas reg to be installed on plinth if external. Install as per Jemena requirements.
checkpoint | Run breather vents off regulators if installed internally. Pipe size usually 25mm
checkpoint | Ensure the Gas reg is installed in correct orientation.
checkpoint | Labelling - 1050kpa, 210kpa and or 5 Kpa
checkpoint | Test all pipework and joints for leaks.
checkpoint | Reg test point to be facing in a direction where accessible.
checkpoint | Union or flange connection with valves so that reg can be removed or serviced.
checkpoint | Take photo of serial number and gas meter.
checkpoint | Arrange gas inspector for inspection.
label | All works completed to specification/drawings, Jemena standards & Area left clean/tidy
checklist | Oil Separator Install
checkpoint | Check Tank, Clean and flush out.
checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
checkpoint | Check all connections are secured and sound,
checkpoint | Ensure power has been connected to pump set. Tank to be a minimum 1500mm away from pump.
checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
checkpoint | Check for leaks as fill outlet line with water.
checkpoint | Oil Separator installed in correct orientation (inlet/outlet).
checkpoint | Ensure all items including oil drum are with oil Separator
checkpoint | Ensure all venting requirements are met
checkpoint | Take photo of serial number and tank.
label | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
checklist | Grease Tank
checkpoint | Check Tank, Clean and flush out.
checkpoint | Grease tank installed in correct orientation (inlet/outlet)
checkpoint | 100mm Chamber vent to atmosphere.
checkpoint | Trade waste inlet connection.
checkpoint | Accessibility around tank minimum 600mm.
checkpoint | Platform installed within room.
checkpoint | Suction line within room installed. 80mm minimum line, storz adapter and shut off valve.
checkpoint | I.O's installed inlet and outlet.
checkpoint | Ensure lids are closed off properly.
checkpoint | Take photo of serial number and tank.
checkpoint | RPZD valve installed as per AS3500.
button | RPZD drain installed & tested. | Yes,No
label | Please attach photo of serial number and valve.
checkpoint | Arrange trade waste inspection if required.
label | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
checklist | Sewer Pump Station
checkpoint | Check Tank, Clean and flush out.
checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
checkpoint | Check all connections are secured and sound,
checkpoint | Ensure power has been connected to pump set.
checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
checkpoint | Check for leaks as fill outlet line with water.
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
checklist | Storm Water Pump Station
checkpoint | Check Tank, Clean and flush out.
checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
checkpoint | Check all connections are secured and sound,
checkpoint | Ensure power has been connected to pump set.
checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
checkpoint | Check for leaks as fill outlet line with water.
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
checklist | Rainwater Pressure Pump and filtration
checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
checkpoint | Plinth Poured and vibration mounts installed.
checkpoint | Ensure all connections are sound and secure.
checkpoint | Ensure all clips & fixings installed as required.
checkpoint | Pump and filtration panel to have electrical wired up
checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
text | Date of commission
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
checklist | Cold Water Pressure Pump
checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
checkpoint | Plinth Poured and vibration mounts installed.
checkpoint | Ensure all connections are sound and secure.
checkpoint | Ensure all clips & fixings installed as required.
checkpoint | Pump and filtration panel to have electrical wired up
checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
text | Date of commission
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
checklist | Water Storage Tank
checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
checkpoint | Slab or plinth Poured and waterproofed.
checkpoint | Tank installers to install tank only.
Button | Tank supplier issues certificates and authorisation to fill tank. | Yes,No
checkpoint | All valves, overflows , tank top up and sludge drains installed to tank.
checkpoint | Fill tank up in 500mm increments. Inspect tank for any leaks and continue till you reach desired level design.
checkpoint | Dump tank and ensure sludge drain and pipe work is operational.
checkpoint | Set float valve as per manufacturer's specification.
checkpoint | Once tank is commissioned book in Chlorination by tank supplier.
checkpoint | Tank level indicator installed and connected to BMS
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
checklist | Fire Hydrant/Sprinkler Pump Room & Tank
checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
checkpoint | Cold water services installed correctly as per workshop drawings
checkpoint | Rainwater reuse service s installed correctly as per workshop drawings.
checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
checkpoint | Supply & install tank top up supply with correct float valve.
checkpoint | Wastes to be in correct locations
checkpoint | Floor wastes installed
checkpoint | Clear out debris from floor wastes
checkpoint | Tundish points installed as required
checkpoint | Water services pressure tested @ 1500KPA or 1.5 x working pressure
label | Whichever is higher for a minimum duration of 60 minutes
checkpoint | Coordination with walls and other services overviewed and coordinated onsite.
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
checklist | Hot water flush for trade waste
checkpoint | HW heater installed as per drawings and specification, purged and tested.
checkpoint | Drainage installed as per AS3500
button | Hot water flush installed and commissioned | Yes,No
checkpoint | 25mm air gap to void cross contamination
checkpoint | All tests completed as per AS3500.
checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Car Park Finalisation
checkpoint | Bracketing completed as per AS3500
checkpoint | Pipe jetting and CCTV completed
checkpoint | All RWO or CPO grates installed and secured.
checkpoint | Fire doc finalised and submitted
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
checklist | Project finalisation
checkpoint | CCTV completed throughout
checkpoint | Fire doc finalised and submitted
checkpoint | SSD produced by designer.
checkpoint | As Builts completed and issued to builder.
checkpoint | O&M manual completed and sent to builder.
checkpoint | RPZ test completed and issued to Sydney water.
checkpoint | DDCV test completed and issued to Sydney water.
checkpoint | TMV's tested throughout.
checkpoint | Gas final inspection completed and certificates sent.
checkpoint | Certification of everything required issued to builder.
checkpoint | Trade waste final inspection and certified.
checkpoint | Maintenance manual created and locked in.
checkpoint | FHR flow test completed and issued.
checklist | Variation
checkpoint | Variation Details Approved
text | Reference/Drawing/Instruction Number
text | Variation Area
text | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
checkpoint | Variation Completed