## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Aerial Drainage |  | Aerial Drainage | 6ae6f6f8-683c-44e4-9107-6f412c065b94
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
da305260-e4ae-5554-8c34-c1a6c3b425c3 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Fire collars cleared of concrete slurry & replaced if damaged.
| checkpoint | Sewer, Stormwater, tradewaste and vent services installed correctly as per workshop drawings and schematics.
387d69aa-776b-559a-b501-79374b458e48 | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
d97862c3-95e2-5adf-babe-812a7539b5ba | button | Check for cross connections. | Yes,No
1fcfbec5-b2e3-5f05-a496-464501c38431 | note | Pink primer and Blue glue used only on UPVC.
| checkpoint | Syphonics installed as per manufacturers recommendation
b0425179-1437-5fd3-b075-ddf5c08a7fa8 | button | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults. | Yes,No
| checkpoint | Hydrostatic test filled with water to a height not less than 1m above soffit level of highest pipe for a minimum of 30min.
| checkpoint | PAPA Valve installed in correct position and within maximum distance from stack
| checkpoint | Retro fit fire collars installed.
768ec93e-93fa-54fc-baf0-f225ba2bccab | button | Fire penetration stickers installed and photographed. High top collars to be smoke sealed. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Acoustic lagging as per project requirements.
| checkpoint | All points capped off to ensure no builders debri enters system.
b9aadfd5-ec94-50eb-8558-82eddd264e8b | button | Floor waste protected with sponge. | Yes,No
| checkpoint | Update As Built drawing immediately. Confirm IL of pipework.
| checkpoint | All Drainage works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Apartment / Hotel |  | Apartment / Hotel | bdaba6a1-e6ea-4ceb-8072-9b7d6e81d72e
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
f89ebe91-0534-5727-8388-5aeb3d030653 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics
| checkpoint | Check for any cross connections.
| checkpoint | Balcony gas bayonet or water taps installed as per AS5601 and AS3500. Check foothold requirements
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cistern installed and tested. Ensure cistern is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
cd4627b0-4d05-55bc-9734-e30fd3c704bf | button | Seperation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | HOLD POINT - Inspections if required by relevant authorised persons .
ee8ad886-44ef-5a0a-b01f-1b1f4d803591 | note | Photograph inspection booking.
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
b325376b-0cc3-5cc9-9d3e-7fd9d46efe43 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy
205d44bd-440d-5499-a49f-84f73c817003 | note | Pictures of works completed if applicable.
| section | Apartment Commissioning
| checkpoint | Bathroom, Kitchen and Laundry setout off current Architectural drawings.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED, Laundry,bathroom, ensuite and balcony.
| checkpoint | Kitchen mixer and sink installation complete.
5210df13-5ca1-57d9-aa3f-fe4a59e4c2fb | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes,No
b3bb2cfc-7cce-5529-9625-740574b385e4 | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Dishwaher installed with hoses, Power lead not kinked and dishwasher plum. (cover plate for hoses must be installed)
71b30427-baf3-522b-94df-3b7f2df4fd71 | button | Run full dishwashing cyle and inspect for faults. | Yes,No
c4d7d535-7f47-58ab-83fd-cf3a116616f5 | button | Once gas is on, purge gas safely. Confirm yes once complete. | Yes,No
f471c7e6-3687-5e59-bf41-0eb740c9107e | textbox | Hot water delivery to kitchen sink.
| checkpoint | Laundry tub and mixer installed?
b2c1a0dc-a4f2-5cb0-8f3f-cfa17e9bf14f | note | Tub door to swing the correct way.
351b0f07-51a8-502e-a1c9-6cdc60cd29b8 | button | Clean aerator, Remove Trap & Clean Out (Tighten Trap) & Test Floor Waste - Clean Out | Yes,No
7eb5e944-b62b-5c43-a0b8-7d6920579113 | button | Laundry mixer solid, check for cross connection, run tap, tighten flexis& trap and check mini cock and trap for leaks. | Yes,No
19e32657-49eb-5ad2-a69b-38b5df12c1db | button | A/C Tundish(Cap if there is no Tundish by AC). Ensure 25mm airgap achieved. | Yes,No
a1b6afdd-40fa-5cbc-829b-83a8b850590b | button | Washing Machine taps Installed Under Tub/Opp Tub, cover plates installed and AAV installed if applicable. | Yes,No
| checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested.
68b504ff-4c6f-5e10-aeb7-4fb43d422fa4 | button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer's and basin's installed. (photo)
d3468432-95fe-570b-9924-d9c71049e09c | button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
6f5af162-5621-5492-b349-7226e8309489 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
a6e06745-0a11-5f19-aef3-9032dad84beb | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes,No
c104fba1-f7c0-549d-977f-ce72903bfd87 | textbox | Hot water delivery to Shower.
| checkpoint | Bath installed, Cement grouted in, fill tested and water tetsed for any pipe or plug and waste leaks.
| checkpoint | Bath mixer cover plate/handle and bath spout installed.
9233dc3a-d569-5fd7-ac4d-cee465f008ed | button | Bath fill test and water run test, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Balcony drians clear, overflows in place?
| checkpoint | Balcony gas bayonet and or water taps installed as per AS5601 and AS3500. Test for leaks and operation.
| checkpoint | Gas valves tagged, CW meter installed and tagged, Hw meter installed and tagged and NPCW installed if applicable.
| checkpoint | Gas Tested with Manometer - on hold for 10 minutes. Ensure absolutely no leaks!
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
ce2db531-599d-5c63-bde1-b2fd258a5083 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
975b9c27-9b76-53cc-87c7-687bab89faf5 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
f0d20b6f-2932-57f5-a857-8592c58cdd99 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Carpark finalisation |  | Carpark finalisation | 1479da93-c04a-449b-a78e-913ed0e4fd18
| checkpoint | Bracketing completed as per AS3500
| checkpoint | Pipe jettiing and CCTV completed
| checkpoint | All RWO or CPO grates installed and secured.
| checkpoint | Fire doc finalised and submitted
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Cleaners Rooms |  | Cleaners Rooms | c5b650cd-adeb-41b3-bb56-abf809965180
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
44567d69-eea5-5d82-8f31-ae89cfb6e967 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drianage services installed as per workshop drawings and AS3500.
dd346d07-f6d0-5322-9a96-bd60163115e3 | button | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap or floor wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap or floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | Fit out of cleaners room hydraulic PC items
4874ccb8-6746-53d6-a1f1-56d7891e7cec | button | Commision PC items and set Temp valve to 49 degrees | Yes,No
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Cold Water Pressure Pump |  | Cold Water Pressure Pump | d245fda1-c321-454f-adc3-a18e89d9777c
| checkpoint | RW pump and fiiltration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have elctrical wired up
| checkpoint | Pump supplier to commission . Purge pumpset and set pressures corrcetly.
98794203-3297-5988-8c5b-1845b2c093ce | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Commercial / Club Tenancy |  | Commercial / Club Tenancy | 3952e228-4bcb-40a8-a668-3faffb3f9e4b
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
88de582b-1d19-5835-88ce-89c4004dc858 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics
| checkpoint | Check for any cross connections.
e6007dec-1485-5cda-9b9e-dbf6e078cddf | button | Seperation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
bea62df1-288d-57b1-8457-a1513e1532e6 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Kitchen mixer and sink installation complete.
a805af0f-65a9-5681-b6c2-d1b616962812 | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes,No
d9716a52-23da-5472-9b14-b55616f16abd | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Tundish point installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
47c96430-1bab-59e2-96b1-b713f53e385b | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
431dedd5-f4ab-50c2-9daa-a1f8ad13e6a1 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
af5dafdb-566d-57a5-a74e-f86b38385188 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Common Disabled bathroom roughins |  | Common Disabled bathroom roughins | 6023dfab-363f-4991-a31e-1f2ef8451d04
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
0533978b-31ef-5ee5-885d-b5ae7789e72f | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
bc95ceeb-2469-574b-b189-a18d6c8a5147 | button | Seperation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
9c71dac5-9d8f-511f-a1a9-f30babc3a760 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested.
0b7b4aae-b93f-5069-a384-426665a4c00c | button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer's and basin's installed.
13b1ba90-edf4-539b-bbb8-d1f0dfd33474 | button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
ddf31a48-c21c-5911-b250-bbe53986fbb4 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
ee640a7f-18c1-5fc6-bc7b-0ae3a8486367 | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
dc51580d-a55f-5dd3-82a7-b14ff304d0e9 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
6c952bce-81a0-562e-9321-1cb2d0910906 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
a5b3f382-1550-52db-b8c0-3a013530127f | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Common Female Bathroom Rough In |  | Common Female Bathroom Rough In | 19795c77-e509-4673-862e-eefa95645367
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
0f73c83d-460f-581e-aa82-8acf73f26cbe | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
d201e0bd-f5b5-5e79-b4e9-30277632a9e1 | button | Seperation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
d6a36994-a13d-5054-99c9-64c3ca9f41af | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested.
4076bd37-326a-5bfe-b4ae-e86bd4320b2a | button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer's and basin's installed.
bb5c73c7-8f30-5971-98e0-3efb5b9495e1 | button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
80e63adf-68e8-5d4c-a2a7-16d8da19fa06 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
4a11a911-2354-565f-8eba-50e3cf7bf1ab | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
2bfdc5d6-706a-570e-9f85-e6d38a919215 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
e0b8a9cc-632a-5275-9728-c18859984ad0 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
4e72f632-7cd9-5395-a4d9-f7864e44d96b | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Common Male Bathroom Rough In |  | Common Male Bathroom Rough In | 11e06330-d523-4bdf-8b24-f7f3fe460b66
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
851340c5-8898-54a3-a210-3f0dfcf3ea33 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
df709564-b5ab-513c-b658-8214c182a392 | button | Seperation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
ad6e9a98-41f4-5a27-90c6-e26c50a36d58 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested.
d4764ef0-fb88-542f-96fb-c35f2d9c110d | button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer's and basin's installed.
9045f7c6-1de2-549b-ae13-4e926e6d730b | button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
8f33b864-698e-50e1-82c9-95d202e6260a | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
276b8a99-4685-5889-930b-bc12c939ba18 | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Urinals installed and connected to solenoid and waste.
0003b0fc-cdcb-590f-ad52-f4a471c581e3 | button | Flush Urinal 3 Times (check that sensor is working fine). | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
9ca5a020-8928-520e-94a4-599dd583377d | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
e2f112ea-edd1-56cf-9744-191444a7bb5b | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
ba5ea167-576d-5c46-9780-e0656af44b23 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Concrete Pour Checklist (Apartment and hotel floors) |  | Concrete Pour Checklist (Apartment and hotel floors) | 54c24546-075b-4ed7-a497-768c4a235e29
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure & drainage services complete & Installed at correct Invert levels.
| checkpoint | Downpipes with columns installed & capped off.
| checkpoint | Correct fire collars installed with test reports on file.
350a5f4d-4df7-5b61-9ebe-48acbd759511 | note | Integrity and insulation hour rating to meet slab FRL.
| checkpoint | All hydraulic service penetrations points installed.
38567e78-3b5d-54c1-832b-d105d7a18497 | note | Cast in services installed at correct grades (as per AS3500) & locations.
| checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in.
c86c30ba-c0ab-5925-9538-dd676dedb409 | note | Photograph inspection booking.
| checkpoint | Balcony, Bathroom, Kitchen & Laundry Layouts Checked.
aee884dc-7d73-5f15-88a8-0e9b2daf3196 | note | Check off Hydraulic plans
| checkpoint | Puddle flanges installed for floor wastes and balcony drains at minimum concrete height stated on structural drawings.
23981587-ec2a-5fc9-b655-f863a6b7f5dc | note | Car Park Drains Checked.
401a0e15-87e4-5c4f-a2bb-208d6ef6cdfb | note | Correct grates, Planter box drains or RWO installed.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Top up water on the morning prior concrete pour for major casting.
| checkpoint | Cold water, Hot water and gas service conduits installed from lobby to apartment/hotel.
e028bc70-ae2b-5d27-9cfc-1dea26c4870b | button | Cold water, Hot water and gas service conduits loops to balconies and kitchen islands installed. | Yes,No
| checkpoint | Pictures of works completed.
dfab8552-836e-5fc5-8c83-92b6cc3c123f | textbox | Concrete pour date:
b24bd130-77e0-535d-9897-ecb7f73fb963 | note | All Penetration Work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | DDCV for Fire supply |  | DDCV for Fire supply | e7fda3c9-8aaa-4d3a-aaab-a1b689681eb9
| checkpoint | DDCV installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | DDCV valve installed as per AS3500. For fire supply.
baba77ad-8732-54ef-af42-2c767f8d5f15 | button | DDCV drain installed and tested. | Yes,No
511c8a46-de64-5cee-b72a-ff1501b68180 | note | Please attach photo of serial number and valve.
| checklist | Fire Hydrant/Sprinkler Pump Room & Tank |  | Fire Hydrant/Sprinkler Pump Room & Tank | 55151560-6fba-4616-822d-ab80aef51557
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Cold water services installed correctly as per workshop drawings
| checkpoint | Rainwater reuse service s installed correctly as per workshop drawings.
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Supply & install tank top up supply with correct float valve.
| checkpoint | Wastes to be in correct locations
| checkpoint | Floor wastes installed
| checkpoint | Clear out debris from floor wastes
| checkpoint | Tundish points installed as required
| checkpoint | Water services pressure tested @ 1500KPA or 1.5 x working pressure
e35a1d68-5c92-5a93-a2cb-32ea0064672d | note | Whichever is higher for a minimum duration of 60 minutes
| checkpoint | Coordination with walls and other services overviewed and coordinated onsite.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Garbage Room Work |  | Garbage Room Work | 9a7c44cb-fca9-4b1e-9aeb-c317c98be352
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
b20c5e67-ea79-5b7c-ad2a-2f486de7d624 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drianage services installed as per workshop drawings and AS3500.
a817c139-e34f-51c1-a900-518c1b81b874 | button | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | RPZD valve installed as per AS3500.
914b4ada-1580-51b9-aaff-b48a8ec03808 | button | RPZD drain installed and tested. | Yes,No
a2ea532e-e05e-560f-9c68-a5f7fed7b1c7 | note | Please attach photo of serial number and valve.
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Gas Connection |  | Gas Connection | 907b98f5-5e3c-4a1e-92bc-7d6fce9fa5a2
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per Jemena requirements (attach photos if necessary)
| checklist | Gas Meter |  | Gas Meter | 78ed59eb-179d-49f9-81ff-aacf990a7ae2
| checkpoint | Arrange gas inspector for inspection and requirements.
| checkpoint | Gas reg to be installed on plinth if external. Install as per Jemena requirments.
| checkpoint | Run breather vents off regulators if installed internally. Pipe size usually 25mm
| checkpoint | Ensure the Gas reg is installed in correct orientation.
| checkpoint | Labelling - 1050kpa, 210kpa and or 5 Kpa
| checkpoint | Test all pipework and joints for leaks.
| checkpoint | Reg test point to be facing in a direction where accessible.
| checkpoint | Union or flange connection with valves so that reg can be removed or serviced.
| checkpoint | Take photo of serial number and gas meter.
| checkpoint | Arrange gas inspector for inspection.
6f181dda-5a94-5af6-8542-a17c08f2dce3 | note | All works completed to specification/drawings, Jemena standards & Area left clean/tidy
| checklist | Grease Tank |  | Grease Tank | 43bb7219-8d4c-4ec7-96e0-d72af5d2177a
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Grease tank installed in correct orientation (inlet/outlet)
| checkpoint | 100mm Chamber vent to atmosphere.
| checkpoint | Trade waste inlet connection.
| checkpoint | Accessibility around tank minimum 600mm.
| checkpoint | Platform installed within room.
| checkpoint | Suction line within room installed. 80mm minimum line, storz adapter and shut off valve.
| checkpoint | I.O's installed inlet and outlet.
| checkpoint | Ensure lids are closed off properly.
| checkpoint | Take photo of serial number and tank.
| checkpoint | RPZD valve installed as per AS3500.
a126837e-84a5-5fb4-947b-d51a2cd3f82b | button | RPZD drain installed & tested. | Yes,No
e1950bbe-d8f4-5281-b96c-3d7a71a8d9f8 | note | Please attach photo of serial number and valve.
| checkpoint | Arrange trade waste inspection if required.
822ab91c-17fc-556f-aba7-26e7add9686a | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Hot water flush for trade waste |  | Hot water flush for trade waste | 8b94ac66-99e8-4c5b-8483-5bdfd6c75d45
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Drainage installed as per AS3500
bde789d3-b493-5b5b-afd7-82eb0e5edffd | button | Hot water flush installed and commissioned | Yes,No
| checkpoint | 25mm airgap to void cross contamination
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | HOT WATER PLANT and RETURN PUMPS |  | HOT WATER PLANT and RETURN PUMPS | 5fa4bb6d-8184-4ab5-95f9-d6a35c36f277
| section | Hot water plant
| checkpoint | Installation – refer to installation check list for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Flue installed as per manufacturers specification.
a7e55e6f-8edf-5ba1-8496-ceb1d4c1f1b6 | button | Power flue turned on. | Yes,No
| checkpoint | Temp relief points ran to tundishes.
| checkpoint | Temperature probe from control box installed into storage tanks.
| checkpoint | Check that an adequate water supply is available to the hot water system.
| checkpoint | Water supply pressure shall not exceed the maximum pressure stated by manufacturer.
| checkpoint | Open cold water inlet valve, hot water outlet valve
| checkpoint | Exercise all valves and ensure correct operation. Ensure all valves are in open position prior turning power on.
| checkpoint | Check the system is fully charged & all air is bled from the system & no leaks are evident
| checkpoint | Ensure hot water heaters and storage tanks are full of water and all valves are open.
| checkpoint | Ensure pressures are not greater then 750Kpa to the heaters or storage tanks.
| checkpoint | Open all individual gas isolation valves & purge gas lines.
| checkpoint | Test gas pipe work for leaks.
| checkpoint | Check the gas supply pressure at the inlet to the water heater with the water heater and all
| checkpoint | Range is NG: 1.13Kpa - 3.5Kpa & LPG: 2.75Kpa - 3.5Kpa
f58eb1ec-bafb-5bc3-ad74-19991651b84d | button | Clean filters and strainers once after 4 hours of use. | Yes,No
| checkpoint | Set temperature to 65 degrees.
| section | HOT WATER RETURN PUMPS
| checkpoint | Hot water return pumps - Installation – refer to installation check list for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Ensure there is water supply to the pumps.
| checkpoint | Clean filters and strainers once after 4 hours of use.
| checkpoint | Turn on power to the pumps. Set the pumps to alternate.
| checkpoint | Purge pumps of air. Ensure water is visible from the purging points.
| checkpoint | Set balancing valves.
| checkpoint | Inspect system for any leaks or faults.
| checklist | In-Ground Drainage Hydraulic Services ITP V.210121 |  | In-Ground Drainage Hydraulic Services ITP V.210121 | 481b2589-7dc0-47d4-9f29-1320e417222e
| section | Sewer/ Tradewaste
| checkpoint | Sewer drainage, Tradewaste drainage and vents installed as per workshop drawings.
f93776c2-c720-53f9-aa03-c25291b81272 | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
ebd46074-1789-5dbe-90b7-7bdef2e180a8 | button | Pipework risers labelled, pink primer and blue glue used only. | Yes,No
| checkpoint | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Inspection by Fair Trading for sewer drainage to be done & other inspections if required by others.
b971c59e-e278-55e0-8ba1-f8637d680dcb | note | Photograph inspection booking.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
26b11abb-db05-5b96-a3e6-b8f9ccf4cc0a | note | Ensure compaction of fill materials is to specifications & Australian Standards.
1178bef7-f494-5d6b-82c5-19a893ac0c24 | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
| checkpoint | All works completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Stormwater
| checkpoint | Stormwater drainage installed as per workshop drawings.
067c07cf-688a-584a-b7fe-fc7089304efa | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
| checkpoint | Installation of pits to the correct levels.
6922fdd1-d7cd-5b0d-b8c7-b80016a11cf1 | button | Ensure correct grates & lids used with appropriate load ratings for locations to traffic movements. | Yes,No
a1e016c2-6cc0-53b5-987a-f9e3f5465aab | button | Pits to be sparged - Made water tight to inlet & outlet pipework. | Yes,No
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | HOLD POINT - Inspections if required by relevant authorised persons .
adab1e9b-8b04-5552-9f64-5585b5e4db3e | note | Attach inspection reports below.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
b1adc01c-d7ad-5bcc-adbe-d60c1411d796 | note | Ensure compaction of fill materials is to specifications & Australian Standards.
dbac801e-2e4c-5551-9e52-3001105b08de | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
| checkpoint | All Stormwater Work completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Handover
| checkpoint | Update As Built drawing immediately - Confirm IL of pipework. Attach with ITP submission.
| checkpoint | CCTV completed pipework to ensure no defects before concrete pour to prevent future problems.
| checkpoint | Pictures of works completed - Attached below.
713815e4-3c3e-50ed-bb39-8192e8490edd | textbox | Concrete pour date.
| checklist | Inground Pressure Services Installation. |  | Inground Pressure Services Installation. | 6d424fe6-d526-4d9e-ae0f-b86efd5d08ea
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
46b4d74c-019c-5c84-95e7-affc2b1c5eb7 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools, welding equipment & deburring machine ready for use..
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics.
cb1dfd4c-a5a6-5565-b38b-4bc65835bbba | note | Ensure to keep seperation between NPCW & other services as per Australian Standards.
cada9f90-8a46-59c5-b823-bdc168b774eb | button | Witness marks on all press fittings checked. | Yes,No
| checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any.
df0a0485-50b5-5b65-bfac-0c1bbd23c0f6 | note | Photograph inspection booking.
| checkpoint | Fire services installed correctly as per workshop drawings.
| checkpoint | Water servces tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
bffb0a90-6e0a-55ad-9cb9-73cbc04ce61b | note | Ensure trace taoe is installed
1fba5f37-43ac-5107-a9ae-2b063b1fee1a | note | Ensure compaction of fill materials is to specifications & Australian Standards.
fdc3dcad-e97f-52ab-90cd-b52935debe98 | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Pass, Fail, N/A
c4634940-a6bf-5ac4-83d1-af738546dd41 | note | All services left under pressure during construction.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Managers Office Work - Bathroom |  | Managers Office Work - Bathroom | 279b9131-f000-4f8b-8457-9b909dff1189
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
db6186bd-bd5e-5ef2-9635-77653bfbfa94 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
195c4bf0-174e-5a94-8635-7b5b838c7052 | button | Seperation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
d84b90ab-b149-5fcf-9c9b-cd5c79afb836 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested.
11fb15df-7a13-5527-bb52-9e2f9cb3ba6f | button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer's and basin's installed.
0c2c95da-a75d-5129-b903-dea3f951c5c8 | button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
5279148c-9fb9-5d6b-85cf-08c96e7fedfd | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
1110cbcc-c206-5b7e-a3b0-04e43364ed2f | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
548ac7b2-c8d7-56bf-844c-ab0f1d37358d | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
eb052419-a68e-5d08-8e17-c97a129a7a0b | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
f3b0853d-eeac-5f52-920d-4bb4cd485d66 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Oil Separator Install |  | Oil Separator Install | 6358360e-2d88-4f54-919f-4a71fec51d30
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set. Tank to be a minimum 1500mm away from pump.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | Oil Separator installed in correct orientation (inlet/outlet).
| checkpoint | Ensure all items including oil drum are with oil Separator
| checkpoint | Ensure all venting requirements are met
| checkpoint | Take photo of serial number and tank.
4359d0f5-6f1d-55af-ab4f-ffcbe05d697f | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Parents Room Rough In |  | Parents Room Rough In | b8dd281f-ac8b-4e23-bd2d-9755c0da06e8
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
a40e9114-be04-5899-8a41-93d6e95e25af | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
35d2385d-a91f-5d09-a344-5946ffc606dc | button | Seperation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
1570f633-c236-5cdc-b099-c4af2a3c12a7 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested.
5d22161c-eb8f-5505-9448-51699625ac6d | button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer's and basin's installed.
cb7c0bcd-bb82-57bf-b32a-ae8756c22d42 | button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
3a01a67f-fa20-56de-80a9-1d30e24e82b4 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
7f09d7c3-7582-559d-a1f0-ec3af944e4ab | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
667d0587-a768-56eb-9e9a-451211507821 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
516ed1fc-c790-54c9-b504-48a73fbe523c | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
9da55754-16ac-5270-a96d-5d9f362a5914 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Pressure Services Installation |  | Pressure Services Installation | ac7deaa8-08d0-4c2e-815c-3ee116cf4cc1
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
e1941997-62e9-52cc-bdaa-345a524922a2 | note | Check scope of works/specification & ensure all documents are current.
0d66669d-5c46-5dfd-9763-73fa8cecf7d5 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics.
f7e26cf6-a395-5889-90b3-39134c703621 | note | Ensure to keep seperation between NPCW & other services as per Australian Standards.
bb925911-4773-504c-94a3-5f71fa3f5132 | button | Witness marks on all press fittings checked. | Yes,No
| checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any.
a204084a-2ef8-55e2-9bdd-1aefb3113a68 | note | Photograph inspection booking.
| checkpoint | Fire services installed correctly as per workshop drawings.
067d6c76-d7c2-5ac7-9832-a71fe96965d3 | button | Gal pipe grooves checked with a groove tape. | Yes,No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
f544352d-168e-5285-87f9-24c374d58438 | button | Pipe spacers installed to avoid electrofusion. | Yes,No
| checkpoint | Water servces tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
9da40e03-57e9-53e2-bf5c-8fac60ce74f0 | note | All services left under pressure during construction.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
4f586440-8b8d-5603-a72c-6507befa6c96 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards and tested.
| checkpoint | Fire hose reel tagged.
| checkpoint | RPZD valve installed as per AS3500.
4d15aae9-eb21-5fba-a2cb-daadf70654f6 | button | RPZD drain installed & tested. | Yes,No
eca0cd03-8671-5569-beb4-06e6e5900af5 | note | Please attach photo of serial number and valve.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Pressure services on apartments/ Hotel or commercial floors. |  | Pressure services on apartments/ Hotel or commercial floors. | a168b2b5-45db-439d-be4b-2c19ae5f8b83
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
8bec3af6-ad73-53d3-bc0c-6060bcc01c51 | note | Check scope of works/specification & ensure all documents are current.
46c66759-6ed3-5ea7-9420-4e380ef1da9f | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics.
cfa40b43-4ce4-58cb-aff1-3536b5333149 | note | Ensure to keep seperation between NPCW & other services as per Australian Standards.
c664c5eb-dc57-5854-a746-f58d3264a2d8 | button | Witness marks on all press fittings checked. | Yes,No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
4e69e1cf-d7d1-5b01-bfb4-098df20aeda7 | button | Pipe spacers installed to avoid electrofusion. | Yes,No
| checkpoint | Water servces tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
bbec29ca-77a0-5bad-8dc0-ac880cf01f45 | note | All services left under pressure during construction.
| checkpoint | Isolation lever shut off valves and PRV,s installed.
ab6f48d8-4178-52b5-8f04-5c36ba421965 | button | Tempering valve or Thermostatic mixing valve installed in the correct orientation. | Yes,No
46c9306b-422f-5054-9d1b-2c43ed4362e8 | button | Cold water, Hot water and or meter bars installed and labelled. | Yes,No
a1e3e8ed-8a77-5829-b880-48bd166b1f78 | button | Connection of all reticulated cold, hot, Gas & NPCW PEX pipes to points of connections from manifold setups. | Yes,No
| checkpoint | Floor waste grate installed.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
7082881b-8df8-5d16-b683-0d20b53e363e | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE).
| checkpoint | Garbage Chute RPZD installed and tested. (IF APPLICABLE).
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary).
| checklist | Project finalisation |  | Project finalisation | eda8b19e-406b-4f11-afbe-2cd14e16933f
| checkpoint | CCTV complted throughout
| checkpoint | Fire doc finalised and submitted
| checkpoint | SSD produced by designer.
| checkpoint | Asbuilts completed and issued to builder.
| checkpoint | O&M manual completed and sent to builder.
| checkpoint | RPZ test completed and issued to Sydney water.
| checkpoint | DDCV test completed and issued to Sydney water.
| checkpoint | TMV's tested throughout.
| checkpoint | Gas final inspection completed and certificates sent.
| checkpoint | Certification of everything required issued to builder.
| checkpoint | Trade waste final inspection and certified.
| checkpoint | Maintenace manual created and locked in.
| checkpoint | FHR flow test completed and issued.
| checklist | Rainwater Pressure Pump and filtration |  | Rainwater Pressure Pump and filtration | f0e44472-535e-4343-800c-8541a31b5551
| checkpoint | RW pump and fiiltration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have elctrical wired up
| checkpoint | Pump supplier to commission . Purge pumpset and set pressures corrcetly.
6a51a019-35d7-5216-b959-2ab595b34dca | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Roof work |  | Roof work | a5a9c568-8735-47a2-82cc-f8adfa8fca26
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
24c9848b-da76-5c88-8969-4b5c4b6fa390 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Builder has overflows installed.
| checkpoint | Sewer vents terminated as per AS3500.
abfb40cc-173d-5c56-b4a5-6071bc8aceaf | button | CCTV of sewer completed | Yes,No
| checkpoint | RWO cleared of debri and CCTV completed.
| checkpoint | RWO grates installed and secured.
c953974a-85e7-5dbf-a062-82925526e8ae | note | Ensure pprotection screen installed so no pebbles block drains
| checkpoint | Pressure services installed.
| checkpoint | Provisions for other services installed. (IF APPLICABLE)
| checkpoint | UV thermal lagging installed.
| checkpoint | All hydraulic works completed to specification/drawings & Area left clean/tidy.
226f28dd-35b9-5aff-abdb-d3c952a19367 | note | Pictures of works completed if applicable.
| checklist | RPZD and Water Meter Install |  | RPZD and Water Meter Install | 8f274160-1c94-4ecd-a60c-9cbc2c7fa760
| checkpoint | Water meter installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | Take photos of device & ensure to get all serial numbers
| checkpoint | Test & commission device as required by certified persons
| checkpoint | RPZD valve installed as per AS3500.
f2f14121-f789-5d5c-ac22-5481513e1bce | button | RPZD drain installed & tested. | Yes,No
58f129e1-aa5a-587b-b171-8bef7befb908 | note | Please attach photo of serial number and valve.
| checklist | Setout and Penetration installation (Retail, Commercial and carpark areas) |  | Setout and Penetration installation (Retail, Commercial and carpark areas) | 0d4b65fc-cbe6-455b-9dd6-65b9ae41dfe0
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure and drainage services complete? Installed at correct Invert levels?
| checkpoint | Downpipes with columns installed and capped off with DWV caps ONLY.
| checkpoint | Sewer, stormwater and pressure penetration points installed. Check off Hydraulic plans.
| checkpoint | Cast in services installed at correct grades (as per AS3500) and locations. Check off Hydraulic plans.
| checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in.
6dc81091-8168-5dab-b984-7e2e649672db | note | Photograph inspection booking.
| checkpoint | Correct fire collars installed with test reports on file.
7cee8454-fbb4-508e-87d4-216223edda3d | note | Hour rating to meet slab FRL.
| checkpoint | Puddle flanges installed for floor wastes and balconies at minimum concrete height stated on structural drawings.
| checkpoint | Car park drains,RWO's , trench drains and risers installed. Trafficable grates to be class D only.
5ab321f4-e9eb-54d6-8180-f9fe01670f80 | note | Correct grade of drain to be installed.
| checkpoint | Miscellaneous penetrations installed.
| checkpoint | All pipe risers to be protected with pipe caps and or duck tape.
| checkpoint | Top up water on the morning prior concrete pour for major casting.
| checkpoint | Pictures of works completed.
bc50b969-ad61-5d02-9ea4-6f98a76785e4 | textbox | Concrete pour date:
ddfe3db5-1c2f-51a8-86f5-fa094a21f219 | note | All Penetration Work completed to specification/drawings & Area left clean/tidy.
| checklist | Sewer Connection |  | Sewer Connection | 9ae6e9f9-a317-4e79-aa9e-c7867db7e047
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Fair trading inspection complete.
| checklist | Sewer Pump Station |  | Sewer Pump Station | 8eab3e0a-a4e7-4dc6-8ecc-6126afa9a502
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Storm Water Pump Station |  | Storm Water Pump Station | 8200c10f-ead4-43f6-8872-2dcecbe2ac44
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Stormwater Connection |  | Stormwater Connection | 6e4a04d6-df64-49fe-a645-03cb41eb856b
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Council inspection complete.
| checklist | Tenancy Works |  | Tenancy Works | 30d6dfaa-2798-45da-986f-23efe75a2a06
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
| checkpoint | Sewer and trade waste Provisions installed in correct locations and capped off.
| checkpoint | Vent provisions and AAVS installed as per documetation and AS3500.
| checkpoint | Cold Water Gas Point Provision Installed in correct locations and capped off.
ba716582-2ed1-5c20-9d76-83fe6bdb856e | button | Sydney water meter installed if applicable. | Yes,No
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE)
| checkpoint | CCTV all lines to ensure clear
| checklist | Variation |  | Variation | b57fa43a-f8d6-4a0a-8880-28fd50281901
| checkpoint | Variation Details Approved
a929ac5e-2bce-59ce-aa5d-7f75907c1cb4 | textbox | Reference/Drawing/Instruction Number
c6c72571-6b2f-56b2-9721-edf43352dcc0 | textbox | Variation Area
399da4fe-fbcb-547d-b5e7-bd395bae061e | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
| checkpoint | Variation Completed
| checklist | Water Connection |  | Water Connection | 7b140b4b-75a7-45fb-8c67-e576b7d86405
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checklist | Water Storage Tank |  | Water Storage Tank | ceab7ef9-dde5-4113-b9a5-b617f7259599
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Slab or plinth poured and waterproofed.
| checkpoint | Tank installers to install tank only.
17db4347-257d-589a-81b4-e8f01071ee9c | button | Tank supplier issues certificates and authorisation to fill tank. | Pass, Fail, N/A
| checkpoint | All valves, overflows , tank top up and sludge drains installed to tank.
| checkpoint | Fill tank up in 500mm increments. Inspect tank for any leaks and continue till you reach desired level design.
| checkpoint | Dump tank and ensure sludge drain and pipe work is operational.
| checkpoint | Set float valve as per manufacturer's specification.
| checkpoint | Once tank is commissioned book in Chlorination by tank supplier.
| checkpoint | Tank level indicator installed and connected to BMS
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)