## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Aerial Drainage |  | Aerial Drainage | f649e138-206b-48dc-8c00-002e1fed261f
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
de75d48d-6b24-59f4-96e3-57af7ba9b1a4 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Fire collars cleared of concrete slurry & replaced if damaged.
| checkpoint | Sewer, Stormwater, Trade Waste and vent services installed correctly as per workshop drawings and schematics.
ea57f42e-3d54-500e-9bcc-0f94f3cc1146 | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
11e8e96a-d798-573e-95ff-0f2589712026 | button | Check for cross connections. | Yes,No
f804c161-baa0-56d0-9180-5103bfd1901d | note | Pink primer and Blue glue used only on UPVC.
| checkpoint | Syphonics installed as per manufacturer's recommendation
78e417d7-8e6b-5526-b57a-027b1a2281e2 | button | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults. | Yes,No
| checkpoint | Hydrostatic test filled with water to a height not less than 1m above sofFit level of highest pipe for a minimum of 30min.
| checkpoint | RetroFit fire collars installed.
69e8369e-e7c4-5b22-9e96-672b76d7c497 | button | Fire penetration stickers installed and photographed. High top collars to be smoke sealed. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Acoustic lagging as per project requirements.
| checkpoint | All points capped off to ensure no builders debri enters system.
8d220e87-7511-5008-8af4-228620b17648 | button | Floor waste protected with sponge. | Yes,No
| checkpoint | Update As Built drawing immediately. Confirm IL of pipework.
| checkpoint | All Drainage works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Apartment / Hotel |  | Apartment / Hotel | 88eab8a7-c4c2-4356-9ab4-ee1bf4a0b1d4
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
786a9a17-4ec3-5be0-a7ee-7a50ebcc80f3 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Balcony gas bayonet or water taps installed as per AS5601 and AS3500. Check foothold requirements
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cistern installed and tested. Ensure cistern is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
b714287f-8b77-541e-bf9c-7f1571f8d48d | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | HOLD POINT - Inspections if required by relevant authorised persons .
5a27a43c-ff62-5f05-9e06-db8e71cee79a | note | Photograph inspection booking.
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
e5cf3ce6-58e7-5230-bac0-3f249e776398 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy
6b1700ca-f765-507b-b648-a2da1d4cef3f | note | Pictures of works completed if applicable.
| section | Apartment Commissioning
| checkpoint | Bathroom, Kitchen and Laundry set out off current Architectural drawings.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED, Laundry,bathroom, ensuite and balcony.
| checkpoint | Kitchen mixer and sink installation complete.
bd4832aa-5b1e-5ab8-98a2-d5363a28af1b | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexi & trap and check mini cock for leaks. | Yes,No
2b83a908-f425-5126-a9fb-42c403cc81e9 | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Dishwasher installed with hoses, Power lead not kinked and dishwasher plum. (cover plate for hoses must be installed)
ad47e6ef-7f1a-50bf-afcb-8e3d5bbd72e9 | button | Run full dishwashing cycle and inspect for faults. | Yes,No
| checkpoint | Cooktop installed and power plugged in.
54ac773c-71f8-59cd-a4ed-3cf152119898 | button | Once gas is on, purge gas safely and ignite cooktop for its operation. Confirm yes once complete. | Yes,No
c5de9cb7-bc02-552f-98e9-898c583ba833 | textbox | Hot water delivery to kitchen sink.
| checkpoint | Laundry tub and mixer installed?
d70ca29a-412d-5ed3-befe-0bfb5d0230c6 | note | Tub door to swing the correct way.
997a7448-28e0-51b4-a292-d5e6161163de | button | Clean aerator, Remove Trap & Clean Out (Tighten Trap) & Test Floor Waste - Clean Out | Yes,No
ccfb06b1-03ce-5f17-9256-9e4a0087fd4f | button | Laundry mixer solid, check for cross connection, run tap, tighten flexi & trap and check mini cock and trap for leaks. | Yes,No
0ac0453b-ec55-5c3a-a054-e987abbda806 | button | A/C Tundish(Cap if there is no Tundish by AC). Ensure 25mm air gap achieved. | Yes,No
be45a28f-09a9-52dc-b796-73f29f48421d | button | Washing Machine taps Installed Under Tub/Opp Tub, cover plates installed and AAV installed if applicable. | Yes,No
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
8c6ad8ff-9044-5c82-af71-4823bf900ec2 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed. (photo)
a6e33fb0-a148-572a-b4f5-17eb6e8d2443 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
b4fcc54f-4bf0-5f9d-a6ba-c6885ab459eb | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
4ea2c75b-82ea-58a1-9f44-ba45dd74a72b | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
64f113d8-f2e1-548a-942f-7ba6db24a894 | textbox | Hot water delivery to Shower.
| checkpoint | Bath installed, Cement grouted in, fill tested and water tested for any pipe or plug and waste leaks.
| checkpoint | Bath mixer cover plate/handle and bath spout installed.
89ec63a3-4a1f-5b86-b74d-be349033f7e3 | button | Bath fill test and water run test, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Balcony drains clear, overflows in place?
| checkpoint | Balcony gas bayonet and or water taps installed as per AS5601 and AS3500. Test for leaks and operation.
| checkpoint | Gas valves tagged, CW meter installed and tagged, Hw meter installed and tagged and NPCW installed if applicable.
| checkpoint | Gas Tested with Manometer - on hold for 10 minutes. Ensure absolutely no leaks!
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
4ee2716d-1ff5-5be3-9432-9485e3e52804 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
a97ffd50-5bf5-575a-b9e2-c4db4d5dd3eb | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
d7f2ac25-f5ea-50ba-bff4-cb1f5640927b | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Car Park Finalisation |  | Car Park Finalisation | 19608214-7c8e-4704-9101-bd9cdf5b97d7
| checkpoint | Bracketing completed as per AS3500
| checkpoint | Pipe jetting and CCTV completed
| checkpoint | All RWO or CPO grates installed and secured.
| checkpoint | Fire doc finalised and submitted
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Cleaners Rooms |  | Cleaners Rooms | 08716c6c-55d3-4393-8ec4-c173001b02f5
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
d9c24efb-4b21-5f83-a17a-2f640e0b86f7 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
38569804-21eb-5c1a-b611-5021e2dac22a | button | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap or floor wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap or floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | Fit out of cleaners room hydraulic PC items
d2dd02f5-fa4f-57d7-9e8a-eabdc7677642 | button | Commision PC items and set Temp valve to 49 degrees | Yes,No
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Cold Water Pressure Pump |  | Cold Water Pressure Pump | 671276b1-a9a8-42d7-9422-3458a23ae389
| checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth Poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have electrical wired up
| checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
a4e894e7-a47f-54f1-9db0-c2233736d193 | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Commercial Tenancy |  | Commercial Tenancy | 0ffb4159-1166-4ba5-8d5a-89140da38ab4
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
96d2cf38-1583-519a-8da8-f89c0da6b673 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
f57818d2-e54f-5cee-9d9f-ee60de6612d0 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
2e52335e-e919-58cc-8eb4-2dcb127c0788 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Kitchen mixer and sink installation complete.
23331d31-f806-5419-b101-7af531d2c366 | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes,No
9ded845c-44c0-564a-9ca0-d3c9265361cf | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Tundish point installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
6c4495c3-13a5-58db-8b1d-4a70b97c54ad | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
52b5a3c9-d6ed-5b63-80f1-29da43017088 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
cb1f1bf0-95ee-5757-8039-6fd5d7258046 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Disabled bathroom Rough Ins |  | Common Disabled bathroom Rough Ins | 57f73e68-5d9b-4a3d-b6db-3819b7535388
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
c274cec3-e405-5427-93e1-9af6b6db5d63 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
d67b51cf-bbfc-5509-85d2-6011e1d2eca1 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
a8548dcc-c2da-5159-aefe-ddb0fbf587a3 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
4cfcaae0-a094-5a0d-8c2d-1d5d5c9ab69c | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
63bfda1a-5b6e-5034-8acd-32775c6c418f | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
3466a483-16d1-5c0f-ba60-1c84da34896f | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
094a0606-5eae-5ec2-ae70-d6b20f408215 | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
bbba9a3a-1f94-5ae2-b389-7beef01380a8 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
e28ec742-3208-5200-bade-d6868acc53a0 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
c3f61c1f-a564-5b7a-89c3-b458cdeb2d34 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Female Bathroom Rough In |  | Common Female Bathroom Rough In | cbe12ed4-254d-4e47-b5d3-298a6e06d019
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
67f9bade-9fa1-56c8-9ba7-ee790ba4f15b | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
66034249-741e-5b11-8e67-5e93de6adeca | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
13af7e1b-b459-5439-affd-5f52b1521a35 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
e8610e30-49b6-5bd5-a043-43ef39dcc221 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
c55ba983-0194-5fe9-90df-996ae0a50e47 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
018a1a75-8944-540c-91d5-901b7558325b | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
5357dc7b-d924-5ee7-860c-148aef44967c | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
4255a2d7-2a0e-5462-9d2c-54d5ae78c2e0 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
46a0cd8f-49c7-5c27-ba98-d1ac54d24634 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
5ba5818c-76af-5bd1-b41b-71199246282f | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Male Bathroom Rough In |  | Common Male Bathroom Rough In | f278736b-1d25-4aee-a38d-8730d5ac7262
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
786b4206-c87b-5657-9ee5-33c36e2f0c8f | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
b5c9c15f-4392-5d46-ba85-c8fe21dcbe63 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
d95696ed-5e73-5fe1-bc53-1c67eb4d0f35 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
8cf39be4-4cbd-5a62-b036-c6e2bacae7ed | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
08784e3c-4c6e-5fb3-ad10-d9a4eb531e12 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
81031148-c44f-5562-9ac2-4633190b52b3 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
e28233ee-8924-5847-926f-f1b378f5d826 | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Urinals installed and connected to solenoid and waste.
2c5893d5-cc45-5983-9439-c3249c258dd4 | button | Flush Urinal 3 Times (check that sensor is working fine). | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
60c1b4bf-dfba-5d32-8bac-b386a837b38d | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
c6effbad-e489-52c1-af55-cb72b3af8525 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
591405a0-de09-5daf-9319-79dcb957513c | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Concrete Pour Checklist (Apartment and hotel floors) |  | Concrete Pour Checklist (Apartment and hotel floors) | e62cf62c-89fa-47de-8fe9-c9ab4b25ba26
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure & drainage services complete & Installed at correct Invert levels.
| checkpoint | Downpipes with columns installed & capped off.
| checkpoint | Correct fire collars installed with test reports on file.
9caff468-0806-5a3f-82d4-60f717e60b82 | note | Integrity and insulation hour rating to meet slab FRL.
| checkpoint | All hydraulic service penetrations points installed.
b684ee6a-7828-5f2d-9d8e-87932f20e167 | note | Cast in services installed at correct grades (as per AS3500) & locations.
| checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in.
b03ee4c7-2ad5-5859-9a9e-58d3c36696d2 | note | Photograph inspection booking.
| checkpoint | Balcony, Bathroom, Kitchen & Laundry Layouts Checked.
| checkpoint | Puddle flanges installed for floor wastes and balcony drains at minimum concrete height stated on structural drawings.
7244c977-cf92-5edd-b93e-ffc12a3e08ac | note | Car Park Drains Checked.
f70dc3b4-c486-5cf9-8dcf-4c90721e2b74 | note | Correct grates, Planter box drains or RWO installed.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Top up water on the morning prior concrete Pour for major casting.
| checkpoint | Cold water, Hot water and gas service conduits installed from lobby to apartment/hotel.
05bb1588-9660-5acc-9d9d-8372de92be9a | button | Cold water, Hot water and gas service conduits loops to balconies and kitchen islands installed. | Yes,No
| checkpoint | Pictures of works completed.
972ee23e-7671-5f3d-b6d7-5427ebb03f57 | textbox | Concrete Pour date:
8cb2079f-a356-580c-968a-62066b1fbbd1 | note | All Penetration Work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | DDCV for Fire supply |  | DDCV for Fire supply | e9a9909a-2064-4da5-894e-b39dbc2bf7bf
| checkpoint | DDCV installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | DDCV valve installed as per AS3500. For fire supply.
40f4379c-a92f-56b1-91cc-fa661f0a6b63 | button | DDCV drain installed and tested. | Yes,No
8b5b5c38-baab-518f-b851-92559e474d24 | note | Please attach photo of serial number and valve.
| checklist | Fire Hydrant/Sprinkler Pump Room & Tank |  | Fire Hydrant/Sprinkler Pump Room & Tank | c5e9d102-3486-4318-aab0-91fc763b52ee
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Cold water services installed correctly as per workshop drawings
| checkpoint | Rainwater reuse service s installed correctly as per workshop drawings.
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Supply & install tank top up supply with correct float valve.
| checkpoint | Wastes to be in correct locations
| checkpoint | Floor wastes installed
| checkpoint | Clear out debris from floor wastes
| checkpoint | Tundish points installed as required
| checkpoint | Water services pressure tested @ 1500KPA or 1.5 x working pressure
a97812c3-c59f-5cda-819a-c501677f8380 | note | Whichever is higher for a minimum duration of 60 minutes
| checkpoint | Coordination with walls and other services overviewed and coordinated onsite.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Garbage Room Work |  | Garbage Room Work | 8bed1db3-e4fe-49c2-b896-a40a33704637
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
c30c978f-a102-526e-a326-eecdcca8d822 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
3c44be9b-fc3c-52f2-85b5-7af18e7a401b | button | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | RPZD valve installed as per AS3500.
405f70cb-0812-5501-979d-66248471e1b7 | button | RPZD drain installed and tested. | Yes,No
faf74fb6-7b74-5da7-b20f-415f20b9dd99 | note | Please attach photo of serial number and valve.
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Gas Connection |  | Gas Connection | 253425e1-1d42-45e8-9c9b-8b387a449c5c
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per Jemena requirements (attach photos if necessary)
| checklist | Gas Meter |  | Gas Meter | a6d2e1d8-8d0e-4208-87ef-5fe0825c3e68
| checkpoint | Arrange gas inspector for inspection and requirements.
| checkpoint | Gas reg to be installed on plinth if external. Install as per Jemena requirements.
| checkpoint | Run breather vents off regulators if installed internally. Pipe size usually 25mm
| checkpoint | Ensure the Gas reg is installed in correct orientation.
| checkpoint | Labelling - 1050kpa, 210kpa and or 5 Kpa
| checkpoint | Test all pipework and joints for leaks.
| checkpoint | Reg test point to be facing in a direction where accessible.
| checkpoint | Union or flange connection with valves so that reg can be removed or serviced.
| checkpoint | Take photo of serial number and gas meter.
| checkpoint | Arrange gas inspector for inspection.
d64f3d4f-45db-540d-84bb-dd2fdfb8e437 | note | All works completed to specification/drawings, Jemena standards & Area left clean/tidy
| checklist | Grease Tank |  | Grease Tank | 26f81da3-71e6-490f-9052-8ad596ba788a
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Grease tank installed in correct orientation (inlet/outlet)
| checkpoint | 100mm Chamber vent to atmosphere.
| checkpoint | Trade waste inlet connection.
| checkpoint | Accessibility around tank minimum 600mm.
| checkpoint | Platform installed within room.
| checkpoint | Suction line within room installed. 80mm minimum line, storz adapter and shut off valve.
| checkpoint | I.O's installed inlet and outlet.
| checkpoint | Ensure lids are closed off properly.
| checkpoint | Take photo of serial number and tank.
| checkpoint | RPZD valve installed as per AS3500.
a99b0d9c-9038-5742-8ee3-f78fb0d62d23 | button | RPZD drain installed & tested. | Yes,No
d7730cb9-f9e8-567c-a5d8-d3f7c5eb067f | note | Please attach photo of serial number and valve.
| checkpoint | Arrange trade waste inspection if required.
ae3d3df1-9b69-5ec0-90f6-320b0d587ee4 | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Hot water flush for trade waste |  | Hot water flush for trade waste | e10a43d0-6eef-491d-ab45-d594cfca13de
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Drainage installed as per AS3500
3f28360a-c9de-502a-90b7-f4225b2acd4e | button | Hot water flush installed and commissioned | Yes,No
| checkpoint | 25mm air gap to avoid cross contamination
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Hot Water Plant & Return Pumps |  | Hot Water Plant & Return Pumps | def53ea5-ad50-4077-99d3-3a37c76da32f
| section | Hot water plant
| checkpoint | Installation – refer to installation checklist for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Flue installed as per manufacturer's specification.
0a5c4545-0817-52f4-8be1-c58919c830ae | button | Power flue turned on. | Yes,No
| checkpoint | Temp relief points ran to tundishes.
| checkpoint | Temperature probe from control box installed into storage tanks.
| checkpoint | Check that an adequate water supply is available to the hot water system.
| checkpoint | Water supply pressure shall not exceed the maximum pressure stated by manufacturer.
| checkpoint | Open cold water inlet valve, hot water outlet valve
| checkpoint | Exercise all valves and ensure correct operation. Ensure all valves are in open position prior turning power on.
| checkpoint | Check the system is fully charged & all air is bled from the system & no leaks are evident
| checkpoint | Ensure hot water heaters and storage tanks are full of water and all valves are open.
| checkpoint | Ensure pressures are not greater than 750Kpa to the heaters or storage tanks.
| checkpoint | Open all individual gas isolation valves & purge gas lines.
| checkpoint | Test gas pipe work for leaks.
| checkpoint | Check the gas supply pressure at the inlet to the water heater with the water heater and all
| checkpoint | range is NG: 1.13Kpa - 3.5Kpa & LPG: 2.75Kpa - 3.5Kpa
66ed7f2d-ca15-51d5-804d-43b119e9390f | button | Clean filters and strainers once after 4 hours of use. | Yes,No
| checkpoint | Set temperature to 65 degrees.
| section | Hot Water Return Pumps
| checkpoint | Hot Water Return Pumps - Installation – refer to installation checklist for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Ensure there is water supply to the pumps.
| checkpoint | Clean filters and strainers once after 4 hours of use.
| checkpoint | Turn on power to the pumps. Set the pumps to alternate.
| checkpoint | Purge pumps of air. Ensure water is visible from the purging points.
| checkpoint | Set balancing valves.
| checkpoint | Inspect system for any leaks or faults.
| checklist | In-Ground Drainage Hydraulic Services ITP |  | In-Ground Drainage Hydraulic Services ITP | ba744aec-9b29-4e7a-823a-3946fd780cba
| section | Sewer/ Trade Waste
| checkpoint | Sewer drainage, Trade Waste drainage and vents installed as per workshop drawings.
1aa29d91-ae5c-5cd4-a40c-a3a1a96161cd | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
7685c4d8-942d-54e1-8a55-8f811c8f0ccf | button | Pipework risers labelled, pink primer and blue glue used only. | Yes,No
| checkpoint | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Inspection by Fair Trading for sewer drainage to be done & other inspections if required by others.
a0c25189-3ccc-5bed-876a-63cecc78879e | note | Photograph inspection booking.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
fb2caac8-c462-5234-889d-d7e027bd2ec1 | note | Ensure compaction of fill materials is to specifications & Australian Standards.
e5dae788-8d86-5641-8d48-a4aeab94f82e | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
| checkpoint | All works completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Stormwater
| checkpoint | Stormwater drainage installed as per workshop drawings.
45d5dac3-774e-52bd-8e81-73ba6e9adac8 | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
| checkpoint | Installation of pits to the correct levels.
b836265b-b074-5f4c-b334-70b4ee198a73 | button | Ensure correct grates & lids used with appropriate load ratings for locations to traffic movements. | Yes,No
b634afc4-c0a3-5dd1-9605-d03bf155adbf | button | Pits to be sparged - Made water tight to inlet & outlet pipework. | Yes,No
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | HOLD POINT - Inspections if required by relevant authorised persons .
4bfb8f6f-70af-59c8-a8d4-84413cc50609 | note | Attach inspection reports below.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
6a40c69f-10ea-550c-a86b-156b800608e0 | note | Ensure compaction of fill materials is to specifications & Australian Standards.
2323fe93-6167-5620-99a8-4f47cdc3ded2 | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
| checkpoint | All Stormwater Work completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Handover
| checkpoint | Update As Built drawing immediately - Confirm IL of pipework. Attach with ITP submission.
| checkpoint | CCTV completed pipework to ensure no defects before concrete Pour to prevent future problems.
| checkpoint | Pictures of works completed - Attached below.
24de61e2-9e05-5872-95f7-22094a03c137 | textbox | Concrete Pour date.
| checklist | Inground Pressure Services Installation. |  | Inground Pressure Services Installation. | f908581b-f4d1-4ec5-8008-2b1d4e407c92
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
d6a154a0-6ea8-505c-ac26-1c180a5ab485 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools, welding equipment & deburring machine ready for use..
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
f35b0752-d19b-5062-9356-de92918e49fb | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
c46599d4-29f7-5113-b4c9-ca5010c8b224 | button | Witness marks on all press Fittings checked. | Yes,No
| checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any.
6f3cbd3d-9f2b-5358-86cf-817d4a47c2e6 | note | Photograph inspection booking.
| checkpoint | Fire services installed correctly as per workshop drawings.
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
dec9ff40-63e7-5a48-a0ef-918d95b3f783 | note | Ensure trace tape is installed
ec60e6dd-9f0a-5c30-a696-ab9993af975f | note | Ensure compaction of fill materials is to specifications & Australian Standards.
a9fa5df7-7c09-58c9-b86a-710f2b981c04 | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
a0575f1c-1233-57e1-bdca-098f716eab0e | note | All services left under pressure during construction.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Managers Office Work - Bathroom |  | Managers Office Work - Bathroom | 582d08f1-b6bb-4020-8152-2a7bb22b9edc
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
cd7d5eba-46a6-5820-806e-71de07d24a43 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
deb8e3b8-9bec-53c2-a982-1d10bc9f8497 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
da2c3649-1597-5d8f-8c0c-db051b707aa8 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
5b0b4bfc-8e54-5384-b915-d3f4eaf72440 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
02f4261a-f1d9-55bc-bfdd-98ee164170ef | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
d967abae-8538-5daa-b82e-24d0ca9b79e6 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
127abfa7-8669-564e-a0bf-fbe4d40dd93b | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
32c9a7b1-919a-5c28-a242-a31863653c76 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
d606b9eb-aaf3-5dff-aa3d-8fafb0f2ce1a | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
02a85870-a59d-55f7-bcb1-8911f547de9c | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Oil Separator Install |  | Oil Separator Install | 4169f673-25bb-43af-81f1-0f438270f2a0
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set. Tank to be a minimum 1500mm away from pump.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | Oil Separator installed in correct orientation (inlet/outlet).
| checkpoint | Ensure all items including oil drum are with oil Separator
| checkpoint | Ensure all venting requirements are met
| checkpoint | Take photo of serial number and tank.
9b09e4b2-7829-5854-82d7-58acc828b2b8 | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Parents Room Rough In |  | Parents Room Rough In | 8dc81f66-be12-4ed5-b55b-88dd984ea905
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
57d2934f-6637-544a-9058-a32421b8ecaa | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
e1a2f217-3583-5a99-9b78-76da9eab29e2 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
a75535cf-09ab-5aad-8316-c8e57c0c0e0f | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
e741066e-e2f9-536c-b4f2-834da4b4fb17 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
92d11fad-3e55-5933-8e53-cc18e7a21632 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
371bedcf-3aa2-5e35-90af-fd7cbdb82be1 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
ea51906c-65a0-5579-8c9d-c9039c36ef89 | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
c6005d4a-1d8b-5f43-b778-ab600390129a | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
e010af72-71a5-5df2-b69b-116277ac67df | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
74cd382a-7d52-5eb6-9004-7c0ef50a2228 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Pressure Services Installation |  | Pressure Services Installation | 95287f35-8b52-4d8f-99c5-a4b8355b0bb7
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
c5faeb36-a89c-5cf4-9238-18e663f11633 | note | Check scope of works/specification & ensure all documents are current.
964bdb00-960f-543e-b713-53d7375bba76 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
64331c84-b7e9-5b0a-994a-8827d33dd572 | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
d812db5c-7ad0-577b-b5b3-0c67c3e1dacb | button | Witness marks on all press Fittings checked. | Yes,No
| checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any.
91956798-2a2b-5bf5-83db-61c7694aedd2 | note | Photograph inspection booking.
| checkpoint | Fire services installed correctly as per workshop drawings.
854e5378-c43a-5ae2-ae2b-cb937af8c394 | button | Gal pipe grooves checked with a groove tape. | Yes,No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
a1aef1d8-00b9-5233-b195-b64048fbae28 | button | Pipe spacers installed to avoid electrofusion. | Yes,No
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
038bdd69-a080-5c00-b6f4-b75b57901e0a | note | All services left under pressure during construction.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
ba0dc927-f821-53ba-9703-e72e6835b5c9 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards and tested.
| checkpoint | Fire hose reel tagged.
| checkpoint | RPZD valve installed as per AS3500.
3ad7b086-4435-5664-8f73-1fc02e43668c | button | RPZD drain installed & tested. | Yes,No
8d20492c-7281-5905-95cf-585496c15cd1 | note | Please attach photo of serial number and valve.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Pressure services on apartments/ Hotel or commercial floors. |  | Pressure services on apartments/ Hotel or commercial floors. | af9fcece-3430-47d5-bc9b-7300bb6fe3aa
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
8b6089ac-6a29-50c2-af9a-39dedf5a5d14 | note | Check scope of works/specification & ensure all documents are current.
b1001395-2aa1-55e6-b954-9b6499eb1c72 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
72e5f4e6-a33a-57fd-8c24-967e567bf361 | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
338e6a00-f038-56c8-89af-47cb613fe772 | button | Witness marks on all press Fittings checked. | Yes,No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
3f628478-6ffc-5e94-9eac-c78602ca0ac5 | button | Pipe spacers installed to avoid electrofusion. | Yes,No
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
afc0f9c5-91d0-5103-b165-9708f25eba86 | note | All services left under pressure during construction.
| checkpoint | Isolation lever shut off valves and PRV,s installed.
ccf900ba-4513-57b6-a133-9cff4bbb9ad7 | button | Tempering valve or Thermostatic mixing valve installed in the correct orientation. | Yes,No
aef01340-548f-57dd-ae5a-381df4a79bdc | button | Cold water, Hot water and or meter bars installed and labelled. | Yes,No
b24a2d66-f8f1-539d-bdfa-c35241355661 | button | Connection of all reticulated cold, hot, Gas & NPCW PEX pipes to points of connections from manifold setups. | Yes,No
| checkpoint | Floor waste grate installed.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
f01f68e8-1035-59e6-ad32-34184e47fb94 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE).
| checkpoint | Garbage Chute RPZD installed and tested. (IF APPLICABLE).
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary).
| checklist | Project finalisation |  | Project finalisation | 546f4ce3-39f3-4801-811d-bfd6246d2813
| checkpoint | CCTV completed throughout
| checkpoint | Fire doc finalised and submitted
| checkpoint | SSD produced by designer.
| checkpoint | As Builts completed and issued to builder.
| checkpoint | O&M manual completed and sent to builder.
| checkpoint | RPZ test completed and issued to Sydney water.
| checkpoint | DDCV test completed and issued to Sydney water.
| checkpoint | TMV's tested throughout.
| checkpoint | Gas final inspection completed and certificates sent.
| checkpoint | Certification of everything required issued to builder.
| checkpoint | Trade waste final inspection and certified.
| checkpoint | Maintenance manual created and locked in.
| checkpoint | FHR flow test completed and issued.
| checklist | Rainwater Pressure Pump and filtration |  | Rainwater Pressure Pump and filtration | ededd51c-152e-4268-aa87-8134cf55bb89
| checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth Poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have electrical wired up
| checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
2a46ecb3-5266-51e5-a858-bfb755bfda60 | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Roof work |  | Roof work | b4457e7b-94eb-4810-b932-d273b45973ba
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
597f2e6f-15e9-5cbb-9f9e-1ceaf96cfee8 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Builder has overflows installed.
| checkpoint | Sewer vents terminated as per AS3500.
d5ef65dd-999a-5d3e-aa3a-ad594e613007 | button | CCTV of sewer completed | Yes,No
| checkpoint | RWO cleared of debri and CCTV completed.
| checkpoint | RWO grates installed and secured.
0eb5203d-0ad9-5e50-96d6-408c97d896b9 | note | Ensure protection screen installed so no pebbles block drains
| checkpoint | Pressure services installed.
| checkpoint | Provisions for other services installed. (IF APPLICABLE)
| checkpoint | UV thermal lagging installed.
| checkpoint | All hydraulic works completed to specification/drawings & Area left clean/tidy.
798a1f05-5690-595b-8779-7ae024441e2f | note | Pictures of works completed if applicable.
| checklist | Set out and Penetration installation (Retail, Commercial and car park areas) |  | Set out and Penetration installation (Retail, Commercial and car park areas) | e0bcba33-f324-40f6-aac1-8697686d4ddb
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure and drainage services complete? Installed at correct Invert levels?
| checkpoint | Downpipes with columns installed and capped off with DWV caps ONLY.
| checkpoint | Sewer, stormwater and pressure penetration points installed. Check off Hydraulic plans.
| checkpoint | Cast in services installed at correct grades (as per AS3500) and locations. Check off Hydraulic plans.
| checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in.
99072599-a60f-5743-83ff-17d97baaf161 | note | Photograph inspection booking.
| checkpoint | Correct fire collars installed with test reports on file.
3f4a9403-8d56-5618-94e3-d27e3cc2ab5b | note | Hour rating to meet slab FRL.
| checkpoint | Puddle flanges installed for floor wastes and balconies at minimum concrete height stated on structural drawings.
| checkpoint | Car park drains,RWO's , trench drains and risers installed. Trafficable grates to be class D only.
b55d434e-3a64-593e-bdcb-65c7c143639d | note | Correct grade of drain to be installed.
| checkpoint | Miscellaneous penetrations installed.
| checkpoint | All pipe risers to be protected with pipe caps and or duck tape.
| checkpoint | Top up water on the morning prior concrete Pour for major casting.
| checkpoint | Pictures of works completed.
bb5dcae1-dbc1-57ac-8cad-ab46c5f9c891 | textbox | Concrete Pour date:
ff2e9b6e-08f3-5fa8-8ed3-d95aa290990f | note | All Penetration Work completed to specification/drawings & Area left clean/tidy.
| checklist | Sewer Connection |  | Sewer Connection | a8d307a0-2934-4941-a7ef-c23d6d8b0389
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Fair trading inspection complete.
| checklist | Sewer Pump Station |  | Sewer Pump Station | c784a3a4-ee67-49b5-b0eb-b69d53b53157
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Storm Water Pump Station |  | Storm Water Pump Station | 0c6d2fea-0ea9-4b86-93da-65e30267b7b6
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Stormwater Connection |  | Stormwater Connection | d3a5a7bc-9c85-4e0e-8f75-5f38b752488c
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Council inspection complete.
| checklist | Tenancy Works |  | Tenancy Works | 20604654-9a14-41a2-a7e9-9ec11bffaaaf
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
| checkpoint | Sewer and trade waste Provisions installed in correct locations and capped off.
| checkpoint | Vent provisions and AAVS installed as per documentation and AS3500.
| checkpoint | Cold Water Gas Point Provision Installed in correct locations and capped off.
7f107e78-32ae-5f8c-ac4d-ed6ee34e66ac | button | Sydney water meter installed if applicable. | Yes,No
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE)
| checkpoint | CCTV all lines to ensure clear
| checklist | Variation |  | Variation | 30ded137-0f01-4bd6-867a-22a4a6bbdb58
| checkpoint | Variation Details Approved
41e427d6-3834-5dc3-b296-18f719069a35 | textbox | Reference/Drawing/Instruction Number
5073f23f-c7c4-5064-a7ac-4bb4da9fb32f | textbox | Variation Area
2fca923f-7e60-566d-b666-49d5b84bd011 | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
| checkpoint | Variation Completed
| checklist | Water Connection |  | Water Connection | af438cae-80e1-4607-9770-cec75fd6f271
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checklist | Water Meter Install & RPZD |  | Water Meter Install & RPZD | 49ef5dc3-0705-47f3-97f7-115afaf61c63
| checkpoint | Water meter installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | Take photos of device & ensure to get all serial numbers
| checkpoint | Test & commission device as required by certified persons
| checkpoint | RPZD valve installed as per AS3500.
e951fc4e-b6b4-584a-aa77-f3c31d6447cd | button | RPZD drain installed & tested. | Yes,No
84bf299c-81d4-56d0-b804-4e47025f801b | note | Please attach photo of serial number and valve.
| checklist | Water Storage Tank |  | Water Storage Tank | 29eb3676-7e11-42d9-999d-c0ea64a02a0c
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Slab or plinth Poured and waterproofed.
| checkpoint | Tank installers to install tank only.
eebfeade-ebf8-5083-8d60-2abd3f8d8133 | button | Tank supplier issues certificates and authorisation to fill tank. | Yes,No
| checkpoint | All valves, overflows , tank top up and sludge drains installed to tank.
| checkpoint | Fill tank up in 500mm increments. Inspect tank for any leaks and continue till you reach desired level design.
| checkpoint | Dump tank and ensure sludge drain and pipe work is operational.
| checkpoint | Set float valve as per manufacturer's specification.
| checkpoint | Once tank is commissioned book in Chlorination by tank supplier.
| checkpoint | Tank level indicator installed and connected to BMS
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)