## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Add Variation |  | Variation | ab13edfa-6a41-4ee6-982f-f3d0897ec675
| checkpoint | Variation Details Approved
7d5a8792-1e40-59d4-949d-e63ed9050cab | textbox | Reference/Drawing/Instruction Number
8bd69c1f-9bcc-5193-b665-9d72b6458023 | textbox | Variation Area
335776a9-4696-570e-816e-af5985671159 | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
| checkpoint | Variation Completed
| checklist | Aerial Drainage |  | Aerial Drainage | fde3f832-6373-4aec-81bb-b6986ca07f80
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
0937c3ca-bc0c-5466-a87c-5eb5cba913b3 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Fire collars cleared of concrete slurry & replaced if damaged.
| checkpoint | Sewer, Stormwater, Trade Waste and vent services installed correctly as per workshop drawings and schematics.
f6f4040b-f37b-5482-b2ea-965343976bdd | tickbox | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
168f968c-2f24-5248-bf79-aba36821af61 | tickbox | Check for cross connections. | Yes,No
d15b8837-8375-5e4f-9a1e-ce9f8eeea8d7 | note | Pink primer and Blue glue used only on UPVC.
| checkpoint | Syphonics installed as per manufacturer's recommendation
aad33f29-04ef-5a30-bf9e-b8238e16b7fb | tickbox | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults. | Yes,No
| checkpoint | Hydrostatic test filled with water to a height not less than 1m above sofFit level of highest pipe for a minimum of 30 min.
| checkpoint | RetroFit fire collars installed.
c664354e-3f57-58a4-9abb-521f8e430ec9 | tickbox | Fire penetration stickers installed and photographed. High top collars to be smoke sealed. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Acoustic lagging as per project requirements.
| checkpoint | All points capped off to ensure no builders debri enters system.
889ecd49-98b8-5a6b-97de-4e54c680723e | tickbox | Floor waste protected with sponge. | Yes,No
| checklist | Apartment / Hotel |  | Apartment / Hotel | 7a562442-9518-407a-bd17-6638145906a4
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
0c7a7ed1-fc45-5efd-8e59-7756879cb13d | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Balcony gas bayonet or water taps installed as per AS5601 and AS3500. Check foothold requirements
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cistern installed and tested. Ensure cistern is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
c5ba32b4-d0d7-5839-998e-7359fe89bf77 | tickbox | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
a64419a3-1569-521a-b18f-58417233d767 | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy
| section | Apartment Fit Off & Commissioning
| checkpoint | Bathroom, Kitchen and Laundry set out off current Architectural drawings.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED, Laundry,bathroom, ensuite and balcony.
| checkpoint | Kitchen mixer and sink installation complete.
81a8353f-64ff-507c-9851-07283d78a917 | tickbox | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexi & trap and check mini cock for leaks. | Yes,No
8dab68ad-0037-5888-be7c-2dafcf2547d3 | tickbox | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Dishwasher installed with hoses, Power lead not kinked and dishwasher plum. (cover plate for hoses must be installed)
36b6d392-bcfc-5353-a991-d5873899c0d2 | tickbox | Run full dishwashing cycle and inspect for faults. | Yes,No
| checkpoint | Cooktop installed and power plugged in.
739632e9-9e85-57e3-a56a-d642e2834751 | tickbox | Once gas is on, purge gas safely and ignite cooktop for its operation. Confirm yes once complete. | Yes,No
32a79c92-17e5-5c4a-bfe1-40f88a306151 | textbox | Hot water delivery to kitchen sink.
| checkpoint | Laundry tub and mixer installed?
aa6cc385-cf84-5225-adbb-9bd634410094 | note | Tub door to swing the correct way.
2fda3521-169d-5e27-8b3c-84c072b2237f | tickbox | Clean aerator, Remove Trap & Clean Out (Tighten Trap) & Test Floor Waste - Clean Out | Yes,No
5f03836f-5869-5761-bd86-417056f925db | tickbox | Laundry mixer solid, check for cross connection, run tap, tighten flexi & trap and check mini cock and trap for leaks. | Yes,No
c4385f50-363b-5a3e-a811-1972d93949d3 | tickbox | A/C Tundish(Cap if there is no Tundish by AC). Ensure 25mm air gap achieved. | Yes,No
dbce529b-7798-50d1-84a9-b3a2f9f718fa | tickbox | Washing Machine taps Installed Under Tub/Opp Tub, cover plates installed and AAV installed if applicable. | Yes,No
| checkpoint | Toilet, Toilet seat's, Cistern and flush bool installed and water tested.
5ed103c1-5802-51dc-94da-a1d596cc55d6 | tickbox | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and bool operation. | Yes,No
| checkpoint | Basin mixer and basin installed. (photo)
72f34269-79d7-507c-9d8a-de5c30496e8b | tickbox | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
41364023-fe7b-53a0-b2bb-ffe36c142332 | tickbox | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
45af4f02-ded5-5af8-9437-75e07378debd | tickbox | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
c731baa9-cf7f-5fec-880d-163ca1564692 | textbox | Hot water delivery to Shower.
| checkpoint | Bath installed, Cement grouted in, fill tested and water tested for any pipe or plug and waste leaks.
| checkpoint | Bath mixer cover plate/handle and bath spout installed.
408712dc-6671-5e17-b17a-035e9c51bd0d | tickbox | Bath fill test and water run test, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Balcony drains clear, overflows in place?
| checkpoint | Balcony gas bayonet and or water taps installed as per AS5601 and AS3500. Test for leaks and operation.
| checkpoint | Gas valves tagged, CW meter installed and tagged, Hw meter installed and tagged and NPCW installed if applicable.
| checkpoint | Gas Tested with Manometer - on hold for 10 minutes. Ensure absolutely no leaks!
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
c7e49d50-b470-5c11-9baa-837184dcfed3 | tickbox | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
fd7a473c-14c5-555f-a8fc-f041499d4abe | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
711cd0f1-8c4e-595c-b838-6a8467a53338 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Car Park Finalisation |  | Car Park Finalisation | babb84bb-b1d2-4366-abb1-9b0af9e712c4
| checkpoint | Bracketing completed as per AS3500
| checkpoint | Pipe jetting and CCTV completed
| checkpoint | All RWO or CPO grates installed and secured.
| checkpoint | Fire doc finalised and submitted
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Cleaners Rooms |  | Cleaners Rooms | 0e3f34ce-b697-4f0a-8a8d-a7d149d619aa
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
b849690d-55da-50d8-8021-db2560e5a859 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
10f73927-e1dd-5a55-8ca5-684f92a03e88 | tickbox | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap or floor wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap or floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | Fit out of cleaners room hydraulic PC items
60b26ae0-cd86-5344-be3f-acd09ff89388 | tickbox | Commision PC items and set Temp valve to 49 degrees | Yes,No
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Cold Water Pressure Pump |  | Cold Water Pressure Pump | 8bae26e2-97f4-4459-9062-a51e3a39fe0f
| checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth Poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have electrical wired up
| checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
fb268a0f-b368-50cb-a24d-2aaaf11f2394 | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Commercial Tenancy |  | Commercial Tenancy | fc908413-d93e-490c-a49a-10c5338c12bf
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
008d61aa-9062-5402-8bca-c3e61b3733bf | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
2cbf8a9f-6b0e-5cf7-b449-08cdaf946f4f | tickbox | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
acae1483-e810-5f6c-b60a-d83e3694dfff | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Kitchen mixer and sink installation complete.
6c1f93ad-55a2-5d76-aab1-3a1274eab461 | tickbox | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes,No
a092befa-6609-5af4-8aec-be521550d273 | tickbox | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Tundish point installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
3072b5d1-8d17-56d3-a557-491ae351c9a8 | tickbox | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
b4a9dcb1-9624-5d14-8c29-a8c8d11250a5 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
90d698c4-2335-51d7-a755-5d000cbee4f5 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Disabled bathroom Rough Ins |  | Common Disabled bathroom Rough Ins | b7855bc9-baa2-42a3-98a7-3ccf688bc796
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
236d61ee-df85-5119-b315-f70fad935040 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
4a85f546-e6f1-50f9-a4ae-dbc200563f18 | tickbox | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
64ba0f01-8570-5299-b984-a0152c0b3845 | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush bool installed and water tested.
267b99b1-b8dd-5fc2-a309-a918ac06be83 | tickbox | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and bool operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
db78d8ee-a2ce-57e2-9b19-dd756f552ca2 | tickbox | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
27d4caab-ab19-5d18-b671-0a0378d51808 | tickbox | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
6b16b3b3-aa07-5410-80f0-e9a456afa092 | tickbox | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
1065798a-e7b9-55ea-90d8-5a1620b4e202 | tickbox | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
b22d469b-4fb0-5197-ac48-e2378b7b788c | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
9ebf4bd5-8eaf-5cd4-9f8f-328cecfa4f33 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Female Bathroom Rough In |  | Common Female Bathroom Rough In | d792b0c5-d0b2-4ca7-8b50-491ee4433455
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
51ce1de5-8845-5734-a74d-00195d11269c | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
08119166-42d8-5dc1-bb15-3b2c12c97ab9 | tickbox | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
b04ab8dc-35d0-5679-a725-9894bf85d7a2 | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush bool installed and water tested.
78b420ae-dfb8-5a67-bd59-96513c28e4dc | tickbox | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and bool operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
f5176553-b969-5a66-9d67-70e08df90fff | tickbox | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
eb5b1e60-0434-5950-9640-fff7d6cb2913 | tickbox | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
38866226-6e9a-5ecc-803c-015023752efb | tickbox | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
6a2610d5-3331-5e98-9cf7-e3b00dea4d66 | tickbox | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
091b411a-7e18-5643-9ee7-77585719b757 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
fb1c346b-82c1-5341-8a37-430b0a01cfd1 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Male Bathroom Rough In |  | Common Male Bathroom Rough In | 2ef6131c-7f17-40e3-a8d7-b3f49f22af47
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
aa07251a-a623-5aec-ac12-8c06b9faba1a | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
49ebd02b-249c-5f52-b5bf-bfbc2347684c | tickbox | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
06641d25-5d25-58ab-ada7-871e2a9a4396 | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush bool installed and water tested.
248f37a4-9917-57d0-bb0a-b39583a4f761 | tickbox | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and bool operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
fffa2f6a-e830-5f5b-9c62-8f93edd25fdc | tickbox | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
8144b871-b714-58ac-bca8-cd76319c3eb3 | tickbox | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
c0af71e0-c4d3-5808-ac39-5992c657fde2 | tickbox | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Urinals installed and connected to solenoid and waste.
f1f755cf-5d78-59fd-a684-5cc8ddfa68bb | tickbox | Flush Urinal 3 Times (check that sensor is working fine). | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
222fd9ab-da99-5efa-8056-1ee5e4c75cb7 | tickbox | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
8a594534-9a8a-5778-90d5-2ed5476908c8 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
87fd7e6c-5833-5e8c-be2d-57a3f0c18076 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Concrete Pour Checklist (Apartment and hotel floors) |  | Concrete Pour Checklist (Apartment and hotel floors) | 6188a3dc-5778-4ae3-a20a-33bc373f4d41
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure & drainage services complete & Installed at correct Invert levels.
| checkpoint | Downpipes with columns installed & capped off.
| checkpoint | Correct fire collars installed with test reports on file.
d80582b7-4399-5c0d-872d-e6a307fd6b80 | note | Integrity and insulation hour rating to meet slab FRL.
| checkpoint | All hydraulic service penetrations points installed.
| checkpoint | Balcony, Bathroom, Kitchen & Laundry Layouts Checked.
| checkpoint | Puddle flanges installed for floor wastes and balcony drains at minimum concrete height stated on structural drawings.
bef65962-f1f0-58f8-9998-b17ca8752672 | note | Car Park Drains Checked.
b835227b-1615-5da1-83d9-57bf4e2c65b2 | note | Correct grates, Planter box drains or RWO installed.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Top up water on the morning prior concrete Pour for major casting.
| checkpoint | Cold water, Hot water and gas service conduits installed from lobby to apartment/hotel.
32066a80-7c25-5a50-b59e-340de1a6b7f0 | tickbox | Cold water, Hot water and gas service conduits loops to balconies and kitchen islands installed. | Yes,No
| checklist | DDCV for Fire supply |  | DDCV for Fire supply | 9e891fde-8cbd-48fc-816e-9e6b74e376f3
| checkpoint | DDCV installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | DDCV valve installed as per AS3500. For fire supply.
be2b7230-4008-5b96-ab3f-53543aa6c201 | tickbox | DDCV drain installed and tested. | Yes,No
1c50faff-064f-552e-aafc-d40f62e3a6fd | note | Please attach photo of serial number and valve.
| checklist | Fire Hydrant/Sprinkler Pump Room & Tank |  | Fire Hydrant/Sprinkler Pump Room & Tank | 3c151d1e-9f6f-4d01-8c87-eeae523a9c79
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Cold water services installed correctly as per workshop drawings
| checkpoint | Rainwater reuse service s installed correctly as per workshop drawings.
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Supply & install tank top up supply with correct float valve.
| checkpoint | Wastes to be in correct locations
| checkpoint | Floor wastes installed
| checkpoint | Clear out debris from floor wastes
| checkpoint | Tundish points installed as required
| checkpoint | Water services pressure tested @ 1500KPA or 1.5 x working pressure
360ce166-b6ba-5248-9bf4-6eca1b2ae929 | note | Whichever is higher for a minimum duration of 60 minutes
| checkpoint | Coordination with walls and other services overviewed and coordinated onsite.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Garbage Room Work |  | Garbage Room Work | 55d9a268-27cb-4682-9cd7-27b8d14c087b
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
12d4c14a-e31e-5d65-a895-0dec8bcf6c1c | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
947d4680-5706-531e-9e45-5cfbc127e2fa | tickbox | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | RPZD valve installed as per AS3500.
6b664cd1-6f8b-5e0c-88ca-2fb892843c3d | tickbox | RPZD drain installed and tested. | Yes,No
09c97b27-b468-5588-be1a-25035713bf76 | note | Please attach photo of serial number and valve.
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Gas Connection |  | Gas Connection | 2c34efa8-4bb1-452c-9227-ae9765dfd131
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per Jemena requirements (attach photos if necessary)
| checklist | Gas Meter |  | Gas Meter | d22d691e-77d9-4658-9a1d-76e4bba526e5
| checkpoint | Arrange gas inspector for inspection and requirements.
| checkpoint | Gas reg to be installed on plinth if external. Install as per Jemena requirements.
| checkpoint | Run breather vents off regulators if installed internally. Pipe size usually 25mm
| checkpoint | Ensure the Gas reg is installed in correct orientation.
| checkpoint | Labelling - 1050kpa, 210 kpa and or 5 Kpa
| checkpoint | Test all pipework and joints for leaks.
| checkpoint | Reg test point to be facing in a direction where accessible.
| checkpoint | Union or flange connection with valves so that reg can be removed or serviced.
| checkpoint | Take photo of serial number and gas meter.
| checkpoint | Arrange gas inspector for inspection.
9ad45ee7-56dd-52c9-b64a-cd3ac4279454 | note | All works completed to specification/drawings, Jemena standards & Area left clean/tidy
| checklist | Grease Tank |  | Grease Tank | df2d3e6e-92f8-4bcb-9b65-0618d5a2e64e
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Grease tank installed in correct orientation (inlet/outlet)
| checkpoint | 100mm Chamber vent to atmosphere.
| checkpoint | Trade waste inlet connection.
| checkpoint | Accessibility around tank minimum 600mm.
| checkpoint | Platform installed within room.
| checkpoint | Suction line within room installed. 80mm minimum line, storz adapter and shut off valve.
| checkpoint | I.O's installed inlet and outlet.
| checkpoint | Ensure lids are closed off properly.
| checkpoint | Take photo of serial number and tank.
| checkpoint | RPZD valve installed as per AS3500.
ac9a870e-0a70-5a35-bf3f-7b93d257ccf8 | tickbox | RPZD drain installed & tested. | Yes,No
50fbab06-50e2-5d28-b39e-6f6dee25bb1c | note | Please attach photo of serial number and valve.
| checkpoint | Arrange trade waste inspection if required.
797dcb22-5175-571e-844f-c900b3c659f4 | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Hot water flush for trade waste |  | Hot water flush for trade waste | 9d596746-1a0f-4595-9b59-5b8ee5ec0d5c
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Drainage installed as per AS3500
36e49eb8-2ad1-5c0b-b03a-1f886a3c4d0e | tickbox | Hot water flush installed and commissioned | Yes,No
| checkpoint | 25mm air gap to void cross contamination
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Hot Water Plant & Return Pumps |  | Hot Water Plant & Return Pumps | 2db9ce68-3711-4673-9169-aa869a6c0c08
| section | Hot water plant
| checkpoint | Installation – refer to installation checklist for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Flue installed as per manufacturer's specification.
37b24651-90ea-563b-9878-5dac2a757366 | tickbox | Power flue turned on. | Yes,No
| checkpoint | Temp relief points ran to tundishes.
| checkpoint | Temperature probe from control box installed into storage tanks.
| checkpoint | Check that an adequate water supply is available to the hot water system.
| checkpoint | Water supply pressure shall not exceed the maximum pressure stated by manufacturer.
| checkpoint | Open cold water inlet valve, hot water outlet valve
| checkpoint | Exercise all valves and ensure correct operation. Ensure all valves are in open position prior turning power on.
| checkpoint | Check the system is fully charged & all air is bled from the system & no leaks are evident
| checkpoint | Ensure hot water heaters and storage tanks are full of water and all valves are open.
| checkpoint | Ensure pressures are not greater than 750 Kpa to the heaters or storage tanks.
| checkpoint | Open all individual gas isolation valves & purge gas lines.
| checkpoint | Test gas pipe work for leaks.
| checkpoint | Check the gas supply pressure at the inlet to the water heater with the water heater and all
| checkpoint | range is NG: 1.13Kpa - 3.5Kpa & LPG: 2.75Kpa - 3.5Kpa
7e7afde8-c198-51d0-ae89-248f581f460e | tickbox | Clean filters and strainers once after 4 hours of use. | Yes,No
| checkpoint | Set temperature to 65 degrees.
| section | Hot Water Return Pumps
| checkpoint | Hot Water Return Pumps - Installation – refer to installation checklist for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Ensure there is water supply to the pumps.
| checkpoint | Clean filters and strainers once after 4 hours of use.
| checkpoint | Turn on power to the pumps. Set the pumps to alternate.
| checkpoint | Purge pumps of air. Ensure water is visible from the purging points.
| checkpoint | Set balancing valves.
| checkpoint | Inspect system for any leaks or faults.
| checklist | In-Ground Drainage Hydraulic Services ITP |  | In-Ground Drainage Hydraulic Services ITP | 5e267c70-5043-4e31-938a-57122fc88df0
| section | Sewer/ Trade Waste
| checkpoint | Sewer drainage, Trade Waste drainage and vents installed as per workshop drawings.
e80eb601-2030-52f7-9fc5-8ab96cd66436 | tickbox | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
c3e4223e-df64-5708-8ea5-2f5cbaa86953 | tickbox | Pipework risers labelled, pink primer and blue glue used only. | Yes,No
| checkpoint | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
b702329a-f4a6-5168-8d2f-041aa84c55dd | note | Ensure compaction of fill materials is to specifications & Australian Standards.
03108028-966e-56e6-b472-d90cee1626d8 | tickbox | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
| checkpoint | All works completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Stormwater
| checkpoint | Stormwater drainage installed as per workshop drawings.
77b8089c-4ced-5f24-b37a-e148517abc55 | tickbox | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
| checkpoint | Installation of pits to the correct levels.
dca19bdb-10ca-57f3-9d0d-f96bfc956082 | tickbox | Ensure correct grates & lids used with appropriate load ratings for locations to traffic movements. | Yes,No
60689686-8091-58e1-bdb3-c25a89a58aa5 | tickbox | Pits to be sparged - Made water tight to inlet & outlet pipework. | Yes,No
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
d877d1e7-4ad4-5ac6-87e8-f67b18ca79d4 | note | Ensure compaction of fill materials is to specifications & Australian Standards.
e06ce686-abee-5201-b689-e8ce43f0ea41 | tickbox | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
| checkpoint | All Stormwater Work completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Handover
| checkpoint | Update As Built drawing immediately - Confirm IL of pipework. Attach with ITP submission.
| checkpoint | CCTV completed pipework to ensure no defects before concrete Pour to prevent future problems.
| checkpoint | Pictures of works completed - Attached below.
| checklist | Inground Pressure Services Installation. |  | Inground Pressure Services Installation. | 47d000ef-19da-4922-9147-7e36506596ba
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
b6e7162c-8bd2-5d3f-9011-65ffa4e03934 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools, welding equipment & deburring machine ready for use..
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
c130924f-7fe9-5887-ac44-a2f6222acaca | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
bce63e04-2656-5883-b6bf-5d3e05a04b66 | tickbox | Witness marks on all press Fittings checked. | Yes,No
a3fc668c-582f-5d64-8f36-554680ee31cf | note | Photograph inspection booking.
| checkpoint | Fire services installed correctly as per workshop drawings.
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
13d03e87-aacb-5935-818e-e3348241fa08 | note | Ensure trace tape is installed
2763f810-18b9-5486-860b-7fc6f3af1c7a | note | Ensure compaction of fill materials is to specifications & Australian Standards.
6f048718-4e58-51f9-9df9-c77f113136ec | tickbox | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
17cc539f-1f0f-5a47-9fe9-7f120dd5e92b | note | All services left under pressure during construction.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Laundry |  | Laundry | ec318b50-ae69-42c2-afb6-c8886bbd6820
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
d65c79e8-7dc6-5a67-a557-a868a90e798f | tickbox | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap or floor wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap or floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | Fit out of cleaners room hydraulic PC items
7678fb25-db2f-5c70-8a21-abe29b2b3b80 | tickbox | Commision PC items and set Temp valve to 49 degrees | Yes,No
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Managers Office Work - Bathroom |  | Managers Office Work - Bathroom | 9e59ba78-64cb-45e1-95aa-c12a318bc5ea
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
85376a13-d9e3-54c4-b6e4-822adb031b58 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
2f01451b-544c-544c-80bf-55a2a72bb663 | tickbox | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
b6676a01-03ad-580c-ac45-fe87dc30e3a4 | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush bool installed and water tested.
3f745f25-52a7-516f-9bd8-c7230bdc7e60 | tickbox | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and bool operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
b02c74ca-ce9b-55e5-847d-7d01c8c413f7 | tickbox | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
1829d982-4c37-5885-a972-960a346cfbc5 | tickbox | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
c4121985-4d22-5409-a2d6-94c2baf3d142 | tickbox | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
ee1f7265-6c4d-565b-b975-c5966a4105ae | tickbox | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
5fae5fe5-813e-5d78-b858-7955d9f58417 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
f2b9e892-ecdc-58d0-8701-82dc4eaabce3 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Oil Separator Install |  | Oil Separator Install | 4df4f8b2-909b-4161-8ba7-d04d7fe66301
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set. Tank to be a minimum 1500mm away from pump.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | Oil Separator installed in correct orientation (inlet/outlet).
| checkpoint | Ensure all items including oil drum are with oil Separator
| checkpoint | Ensure all venting requirements are met
| checkpoint | Take photo of serial number and tank.
7b165c85-5889-583f-b3ea-424b372bb91d | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Parents Room Rough In |  | Parents Room Rough In | bc98d6a0-c703-4c41-9494-b953b86fc301
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
f8e7f41f-50ec-5569-bf7f-c3aa779bfe22 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
cf203657-4593-54c2-a773-d7ceed688ffc | tickbox | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
aac233ae-7c3f-56fd-9267-c6daf9af3d3c | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush bool installed and water tested.
ef1d56aa-03f0-5ca7-94b1-436783d017cf | tickbox | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and bool operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
563f6267-3599-5bbe-8b67-e7a0d22c2293 | tickbox | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
6a4c7200-e7c5-5cb2-9af5-0c01bcc03f16 | tickbox | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
3da67d84-5bb8-5ad7-b68e-019047626c5c | tickbox | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
d92aaa52-9b90-5cf0-89e1-4df76413ce94 | tickbox | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
59981bad-fce6-5cb8-b3c8-7bc09cab2da9 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
3ca84c74-387f-5fdf-9243-b64293bd470f | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Pressure Services Installation |  | Pressure Services Installation | 924aa64f-6f98-4abe-8201-768488e3ba50
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
237f8370-9ca1-52e2-bd7f-61515477bff2 | note | Check scope of works/specification & ensure all documents are current.
cbfebf02-0411-5a78-91f5-b1279ab37326 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
692c4d2e-66ed-5a62-88bd-fcf018252fa8 | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
| checkpoint | Fire services installed correctly as per workshop drawings.
c4603f5c-0952-57a3-a427-55e8d4136c7f | tickbox | Gal pipe grooves checked with a groove tape. | Yes,No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
34cb5c02-d82b-5772-aa34-23a5f6de4f07 | tickbox | Pipe spacers installed to avoid electrofusion. | Yes,No
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
f12e3958-13ef-5642-90a9-c7b281db5949 | note | All services left under pressure during construction.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
ca247f6d-4d81-52d8-854d-9d9bf12da7da | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards and tested.
| checkpoint | Fire hose reel tagged.
| checkpoint | RPZD valve installed as per AS3500.
12a6b09a-9982-5cad-b779-c26825f7d93a | tickbox | RPZD drain installed & tested. | Yes,No
536774d3-1636-5fef-ace7-a42bc3aae834 | note | Please attach photo of serial number and valve.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Pressure services on apartments/ Hotel or commercial floors. |  | Pressure services on apartments/ Hotel or commercial floors. | 9a5c6328-eb08-4aef-9276-901c0842450d
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
a6e443ca-6a0a-518c-be32-b02076c960f7 | note | Check scope of works/specification & ensure all documents are current.
41629269-29cb-5442-a4d6-d7e1f902a6bf | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
691e9c61-8293-5b44-8f16-6a435862c76e | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
c1fe3222-cfcb-5b3a-9701-d7bb9ac75c1c | tickbox | Witness marks on all press Fittings checked. | Yes,No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
a5a5bc10-d328-5be1-ab41-bc57361bab8b | tickbox | Pipe spacers installed to avoid electrofusion. | Yes,No
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
a15cebad-80f9-58bc-bbab-d9665a024f61 | note | All services left under pressure during construction.
| checkpoint | Isolation lever shut off valves and PRV,s installed.
03ce5efa-fb11-5ee4-b6ca-5404cb0714dd | tickbox | Tempering valve or Thermostatic mixing valve installed in the correct orientation. | Yes,No
3f83e9ea-984f-5bb2-ab45-7e750367ef4c | tickbox | Cold water, Hot water and or meter bars installed and labelled. | Yes,No
f76dff8d-e644-5401-a653-66bc1592ecc8 | tickbox | Connection of all reticulated cold, hot, Gas & NPCW PEX pipes to points of connections from manifold setups. | Yes,No
| checkpoint | Floor waste grate installed.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
83c14fcf-ce53-5bb6-a670-a93048ca1274 | tickbox | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE).
| checkpoint | Garbage Chute RPZD installed and tested. (IF APPLICABLE).
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary).
| checklist | Project finalisation |  | Project finalisation | 7ea08cc2-e204-4d2f-b9e2-e3086ef6d34d
| checkpoint | CCTV completed throughout
| checkpoint | Fire doc finalised and submitted
| checkpoint | SSD produced by designer.
| checkpoint | As Builts completed and issued to builder.
| checkpoint | O&M manual completed and sent to builder.
| checkpoint | RPZ test completed and issued to Sydney water.
| checkpoint | DDCV test completed and issued to Sydney water.
| checkpoint | TMV's tested throughout.
| checkpoint | Gas final inspection completed and certificates sent.
| checkpoint | Certification of everything required issued to builder.
| checkpoint | Trade waste final inspection and certified.
| checkpoint | Maintenance manual created and locked in.
| checkpoint | FHR flow test completed and issued.
| checklist | Rainwater Pressure Pump and filtration |  | Rainwater Pressure Pump and filtration | 2123c7a9-aafb-4e01-bc4b-5bb0b6669c35
| checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth Poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have electrical wired up
| checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
f9e78b48-f015-5579-9c60-219cf5f60fa3 | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Roof work |  | Roof work | eca09976-a42a-4dd4-8b61-d67d66510541
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
9d34e522-8b6d-5bf8-8f7f-9357e9308cc4 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Builder has overflows installed.
| checkpoint | Sewer vents terminated as per AS3500.
f8c4a792-3366-5986-b64b-07d9d84b5206 | tickbox | CCTV of sewer completed | Yes,No
| checkpoint | RWO cleared of debri and CCTV completed.
| checkpoint | RWO grates installed and secured.
834a4139-e264-5d55-af2f-a475f08a4302 | note | Ensure protection screen installed so no pebbles block drains
| checkpoint | Pressure services installed.
| checkpoint | Provisions for other services installed. (IF APPLICABLE)
| checkpoint | UV thermal lagging installed.
| checkpoint | All hydraulic works completed to specification/drawings & Area left clean/tidy.
8b46c66e-edcf-5efc-abd0-7c985620d3c2 | note | Pictures of works completed if applicable.
| checklist | Set out and Penetration installation (Retail, Commercial and car park areas) |  | Set out and Penetration installation (Retail, Commercial and car park areas) | a13ea3a6-594a-4b0f-8a88-2a1eed92cd1b
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure and drainage services complete? Installed at correct Invert levels?
| checkpoint | Downpipes with columns installed and capped off with DWV caps ONLY.
| checkpoint | Sewer, stormwater and pressure penetration points installed. Check off Hydraulic plans.
| checkpoint | Cast in services installed at correct grades (as per AS3500) and locations. Check off Hydraulic plans.
228a6b9f-24c5-5b70-907f-a5e0bcad7046 | note | Photograph inspection booking.
| checkpoint | Correct fire collars installed with test reports on file.
4b5d2a76-1b3f-5aa5-a9f6-d223dcd040d8 | note | Hour rating to meet slab FRL.
| checkpoint | Puddle flanges installed for floor wastes and balconies at minimum concrete height stated on structural drawings.
| checkpoint | Car park drains,RWO's , trench drains and risers installed. Trafficable grates to be class D only.
11b31268-1190-57b7-97f4-530eecd03d5f | note | Correct grade of drain to be installed.
| checkpoint | Miscellaneous penetrations installed.
| checkpoint | All pipe risers to be protected with pipe caps and or duck tape.
| checkpoint | Top up water on the morning prior concrete Pour for major casting.
| checklist | Sewer Connection |  | Sewer Connection | 599bc620-7192-4b54-9deb-d9a624201e43
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Fair trading inspection complete.
| checklist | Sewer Pump Station |  | Sewer Pump Station | a2f3bd4c-0e39-4168-8275-e1993bc0a3ab
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Storm Water Pump Station |  | Storm Water Pump Station | cf43982b-d2ba-495e-ac74-661e52888650
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Stormwater Connection |  | Stormwater Connection | 95423ccb-f2ea-4860-bb06-a3ac3735852a
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Council inspection complete.
| checklist | Tenancy Works |  | Tenancy Works | 0f6414d3-ff72-4022-b218-803a58a759e6
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
| checkpoint | Sewer and trade waste Provisions installed in correct locations and capped off.
| checkpoint | Vent provisions and AAVS installed as per documentation and AS3500.
| checkpoint | Cold Water Gas Point Provision Installed in correct locations and capped off.
1860dc66-6c2f-5aad-953c-5f5f3c0fa46b | tickbox | Sydney water meter installed if applicable. | Yes,No
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE)
| checkpoint | CCTV all lines to ensure clear
| checklist | Water Connection |  | Water Connection | c6af7430-477e-4a19-a38d-cab436ec838d
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checklist | Water Meter Install & RPZD |  | Water Meter Install & RPZD | 6512d21c-e408-43ed-aef1-b1d72c459f39
| checkpoint | Water meter installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | Take photos of device & ensure to get all serial numbers
| checkpoint | Test & commission device as required by certified persons
| checkpoint | RPZD valve installed as per AS3500.
ff868902-a25d-5aed-a7dc-57ec90948093 | tickbox | RPZD drain installed & tested. | Yes,No
e384d12b-c570-507d-9aca-253aac4ff5d1 | note | Please attach photo of serial number and valve.
| checklist | Water Storage Tank |  | Water Storage Tank | 0ee099a8-04c1-4db4-9970-e98040d19666
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Slab or plinth Poured and waterproofed.
| checkpoint | Tank installers to install tank only.
d509198a-95d9-588a-b050-d3490d626997 | tickbox | Tank supplier issues certificates and authorisation to fill tank. | Yes,No
| checkpoint | All valves, overflows , tank top up and sludge drains installed to tank.
| checkpoint | Fill tank up in 500 mm increments. Inspect tank for any leaks and continue till you reach desired level design.
| checkpoint | Dump tank and ensure sludge drain and pipe work is operational.
| checkpoint | Set float valve as per manufacturer's specification.
| checkpoint | Once tank is commissioned book in Chlorination by tank supplier.
| checkpoint | Tank level indicator installed and connected to BMS
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)