## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Aerial Drainage |  | Aerial Drainage | f45c5478-9132-483e-ae3f-6270cc6d8541
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
1b1a9a28-aefa-59c9-8ccc-cade6d5579b4 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Fire collars cleared of concrete slurry & replaced if damaged.
| checkpoint | Sewer, Stormwater, tradewaste and vent services installed correctly as per workshop drawings and schematics.
e22ced09-4d72-505c-96cf-3da2b58579dc | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | yes, no
5b1bb505-9bc5-5845-a9fd-0cb594f7ea42 | button | Check for cross connections. | yes, no
6a02608d-bd3b-500a-8fc3-dc725df96a0f | note | Pink primer and Blue glue used only on UPVC.
| checkpoint | Syphonics installed as per manufacturer's recommendation
d7e4b8c6-fc13-5d14-a37d-c357f2c14930 | button | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults. | yes, no
| checkpoint | Hydrostatic test filled with water to a height not less than 1m above soffit level of highest pipe for a minimum of 30min.
| checkpoint | Retro fit fire collars installed.
4f152ae6-5eac-5174-a0db-f958c51261d2 | button | Fire penetration stickers installed and photographed. High top collars to be smoke sealed. | yes, no
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Acoustic lagging as per project requirements.
| checkpoint | All points capped off to ensure no builders debri enters system.
4f89a3a3-5a83-59a2-84a1-daa9c6d917cc | button | Floor waste protected with sponge. | yes, no
| checkpoint | Update As Built drawing immediately. Confirm IL of pipework.
| checkpoint | All Drainage works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Apartment / Hotel |  | Apartment / Hotel | feada224-d855-43fd-8f80-0bb2b097177e
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
673185ca-ee93-5634-8bcd-dde444c95655 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Balcony gas bayonet or water taps installed as per AS5601 and AS3500. Check foothold requirements
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cistern installed and tested. Ensure cistern is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
b84810eb-e6b4-51f0-99c6-b72174da0d96 | button | separation of services as per AS3500 | Yes, No
| checkpoint | All setouts ok and run eyes over crimps
7684768f-c6a1-5482-84ce-c31eb3c19184 | note | Photograph inspection booking.
| signoff | HOLD POINT - Inspections if required by relevant authorised persons .
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
5b23ace6-3ad9-5c8f-b921-ee33d5c7229e | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy
6bb8829f-1eea-57d0-b89f-12b8354a3854 | note | Pictures of works completed if applicable.
| section | Apartment Commissioning
| checkpoint | Bathroom, Kitchen and Laundry setout off current Architectural drawings.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED, Laundry,bathroom, ensuite and balcony.
| checkpoint | Kitchen mixer and sink installation complete.
577bf61a-1a35-5e03-93ea-f1747cbcb0f3 | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes, No
2c371876-cc83-548e-8e7b-c15d725bc4ad | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes, No
| checkpoint | Dishwasher installed with hoses, Power lead not kinked and dishwasher plum. (cover plate for hoses must be installed)
4ac7944f-3a37-5113-a66e-b7ffbffa7af5 | button | Run full dishwashing cycle and inspect for faults. | Yes, No
| checkpoint | Cooktop installed and power plugged in.
56fea112-0ca6-5cdd-b942-1dbc60a17bae | button | Once gas is on, purge gas safely and ignite cooktop for its operation. Confirm yes once complete. | Yes, No
30204ea9-0433-5801-a035-c9df80998234 | textbox | Hot water delivery to kitchen sink.
| checkpoint | Laundry tub and mixer installed?
8b9713c3-1280-5c60-bf61-a036eee28747 | note | Tub door to swing the correct way.
b6f9fc62-5e08-57dd-a587-a78b7dc71410 | button | Clean aerator, Remove Trap & Clean Out (Tighten Trap) & Test Floor Waste - Clean Out | Yes, No
45890911-1174-58f1-931a-391d93c2a2fb | button | Laundry mixer solid, check for cross connection, run tap, tighten flexis& trap and check mini cock and trap for leaks. | Yes, No
332aacd9-31d9-5b02-8777-2e2184776285 | button | A/C Tundish(Cap if there is no Tundish by AC). Ensure 25mm airgap achieved. | Yes, No
50567eae-e2ed-5f42-bca2-0fdd247b1b37 | button | Washing Machine taps Installed Under Tub/Opp Tub, cover plates installed and AAV installed if applicable. | Yes, No
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
b5ac7dbd-1f71-537d-a7a9-5eb22c8fd855 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
| checkpoint | Basin mixer and basin installed. (photo)
c5ef2501-c538-5fbd-91ee-84663b5e426b | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
6d2bed44-708e-5c8a-96a0-41d60f708e48 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
c4ac1e21-cccc-50ee-9747-4c5a5572092a | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
db7c4455-fae5-5bfc-8309-676680adc10a | textbox | Hot water delivery to Shower.
| checkpoint | Bath installed, Cement grouted in, fill tested and water tested for any pipe or plug and waste leaks.
| checkpoint | Bath mixer cover plate/handle and bath spout installed.
db1a8dc3-dd2f-5440-9206-c623ab0c4505 | button | Bath fill test and water run test, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
| checkpoint | Balcony drains clear, overflows in place?
| checkpoint | Balcony gas bayonet and or water taps installed as per AS5601 and AS3500. Test for leaks and operation.
| checkpoint | Gas valves tagged, CW meter installed and tagged, Hw meter installed and tagged and NPCW installed if applicable.
| checkpoint | Gas Tested with Manometer - on hold for 10 minutes. Ensure absolutely no leaks!
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
c86af5fe-ad70-5921-8410-e533e8b51c41 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
f21cdb8b-d90a-5bc0-8134-f4da990dba4d | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
3a6418af-6b3c-52df-b8da-2fbe7f97704b | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Carpark finalisation |  | Carpark finalisation | fe45b21c-b587-4bb0-bc56-e8c00405aab8
| checkpoint | Bracketing completed as per AS3500
| checkpoint | Pipe jetting and CCTV completed
| checkpoint | All RWO or CPO grates installed and secured.
| checkpoint | Fire doc finalised and submitted
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Cleaners Rooms |  | Cleaners Rooms | dec76f53-6239-416c-99a4-4b3fc64a9cb0
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
9093278d-316a-5759-8d90-fba1ac784c38 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
1862f19c-bb4a-52c2-b2dc-65790b88e2d9 | button | Thermal lagging as per project requirements. | yes, no
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap or floor wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap or floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | Fit out of cleaners room hydraulic PC items
65b23f03-2c1d-5d8d-a1d0-b4768097bde6 | button | Commision PC items and set Temp valve to 49 degrees | yes, no
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Cold Water Pressure Pump |  | Cold Water Pressure Pump | ed90e8ea-5888-4501-b12f-39b012b37bd9
| checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have electrical wired up
| checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
165c5db0-3cf6-52d9-875e-4f7d3fd7aba1 | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Commercial Tenancy |  | Commercial Tenancy | 59f72d4a-4c07-4060-bd9f-02a45937f9cb
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
f0f0b879-2c40-5e60-acac-d0e5d74d499b | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
c3f18a4e-dbf4-5677-afaa-bfd5cff5546d | button | separation of services as per AS3500 | Yes, No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
db221ad2-2e9f-5788-8121-bfbfd5937ddc | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Kitchen mixer and sink installation complete.
792ceef8-6841-5884-9853-48cb3b4b32bf | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes, No
c3b8b671-498f-55b0-9e1b-b8802a36eaec | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes, No
| checkpoint | Tundish point installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
a4ca15ed-54de-562f-beee-816b3f314695 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
c49f324f-105b-502a-8b3e-b2a06d0dee20 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
7e9e505d-eedc-5c35-a8d4-c2db74bd8f2e | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Common Disabled bathroom roughins |  | Common Disabled bathroom roughins | 89b18612-bfbc-49c3-8c61-780a347f2844
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
b28660a2-0552-5a72-9127-366dd8edbfb2 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
da68dcbf-1eea-5904-9365-351d5f6667b5 | button | separation of services as per AS3500 | Yes, No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
b1c4cca4-450d-5a68-bc0a-e309b9967b87 | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
0bb8b365-229b-5ad5-9999-4062925ba07d | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
| checkpoint | Basin mixer and basin installed.
97b47dca-bafb-5043-af1c-5fdcc7166005 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
c8a214ca-6d89-5240-81da-a6ad80f60fb7 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
66fcdf5a-d7f3-5683-a9d0-fef50bef1195 | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
ec21ef39-22f4-5048-90e0-98111cb8144d | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
fe1d7c95-8fe0-53d7-bfb4-00c633bd4073 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
7983aa4f-0eb2-50a9-a7f1-da114da6eff3 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Common Female Bathroom Rough In |  | Common Female Bathroom Rough In | f3e9b107-b404-4921-84b6-80be913801b6
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
46161e53-cdee-5f80-90b6-3cce2f5acb69 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
b048377d-d1dd-5757-9b81-e3a6291261a2 | button | separation of services as per AS3500 | Yes, No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
2734cfb3-1b96-5f73-9abc-aba94587871b | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
43078e88-a201-5103-849a-5d80499fc4d9 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
| checkpoint | Basin mixer and basin installed.
c92d5732-0392-5e40-8d75-a30d7835e201 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
15be89cf-bc80-5fbe-9130-8029269a312f | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
d3abdfac-cbce-570e-8d16-7c541e7d8746 | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
97edef9f-e49b-5e88-8310-2b4875a3fac5 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
aa966e76-5b97-57ee-bb3d-be2eaf1c048d | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
0bf450d6-4972-5ff1-a947-e815c750119d | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Common Male Bathroom Rough In |  | Common Male Bathroom Rough In | 77a78c1a-fb26-4c64-a428-1df0e04d3e35
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
f6ab16f8-8b01-5cb1-9468-dfce85fc13ab | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
45f1dad3-86b8-597a-9d65-3c5399886b35 | button | separation of services as per AS3500 | Yes, No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
aa233f34-6828-5ba4-b571-0b562f462a81 | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
384d3ea6-78ca-5728-8185-42e4e6b3fafd | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
| checkpoint | Basin mixer and basin installed.
2a7dfa24-d81f-566b-acfe-9bf8941191d3 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
cfb1e37e-8403-553c-9176-ca83064a8869 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
ce381289-c8ce-5c7d-9ff3-7d222387ec62 | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
| checkpoint | Urinals installed and connected to solenoid and waste.
f54ef8a0-8355-529c-9903-633440bef61a | button | Flush Urinal 3 Times (check that sensor is working fine). | Yes, No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
19a62bc2-bc7f-57dd-99c7-af3172ef6c03 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
ca7c8c31-828e-5a06-a975-39e58fe12fb0 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
07ee7fda-fbcf-588c-814e-c3f816298107 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Concrete Pour Checklist (Apartment and hotel floors) |  | Concrete Pour Checklist (Apartment and hotel floors) | 7bf538f1-b95c-43e2-873e-d090f989a54d
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure & drainage services complete & Installed at correct Invert levels.
| checkpoint | Downpipes with columns installed & capped off.
| checkpoint | Correct fire collars installed with test reports on file.
58784a42-736a-52fd-8c5d-8f3a6554d93d | note | Integrity and insulation hour rating to meet slab FRL.
| checkpoint | All hydraulic service penetrations points installed.
587e290f-8b10-5b7f-8540-bb028dc72a26 | note | Cast in services installed at correct grades (as per AS3500) & locations.
| checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in.
bf7812e5-c7db-5ad6-99c8-3ccd2d29cb32 | note | Photograph inspection booking.
| checkpoint | Balcony, Bathroom, Kitchen & Laundry Layouts Checked.
| checkpoint | Puddle flanges installed for floor wastes and balcony drains at minimum concrete height stated on structural drawings.
0002a2b2-4fc8-5e49-bef4-b595b0a726e0 | note | Car Park Drains Checked.
9913b2fc-c9e3-5a77-b17b-ef5e3ed15652 | note | Correct grates, Planter box drains or RWO installed.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Top up water on the morning prior concrete pour for major casting.
| checkpoint | Cold water, Hot water and gas service conduits installed from lobby to apartment/hotel.
82da1e8a-2f48-5871-b2ab-e8db742ebf8c | button | Cold water, Hot water and gas service conduits loops to balconies and kitchen islands installed. | yes, no
| checkpoint | Pictures of works completed.
f9dd518b-f986-5753-a029-fce64de5725b | textbox | Concrete pour date:
c6911be2-cb5c-56dd-aa1f-cc8a9e049ab4 | note | All Penetration Work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | DDCV for Fire supply |  | DDCV for Fire supply | ce464b60-9060-442c-ae36-ada8fb73d01c
| checkpoint | DDCV installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | DDCV valve installed as per AS3500. For fire supply.
a937c041-f5ab-50e6-a39c-ea51351fed7e | button | DDCV drain installed and tested. | yes, no
b8311af1-3b00-5c9a-adbe-8291fe7dee7c | note | Please attach photo of serial number and valve.
| checklist | Fire Hydrant/Sprinkler Pump Room & Tank |  | Fire Hydrant/Sprinkler Pump Room & Tank | 817db116-aac7-4b02-a9fb-c2743eed5d72
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Cold water services installed correctly as per workshop drawings
| checkpoint | Rainwater reuse service s installed correctly as per workshop drawings.
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Supply & install tank top up supply with correct float valve.
| checkpoint | Wastes to be in correct locations
| checkpoint | Floor wastes installed
| checkpoint | Clear out debris from floor wastes
| checkpoint | Tundish points installed as required
| checkpoint | Water services pressure tested @ 1500KPA or 1.5 x working pressure
39561766-8560-5ac2-ba5f-682ea46e2297 | note | Whichever is higher for a minimum duration of 60 minutes | yes, no
| checkpoint | Coordination with walls and other services overviewed and coordinated onsite.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Garbage Room Work |  | Garbage Room Work | afbbb8f6-c2e9-49bc-890f-260df4075b6f
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
10c57dc8-49a4-5654-b606-b495f82a0899 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
5533bdb3-8360-5a59-a12a-f75e5afe7d37 | button | Thermal lagging as per project requirements. | yes, no
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | RPZD valve installed as per AS3500.
bfcfd487-ddce-5fed-b007-ba0e8d57d5b5 | button | RPZD drain installed and tested. | yes, no
1e9dc53b-58e4-5eb4-a54e-b6f1e9d72ed8 | note | Please attach photo of serial number and valve.
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Gas Connection |  | Gas Connection | fb666712-3466-4de6-b0e9-2aa52259aa64
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per Jemena requirements (attach photos if necessary)
| checklist | Gas Meter |  | Gas Meter | ae78069f-ed7d-4fd3-b447-4595f526cc25
| checkpoint | Arrange gas inspector for inspection and requirements.
| checkpoint | Gas reg to be installed on plinth if external. Install as per Jemena requirements.
| checkpoint | Run breather vents off regulators if installed internally. Pipe size usually 25mm
| checkpoint | Ensure the Gas reg is installed in correct orientation.
| checkpoint | Labelling - 1050kpa, 210kpa and or 5 Kpa
| checkpoint | Test all pipework and joints for leaks.
| checkpoint | Reg test point to be facing in a direction where accessible.
| checkpoint | Union or flange connection with valves so that reg can be removed or serviced.
| checkpoint | Take photo of serial number and gas meter.
| checkpoint | Arrange gas inspector for inspection.
59af8ef1-7788-5505-911a-a2810686760c | note | All works completed to specification/drawings, Jemena standards & Area left clean/tidy
| checklist | Grease Tank |  | Grease Tank | 0e196c27-0708-4e82-9610-48ce9821db2e
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Grease tank installed in correct orientation (inlet/outlet)
| checkpoint | 100mm Chamber vent to atmosphere.
| checkpoint | Trade waste inlet connection.
| checkpoint | Accessibility around tank minimum 600mm.
| checkpoint | Platform installed within room.
| checkpoint | Suction line within room installed. 80mm minimum line, storz adapter and shut off valve.
| checkpoint | I.O's installed inlet and outlet.
| checkpoint | Ensure lids are closed off properly.
| checkpoint | Take photo of serial number and tank.
| checkpoint | RPZD valve installed as per AS3500.
6b0a0209-7528-5aad-9b4d-a3a9de052076 | button | RPZD drain installed & tested. | yes, no
b97e8fb4-ec5b-543a-9630-a499013b4bf2 | note | Please attach photo of serial number and valve.
| checkpoint | Arrange trade waste inspection if required.
c3ed75ba-b893-5d53-bef6-89bbde51dc92 | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Hot water flush for trade waste |  | Hot water flush for trade waste | fb4d1fe1-1bac-483d-86bb-e52bce6275ff
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Drainage installed as per AS3500
cbaaa244-e7b0-534f-ba36-014c3e3eed32 | button | Hot water flush installed and commissioned | yes, no
| checkpoint | 25mm airgap to avoid cross contamination
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | HOT WATER PLANT and RETURN PUMPS |  | HOT WATER PLANT and RETURN PUMPS | 790f09f7-3da9-4a3b-accb-145ea49c8620
| section | Hot water plant
| checkpoint | Installation – refer to installation checklist for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Flue installed as per manufacturer's specification.
5aadcd77-b7c3-5284-9212-3e59cce15605 | button | Power flue turned on. | Yes, No
| checkpoint | Temp relief points ran to tundishes.
| checkpoint | Temperature probe from control box installed into storage tanks.
| checkpoint | Check that an adequate water supply is available to the hot water system.
| checkpoint | Water supply pressure shall not exceed the maximum pressure stated by manufacturer.
| checkpoint | Open cold water inlet valve, hot water outlet valve
| checkpoint | Exercise all valves and ensure correct operation. Ensure all valves are in open position prior turning power on.
| checkpoint | Check the system is fully charged & all air is bled from the system & no leaks are evident
| checkpoint | Ensure hot water heaters and storage tanks are full of water and all valves are open.
| checkpoint | Ensure pressures are not greater than 750Kpa to the heaters or storage tanks.
| checkpoint | Open all individual gas isolation valves & purge gas lines.
| checkpoint | Test gas pipe work for leaks.
| checkpoint | Check the gas supply pressure at the inlet to the water heater with the water heater and all
| checkpoint | range is NG: 1.13Kpa - 3.5Kpa & LPG: 2.75Kpa - 3.5Kpa
a278b450-af39-506d-9912-52076532fbbb | button | Clean filters and strainers once after 4 hours of use. | Yes, No
| checkpoint | Set temperature to 65 degrees.
| section | HOT WATER RETURN PUMPS
| checkpoint | Hot water return pumps - Installation – refer to installation checklist for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Ensure there is water supply to the pumps.
| checkpoint | Clean filters and strainers once after 4 hours of use.
| checkpoint | Turn on power to the pumps. Set the pumps to alternate.
| checkpoint | Purge pumps of air. Ensure water is visible from the purging points.
| checkpoint | Set balancing valves.
| checkpoint | Inspect system for any leaks or faults.
| checklist | In-Ground Drainage Hydraulic Services ITP V.210121 |  | In-Ground Drainage Hydraulic Services ITP V.210121 | 9ec9232f-edba-4d21-9884-2d97cbde7920
| section | Sewer/ Tradewaste
| checkpoint | Sewer drainage, Tradewaste drainage and vents installed as per workshop drawings.
de535a71-0f31-5700-b2cc-92ca2c6d9091 | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | yes, No
f4d7cb04-6b48-5bcb-adbe-4f6f5bc59a6b | button | Pipework risers labelled, pink primer and blue glue used only. | yes, No
| checkpoint | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Inspection by Fair Trading for sewer drainage to be done & other inspections if required by others.
e45e1c37-8afd-5a06-87a0-ba91f0b42fb0 | note | Photograph inspection booking.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
17882944-6701-5854-9379-34204ba59487 | note | Ensure compaction of fill materials is to specifications & Australian Standards.
70be0d8f-087f-5dd3-b90a-486fe778c52f | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | yes, No
| checkpoint | All works completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Stormwater
| checkpoint | Stormwater drainage installed as per workshop drawings.
500ce6ff-365a-5b38-a26f-8fb868426030 | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | yes, No
| checkpoint | Installation of pits to the correct levels.
a0764859-0fed-527a-8a22-b47fbfdca1c2 | button | Ensure correct grates & lids used with appropriate load ratings for locations to traffic movements. | yes, No
95a582ef-150a-5667-bef3-e9142964de60 | button | Pits to be sparged - Made water tight to inlet & outlet pipework. | yes, No
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | HOLD POINT - Inspections if required by relevant authorised persons .
0ec9bf08-3bc8-5793-b080-6df47470f4e0 | note | Attach inspection reports below.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
cdc9a731-671f-571e-87e9-0d6592e998a8 | note | Ensure compaction of fill materials is to specifications & Australian Standards.
81ae13d0-38c8-5d3f-a0bc-2e33407a1d8c | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | yes, No
| checkpoint | All Stormwater Work completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Handover
| checkpoint | Update As Built drawing immediately - Confirm IL of pipework. Attach with ITP submission.
| checkpoint | CCTV completed pipework to ensure no defects before concrete pour to prevent future problems.
| checkpoint | Pictures of works completed - Attached below.
0ddf3e5d-7d1c-536b-9b80-565ab55dd1ce | textbox | Concrete pour date.
| checklist | Inground Pressure Services Installation. |  | Inground Pressure Services Installation. | ce79aa34-27fc-4c68-baa4-4167a91c23ad
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
0b6b4c29-c0c1-55d6-b926-592ee84fa73b | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools, welding equipment & deburring machine ready for use..
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
67422e17-08ea-51d8-8897-cd20999a87ce | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
18d7f07b-d6dd-5e07-8454-4b583d6efd9e | button | Witness marks on all press fittings checked. | yes, no
| checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any.
fb44cc6d-f597-57e8-b8c5-496738ec5248 | note | Photograph inspection booking.
| checkpoint | Fire services installed correctly as per workshop drawings.
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
10ec23ca-355c-51f0-88e1-0d38ce869be2 | note | Ensure trace tape is installed
68ac642c-b294-5605-b50a-b08058307cb0 | note | Ensure compaction of fill materials is to specifications & Australian Standards.
fb46970a-c163-5b39-936d-cc146665af87 | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | pass, fail, n/a
adb331f9-56d2-5045-bd03-4a9df1dd0a9c | note | All services left under pressure during construction.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Managers Office Work - Bathroom |  | Managers Office Work - Bathroom | a821e0e2-caa5-4389-ad90-d70e14348915
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
6a05b58b-02c8-5f0c-a3ae-bfad4a0af545 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
70bbae32-99ed-5473-b4e6-9ed9e2c31fa4 | button | separation of services as per AS3500 | Yes, No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
d346e26b-3094-59c2-aac0-c9ae9af2a849 | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
637816d9-e533-5d3c-834c-7380e7dba8ab | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
| checkpoint | Basin mixer and basin's installed.
bece190c-783e-554e-b4dc-03d28eed764c | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
8bf814fa-4725-5624-aea1-145fc6724657 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
f1d7ea1d-a085-5b09-bd99-0aca46241252 | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
1621ad32-ef57-5067-8923-f8dd550c2285 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
48c3155b-e584-5c6b-8156-dc2a3d2d03f9 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
f603db04-03ee-52eb-a68a-371f8fe30b51 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Oil Separator Install |  | Oil Separator Install | 63abf66d-e645-4bd7-8b40-f79383b9bd23
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set. Tank to be a minimum 1500mm away from pump.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | Oil Separator installed in correct orientation (inlet/outlet).
| checkpoint | Ensure all items including oil drum are with oil Separator
| checkpoint | Ensure all venting requirements are met
| checkpoint | Take photo of serial number and tank.
6ebaab62-909a-5ad0-b65d-4a316b1a7924 | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Parents Room Rough In |  | Parents Room Rough In | 53415cf1-a131-4f4d-8e8f-33ffdf86f992
| section | Roughin
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
ee5bbeea-564f-5618-a951-47f47e3dc73b | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
13289032-288c-5233-8fb9-8a2ee9b8b6fd | button | separation of services as per AS3500 | Yes, No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
947f71b2-1e10-5d8e-9e8e-474639ac4199 | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fitout and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
034c26a7-6cf8-5f17-b03e-b95bcc1a9be7 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
| checkpoint | Basin mixer and basin's installed.
b0fb6cba-00e1-5263-9f60-d840b49fefd3 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
a1c83922-4a90-57a2-a86b-5695bba264b4 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
4bc558bd-3b6f-5474-9457-052b8a56f8f0 | button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
b748630d-1f7a-5b0f-8459-4ca9fc885ff5 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
f82e78f0-f4b3-5090-8adc-d7065c283fe8 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
f5674a2a-239b-5027-be51-caba3c8224e5 | note | General photos, comments & observations during fitout stage (Add below).
| checklist | Pressure Services Installation |  | Pressure Services Installation | c649fa1e-536c-43b7-8e86-60c3d55d43a4
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
a0aef5f0-e0c2-5386-a296-4085e92ccc3f | note | Check scope of works/specification & ensure all documents are current.
df95e9b3-5634-5826-ad14-70f50ffe5385 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
772aeb8f-2606-56d2-a919-f5dcb1aae297 | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
faf72eb5-00f6-58ea-a8aa-7e31cc03e09e | button | Witness marks on all press fittings checked. | Yes, No
| checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any.
f847204c-fcaf-5f99-8395-15ac4b78bf05 | note | Photograph inspection booking.
| checkpoint | Fire services installed correctly as per workshop drawings.
f3ba133f-0e44-5c1a-b16a-9b3e34915a7b | button | Gal pipe grooves checked with a groove tape. | Yes, No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
ff18b876-e6fe-5ba6-a0d8-b90671f3bef1 | button | Pipe spacers installed to avoid electrofusion. | Yes, No
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
c6badad4-3c91-5581-b4f6-a6e8c95e5f37 | note | All services left under pressure during construction.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
ab621db0-42c5-5692-bc1b-f2ca38b11398 | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards and tested.
| checkpoint | Fire hose reel tagged.
| checkpoint | RPZD valve installed as per AS3500.
0a4efdb1-9749-5a15-afa0-1007d45a8c0f | button | RPZD drain installed & tested. | yes, no
aa59ab6b-d991-5da9-a431-5b11d1c57af5 | note | Please attach photo of serial number and valve.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Pressure services on apartments/ Hotel or commercial floors. |  | Pressure services on apartments/ Hotel or commercial floors. | 1e9d07e0-715f-43ba-9862-e15bf7911e01
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
280323b1-8330-5c76-b2ca-bf3c35012ecc | note | Check scope of works/specification & ensure all documents are current.
5be3d3b6-cdcf-583a-bbc0-ff45e08315e6 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
4f05ca2f-2c21-5f81-b863-a89c86ed8a43 | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
b5852738-2ec5-5510-b878-feada03f1c04 | button | Witness marks on all press fittings checked. | Yes, No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
ae284f86-04dc-5281-aa9f-0a58f6d14ff6 | button | Pipe spacers installed to avoid electrofusion. | Yes, No
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
63af5679-6270-5abf-b52b-6dc43f405209 | note | All services left under pressure during construction.
| checkpoint | Isolation lever shut off valves and PRV,s installed.
3e91ab44-af63-51f0-af23-855c92f513e4 | button | Tempering valve or Thermostatic mixing valve installed in the correct orientation. | Yes, No
b266aeeb-3e5f-5144-9df2-5c4bf6e4a641 | button | Cold water, Hot water and or meter bars installed and labelled. | Yes, No
a212a75e-df67-5527-b29b-260ffcdeac06 | button | Connection of all reticulated cold, hot, Gas & NPCW PEX pipes to points of connections from manifold setups. | Yes, No
| checkpoint | Floor waste grate installed.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
2540a75b-c67a-5f00-9d03-911d74f2f7f2 | button | Smoke seal applied to all penetrations required. | Yes, No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE).
| checkpoint | Garbage Chute RPZD installed and tested. (IF APPLICABLE).
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary).
| checklist | Project finalisation |  | Project finalisation | 38d2d0a2-78e9-409e-b426-eb7e7f8da362
| checkpoint | CCTV completed throughout
| checkpoint | Fire doc finalised and submitted
| checkpoint | SSD produced by designer.
| checkpoint | Asbuilts completed and issued to builder.
| checkpoint | O&M manual completed and sent to builder.
| checkpoint | RPZ test completed and issued to Sydney water.
| checkpoint | DDCV test completed and issued to Sydney water.
| checkpoint | TMV's tested throughout.
| checkpoint | Gas final inspection completed and certificates sent.
| checkpoint | Certification of everything required issued to builder.
| checkpoint | Trade waste final inspection and certified.
| checkpoint | Maintenance manual created and locked in.
| checkpoint | FHR flow test completed and issued.
| checklist | Rainwater Pressure Pump and filtration |  | Rainwater Pressure Pump and filtration | ef072f32-c6cf-466d-855b-82d31435b2e2
| checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have electrical wired up
| checkpoint | Pump supplier to commission . Purge pumpset and set pressures correctly.
87fc5e4e-f511-5ac2-b6c5-a7a10def68eb | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Roof work |  | Roof work | 9364fad7-c287-4bfd-8ced-c315589444e6
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
5810819f-2ad8-5798-8d7d-f5f07d53715a | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Builder has overflows installed.
| checkpoint | Sewer vents terminated as per AS3500.
9ed95ee4-dac7-5862-9d92-3dc1430fc26c | button | CCTV of sewer completed | Yes, No
| checkpoint | RWO cleared of debri and CCTV completed.
| checkpoint | RWO grates installed and secured.
eed05ab6-6687-5000-8bd3-ae9195317081 | note | Ensure protection screen installed so no pebbles block drains
| checkpoint | Pressure services installed.
| checkpoint | Provisions for other services installed. (IF APPLICABLE)
| checkpoint | UV thermal lagging installed.
| checkpoint | All hydraulic works completed to specification/drawings & Area left clean/tidy.
b486bd7e-af06-5c51-affc-05642153c101 | note | Pictures of works completed if applicable.
| checklist | RPZD and Water Meter Install |  | RPZD and Water Meter Install | 1ccce583-08f7-45c8-b427-c14be49d8436
| checkpoint | Water meter installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | Take photos of device & ensure to get all serial numbers
| checkpoint | Test & commission device as required by certified persons
| checkpoint | RPZD valve installed as per AS3500.
40ac7997-1876-5aa4-affb-77088572f000 | button | RPZD drain installed & tested. | yes, no
a756ac64-1d43-54da-b0a3-00ccafcf574d | note | Please attach photo of serial number and valve.
| checklist | Setout and Penetration installation (Retail, Commercial and carpark areas) |  | Setout and Penetration installation (Retail, Commercial and carpark areas) | 96fe5780-6cf2-4140-8776-9f871855665d
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure and drainage services complete? Installed at correct Invert levels?
| checkpoint | Downpipes with columns installed and capped off with DWV caps ONLY.
| checkpoint | Sewer, stormwater and pressure penetration points installed. Check off Hydraulic plans.
| checkpoint | Cast in services installed at correct grades (as per AS3500) and locations. Check off Hydraulic plans.
| checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in.
e390f868-b189-5119-a110-84a1c0a3fb4e | note | Photograph inspection booking.
| checkpoint | Correct fire collars installed with test reports on file.
17a08d14-5825-51cf-b4a0-d700ba4cf460 | note | Hour rating to meet slab FRL.
| checkpoint | Puddle flanges installed for floor wastes and balconies at minimum concrete height stated on structural drawings.
| checkpoint | Car park drains,RWO's , trench drains and risers installed. Trafficable grates to be class D only.
1764bc8b-4f3a-5fd8-b75c-51125ea8f46a | note | Correct grade of drain to be installed.
| checkpoint | Miscellaneous penetrations installed.
| checkpoint | All pipe risers to be protected with pipe caps and or duck tape.
| checkpoint | Top up water on the morning prior concrete pour for major casting.
| checkpoint | Pictures of works completed.
ed6bad26-615e-5b5d-bc4d-8c59f872f012 | textbox | Concrete pour date:
89c472f1-38e0-5018-93f4-78ba7eae25c9 | note | All Penetration Work completed to specification/drawings & Area left clean/tidy.
| checklist | Sewer Connection |  | Sewer Connection | 0d5ad188-a2d8-4659-8c9b-2d86a880dcdd
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Fair trading inspection complete.
| checklist | Sewer Pump Station |  | Sewer Pump Station | da493c1a-bb93-43a6-a631-0d07014f48ac
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Storm Water Pump Station |  | Storm Water Pump Station | 9c09addc-50ac-4c44-9250-f231361b1eb6
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Stormwater Connection |  | Stormwater Connection | 0ecb7b9d-557f-4ead-84f8-4e86dbc789fb
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Council inspection complete.
| checklist | Tenancy Works |  | Tenancy Works | 11750ba5-6665-44d7-b79b-b2129ae8c7d7
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
| checkpoint | Sewer and trade waste Provisions installed in correct locations and capped off.
| checkpoint | Vent provisions and AAVS installed as per documentation and AS3500.
| checkpoint | Cold Water Gas Point Provision Installed in correct locations and capped off.
e2d122a0-0f29-55dc-9f85-75fd69c5883c | button | Sydney water meter installed if applicable. | yes, no
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE)
| checkpoint | CCTV all lines to ensure clear
| checklist | Variation |  | Variation | 54e83bfe-8312-470f-b32d-0ec783a17165
| checkpoint | Variation Details Approved
cc860a14-f5e0-5465-8f46-9fbd3d3f2031 | textbox | Reference/Drawing/Instruction Number
691d0bb0-36a4-5b5f-9f84-8ca8881eda68 | textbox | Variation Area
3bf848c9-b585-58a1-9348-786a5604a8db | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
| checkpoint | Variation Completed
| checklist | Water Connection |  | Water Connection | 60c48a66-6ce3-4329-b9fc-a46882b64110
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checklist | Water Storage Tank |  | Water Storage Tank | 53cdc534-1e0b-4839-9087-550d1288c257
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Slab or plinth poured and waterproofed.
| checkpoint | Tank installers to install tank only.
b09c9157-d348-55db-a591-fe059371191b | button | Tank supplier issues certificates and authorisation to fill tank. | pass, fail, n/a
| checkpoint | All valves, overflows , tank top up and sludge drains installed to tank.
| checkpoint | Fill tank up in 500mm increments. Inspect tank for any leaks and continue till you reach desired level design.
| checkpoint | Dump tank and ensure sludge drain and pipe work is operational.
| checkpoint | Set float valve as per manufacturer's specification.
| checkpoint | Once tank is commissioned book in Chlorination by tank supplier.
| checkpoint | Tank level indicator installed and connected to BMS
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)