## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Aerial Drainage |  | Aerial Drainage | be90a603-0949-452b-9c84-8c12cf98e752
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
fdbca751-4bc6-5afe-9cf9-7afd897f76ef | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Fire collars cleared of concrete slurry & replaced if damaged.
| checkpoint | Sewer, Stormwater, Trade Waste and vent services installed correctly as per workshop drawings and schematics.
ceddedb4-64a1-5fd8-8a25-9b03942a5a8e | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
3e6e1893-ccda-557d-8d56-d62984b31385 | button | Check for cross connections. | Yes,No
153e4274-cfe1-5746-b313-b8f830a6a987 | note | Pink primer and Blue glue used only on UPVC.
| checkpoint | Syphonics installed as per manufacturer's recommendation
eaa97dba-add6-5761-bef8-4821b6e9399f | button | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults. | Yes,No
| checkpoint | Hydrostatic test filled with water to a height not less than 1m above sofFit level of highest pipe for a minimum of 30 min.
| checkpoint | RetroFit fire collars installed.
94b29f0c-5049-5d2a-9697-113be99cc128 | button | Fire penetration stickers installed and photographed. High top collars to be smoke sealed. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Acoustic lagging as per project requirements.
| checkpoint | All points capped off to ensure no builders debri enters system.
a03a893f-e037-5209-9a37-75c3ea7ddf91 | button | Floor waste protected with sponge. | Yes,No
| checklist | Apartment / Hotel |  | Apartment / Hotel | b040c888-dfc8-4c03-bbcc-9057b1dc2764
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
b9998647-e221-5a69-a076-77b228b4128a | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Balcony gas bayonet or water taps installed as per AS5601 and AS3500. Check foothold requirements
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cistern installed and tested. Ensure cistern is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
511ec95f-3e53-5e56-82d7-e44d280e35d1 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
903d117e-83b3-58dd-a19d-fc39f572527e | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy
| section | Apartment Fit Off & Commissioning
| checkpoint | Bathroom, Kitchen and Laundry set out off current Architectural drawings.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED, Laundry,bathroom, ensuite and balcony.
| checkpoint | Kitchen mixer and sink installation complete.
aeb2d544-ff61-5608-b39a-883051160c21 | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexi & trap and check mini cock for leaks. | Yes,No
b40aa3dd-6fb7-5083-b190-ef1899f21a93 | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Dishwasher installed with hoses, Power lead not kinked and dishwasher plum. (cover plate for hoses must be installed)
78de3ef8-c4bd-5eaf-87f0-b24e7159512e | button | Run full dishwashing cycle and inspect for faults. | Yes,No
| checkpoint | Cooktop installed and power plugged in.
4ccfdca0-9c60-5f8b-90b8-ac4a523ac036 | button | Once gas is on, purge gas safely and ignite cooktop for its operation. Confirm yes once complete. | Yes,No
a605e4f6-4c23-57b1-833d-2248e53e63eb | textbox | Hot water delivery to kitchen sink.
| checkpoint | Laundry tub and mixer installed?
a41a5f5b-12db-5580-9685-183da902a527 | note | Tub door to swing the correct way.
827f9631-1a8b-50d5-910e-4a2a4f662db3 | button | Clean aerator, Remove Trap & Clean Out (Tighten Trap) & Test Floor Waste - Clean Out | Yes,No
3005fcb2-38a7-575f-9a96-67078f6e7698 | button | Laundry mixer solid, check for cross connection, run tap, tighten flexi & trap and check mini cock and trap for leaks. | Yes,No
ea11b372-b23c-504f-ae94-74618de8faa6 | button | A/C Tundish(Cap if there is no Tundish by AC). Ensure 25mm air gap achieved. | Yes,No
b17063b9-ee5c-584c-939b-eddfaba7eed8 | button | Washing Machine taps Installed Under Tub/Opp Tub, cover plates installed and AAV installed if applicable. | Yes,No
| checkpoint | Toilet, Toilet seat's, Cistern and flush button installed and water tested.
218c9f52-28a0-5c28-8b04-f0aa211e66dd | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed. (photo)
80e0f647-3952-5616-8641-319f9f411453 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
a9e8af0d-855d-5424-87e8-1bef9fa438ef | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
9d2b370e-67ca-5d2b-aab9-2d508aa9105e | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
d3ab7a81-d946-579e-b24d-8e83455bb020 | textbox | Hot water delivery to Shower.
| checkpoint | Bath installed, Cement grouted in, fill tested and water tested for any pipe or plug and waste leaks.
| checkpoint | Bath mixer cover plate/handle and bath spout installed.
7a0bcf21-7fcf-533f-86a8-4050c5c0251e | button | Bath fill test and water run test, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Balcony drains clear, overflows in place?
| checkpoint | Balcony gas bayonet and or water taps installed as per AS5601 and AS3500. Test for leaks and operation.
| checkpoint | Gas valves tagged, CW meter installed and tagged, Hw meter installed and tagged and NPCW installed if applicable.
| checkpoint | Gas Tested with Manometer - on hold for 10 minutes. Ensure absolutely no leaks!
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
64c29fc9-71e1-5d07-ac4f-d086c47cb21c | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
ed8cd412-11f7-5118-9ad4-b8299c748bff | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
f77937fd-d8c2-540d-85d4-c4f16d0441bf | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Car Park Finalisation |  | Car Park Finalisation | 1953f5cf-791c-46d6-af3a-0d4ea4d092cc
| checkpoint | Bracketing completed as per AS3500
| checkpoint | Pipe jetting and CCTV completed
| checkpoint | All RWO or CPO grates installed and secured.
| checkpoint | Fire doc finalised and submitted
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Cleaners Rooms |  | Cleaners Rooms | e3bbc70c-82f4-46f2-a1ec-ae06f88a4b28
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
1216d482-281a-57ad-b5d6-4ff623927650 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
76fdd7e1-5de0-519b-ade6-bc145da31a0a | button | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap or floor wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap or floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | Fit out of cleaners room hydraulic PC items
64bca623-aec5-54d3-b80a-a63ac3f3df83 | button | Commision PC items and set Temp valve to 49 degrees | Yes,No
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Cold Water Pressure Pump |  | Cold Water Pressure Pump | 4feef422-c6d2-4449-9d4d-25955edbeb56
| checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth Poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have electrical wired up
| checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
b4e9b165-429f-5e15-a9be-1e6502eda76d | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Commercial Tenancy |  | Commercial Tenancy | 238acce1-f385-45aa-a2b3-e286d4c01822
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
1f282f20-91aa-5603-ad8e-38d0cd6e0801 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
1cf54817-c7b4-5117-9bc5-a0af70627f6c | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
df270aef-43d6-5953-abb5-06218ed96eb3 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Kitchen mixer and sink installation complete.
cb37cf48-7ed3-5401-8245-62510fa0e530 | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes,No
1859dbb3-cead-56fa-9c58-3643e72b58ca | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Tundish point installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
c92dccc6-6c72-5907-a8e1-241a006d25d6 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
878eaed1-8404-5d37-8ff0-65fc58025d33 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
efd5b4f4-ae7d-5e19-aa55-f9d4d7914748 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Disabled bathroom Rough Ins |  | Common Disabled bathroom Rough Ins | a2d5c99f-69e1-4c38-a912-4d43aa890685
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
c034bbaf-6958-5994-98c2-ca9736c88e47 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
fc7b57a2-e823-585a-a827-68551cb45dd9 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
4236faae-7f6d-56ee-9e68-6a76fee45310 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
d5664f14-bbe1-51fd-b0cf-368b9b7bf67f | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
199ed9a3-1e7c-5e60-a0af-35b39e886c1d | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
a4fd1062-f898-54c7-ae49-3cff135e458b | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
78377cbb-cf18-5763-a92f-d8067892a1d8 | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
4ac7999d-0852-5a40-95a4-e1116fe7d9dc | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
6b4e12ae-23f7-5461-8169-b97ee31363e2 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
3211ed0b-1fd8-5a72-b599-500db52a1732 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Female Bathroom Rough In |  | Common Female Bathroom Rough In | 694e4a05-1b57-4df3-92ea-ec4629a03104
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
ef78843e-595d-543e-8735-ab1762b11396 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
d9bdab60-6fbd-5940-a6d8-90262c30241c | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
ef605d30-14fd-528b-9df9-f9da1f91a045 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
baf1fbd5-ee46-530b-a75b-3820101c8e95 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
51e13bd3-3b3b-534c-83fb-2939b986dc51 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
76e978bb-ffc2-5d65-8878-9eef4a8ae3f6 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
8229ead6-1c3d-562e-982b-ceeca5d45364 | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
59c212af-ac6b-53c5-98f3-c4830758d1b0 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
4d00dc4a-bb3f-54ff-afb6-a56099dc950f | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
70f16b98-2542-5e01-b771-fbffecc15634 | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Common Male Bathroom Rough In |  | Common Male Bathroom Rough In | 38d664ed-6cf2-464e-9ede-d4b71513e3f6
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
a79ce980-3562-5d63-a8ad-cd802d5a3195 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
613e6ce5-fca5-5d6f-9cd5-ae5d4785a4a3 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
e3b41936-fd7c-5a6a-a319-d09794234c2a | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
e4b0e303-70d5-5242-a6bd-7fc9f29819b8 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
884027f8-041a-516d-8f12-6de1e60a9b33 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
0fec7e2c-4f60-57dc-a621-26512d7c5167 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
c9a081b7-b71b-5d35-98e9-dd7c0b71f705 | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Urinals installed and connected to solenoid and waste.
665cc6f3-602f-5e96-9436-9a2194f81fb3 | button | Flush Urinal 3 Times (check that sensor is working fine). | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
812c5f55-743b-5517-964a-acb5ee31d550 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
c1639cfc-b7fd-5114-936f-c5732554b4d8 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
8957f7a8-f5e2-5714-b8f1-d142a9a91b0b | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Concrete Pour Checklist (Apartment and hotel floors) |  | Concrete Pour Checklist (Apartment and hotel floors) | b8b0cce7-9926-4840-830f-b7f1a7c10dae
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure & drainage services complete & Installed at correct Invert levels.
| checkpoint | Downpipes with columns installed & capped off.
| checkpoint | Correct fire collars installed with test reports on file.
ae743573-f281-59b2-9a97-ebd51587c0a9 | note | Integrity and insulation hour rating to meet slab FRL.
| checkpoint | All hydraulic service penetrations points installed.
| checkpoint | Balcony, Bathroom, Kitchen & Laundry Layouts Checked.
| checkpoint | Puddle flanges installed for floor wastes and balcony drains at minimum concrete height stated on structural drawings.
365fe4da-c4dd-54f3-b98b-de29c0810e85 | note | Car Park Drains Checked.
c239da0e-c7f7-562c-b50e-f75b74f42219 | note | Correct grates, Planter box drains or RWO installed.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Top up water on the morning prior concrete Pour for major casting.
| checkpoint | Cold water, Hot water and gas service conduits installed from lobby to apartment/hotel.
493d05fc-f4da-526f-a49f-84a43708b036 | button | Cold water, Hot water and gas service conduits loops to balconies and kitchen islands installed. | Yes,No
| checklist | DDCV for Fire supply |  | DDCV for Fire supply | 8627d368-01b4-4f33-9f3d-58e59bc96c6a
| checkpoint | DDCV installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | DDCV valve installed as per AS3500. For fire supply.
8c6701ba-ac7c-52f4-8a80-6e33fdbd3d88 | button | DDCV drain installed and tested. | Yes,No
0a33de7d-4783-5068-b65a-2f9f58fee9b0 | note | Please attach photo of serial number and valve.
| checklist | Fire Hydrant/Sprinkler Pump Room & Tank |  | Fire Hydrant/Sprinkler Pump Room & Tank | f28d96b4-39cb-4cab-903e-725edc315cee
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Cold water services installed correctly as per workshop drawings
| checkpoint | Rainwater reuse service s installed correctly as per workshop drawings.
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Supply & install tank top up supply with correct float valve.
| checkpoint | Wastes to be in correct locations
| checkpoint | Floor wastes installed
| checkpoint | Clear out debris from floor wastes
| checkpoint | Tundish points installed as required
| checkpoint | Water services pressure tested @ 1500KPA or 1.5 x working pressure
b948395f-054b-5098-921f-50184dcc5426 | note | Whichever is higher for a minimum duration of 60 minutes
| checkpoint | Coordination with walls and other services overviewed and coordinated onsite.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Garbage Room Work |  | Garbage Room Work | 067bb52a-5577-4f8e-bb13-4cc082da5d9a
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
89e88444-53df-50cb-bb07-fbc460c69905 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
e2a6c8b0-45ac-5738-9add-bb6deca9ef0b | button | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | RPZD valve installed as per AS3500.
ce7d6db2-d20d-541e-aa41-3b8d5c1a1d41 | button | RPZD drain installed and tested. | Yes,No
13b8a6e9-7dfa-545f-8878-2f02afaf4f2d | note | Please attach photo of serial number and valve.
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Gas Connection |  | Gas Connection | ae01ee2b-e199-49be-8b9f-31c0bd2a991d
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per Jemena requirements (attach photos if necessary)
| checklist | Gas Meter |  | Gas Meter | 1fb59216-71cf-4f50-8f1e-61cb657ca0a7
| checkpoint | Arrange gas inspector for inspection and requirements.
| checkpoint | Gas reg to be installed on plinth if external. Install as per Jemena requirements.
| checkpoint | Run breather vents off regulators if installed internally. Pipe size usually 25mm
| checkpoint | Ensure the Gas reg is installed in correct orientation.
| checkpoint | Labelling - 1050kpa, 210 kpa and or 5 Kpa
| checkpoint | Test all pipework and joints for leaks.
| checkpoint | Reg test point to be facing in a direction where accessible.
| checkpoint | Union or flange connection with valves so that reg can be removed or serviced.
| checkpoint | Take photo of serial number and gas meter.
| checkpoint | Arrange gas inspector for inspection.
800a9956-13e1-542c-94bd-a4c2097391bc | note | All works completed to specification/drawings, Jemena standards & Area left clean/tidy
| checklist | Grease Tank |  | Grease Tank | 0d8f181b-952c-473d-bc29-e3e77f181978
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Grease tank installed in correct orientation (inlet/outlet)
| checkpoint | 100mm Chamber vent to atmosphere.
| checkpoint | Trade waste inlet connection.
| checkpoint | Accessibility around tank minimum 600mm.
| checkpoint | Platform installed within room.
| checkpoint | Suction line within room installed. 80mm minimum line, storz adapter and shut off valve.
| checkpoint | I.O's installed inlet and outlet.
| checkpoint | Ensure lids are closed off properly.
| checkpoint | Take photo of serial number and tank.
| checkpoint | RPZD valve installed as per AS3500.
eda02bd1-291c-57d8-a7cd-605ca3efb1e4 | button | RPZD drain installed & tested. | Yes,No
c9c0303d-610b-570c-b065-11a4b59e0226 | note | Please attach photo of serial number and valve.
| checkpoint | Arrange trade waste inspection if required.
1a1fc3d5-f5db-5e32-903e-1b2eedd25e8c | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Hot water flush for trade waste |  | Hot water flush for trade waste | 976eb7b4-0abc-4817-b024-600a3e59b478
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Drainage installed as per AS3500
393352a3-0a5e-5a10-af1f-46467ce0dcb7 | button | Hot water flush installed and commissioned | Yes,No
| checkpoint | 25mm air gap to void cross contamination
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Hot Water Plant & Return Pumps |  | Hot Water Plant & Return Pumps | 9a80707c-d0da-43c0-a578-9b5103da9fb3
| section | Hot water plant
| checkpoint | Installation – refer to installation checklist for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Flue installed as per manufacturer's specification.
a1b6e828-ae7d-5105-9196-f963feec23b2 | button | Power flue turned on. | Yes,No
| checkpoint | Temp relief points ran to tundishes.
| checkpoint | Temperature probe from control box installed into storage tanks.
| checkpoint | Check that an adequate water supply is available to the hot water system.
| checkpoint | Water supply pressure shall not exceed the maximum pressure stated by manufacturer.
| checkpoint | Open cold water inlet valve, hot water outlet valve
| checkpoint | Exercise all valves and ensure correct operation. Ensure all valves are in open position prior turning power on.
| checkpoint | Check the system is fully charged & all air is bled from the system & no leaks are evident
| checkpoint | Ensure hot water heaters and storage tanks are full of water and all valves are open.
| checkpoint | Ensure pressures are not greater than 750 Kpa to the heaters or storage tanks.
| checkpoint | Open all individual gas isolation valves & purge gas lines.
| checkpoint | Test gas pipe work for leaks.
| checkpoint | Check the gas supply pressure at the inlet to the water heater with the water heater and all
| checkpoint | range is NG: 1.13Kpa - 3.5Kpa & LPG: 2.75Kpa - 3.5Kpa
ee6c9674-d226-5e64-92f3-9090b1588979 | button | Clean filters and strainers once after 4 hours of use. | Yes,No
| checkpoint | Set temperature to 65 degrees.
| section | Hot Water Return Pumps
| checkpoint | Hot Water Return Pumps - Installation – refer to installation checklist for hot and cold water.
| checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
| checkpoint | Ensure there is water supply to the pumps.
| checkpoint | Clean filters and strainers once after 4 hours of use.
| checkpoint | Turn on power to the pumps. Set the pumps to alternate.
| checkpoint | Purge pumps of air. Ensure water is visible from the purging points.
| checkpoint | Set balancing valves.
| checkpoint | Inspect system for any leaks or faults.
| checklist | In-Ground Drainage Hydraulic Services ITP |  | In-Ground Drainage Hydraulic Services ITP | 0a18b2e9-f7e8-4455-a963-2c80a85055e8
| section | Sewer/ Trade Waste
| checkpoint | Sewer drainage, Trade Waste drainage and vents installed as per workshop drawings.
2b9a5540-7fe7-570c-b70b-6adb96033986 | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
2d473684-b1ae-533c-842e-956ca77c8280 | button | Pipework risers labelled, pink primer and blue glue used only. | Yes,No
| checkpoint | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults.
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
3bbbb671-363b-5eea-9493-03b252397f4b | note | Ensure compaction of fill materials is to specifications & Australian Standards.
86eacc7b-2809-5069-be64-88811bc30378 | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
| checkpoint | All works completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Stormwater
| checkpoint | Stormwater drainage installed as per workshop drawings.
96bd8581-197f-5b08-82e1-ea4f33af46b0 | button | Minimum Grades, Bracketing and IO's installed as per AS3500. | Yes,No
| checkpoint | Installation of pits to the correct levels.
2475e3f1-ca76-5939-82c4-6e30c40ee4d3 | button | Ensure correct grates & lids used with appropriate load ratings for locations to traffic movements. | Yes,No
b097faeb-1b8e-554f-a2c0-9f4d184c6818 | button | Pits to be sparged - Made water tight to inlet & outlet pipework. | Yes,No
| checkpoint | All pipe risers to be protected with pipe caps & or duck tape.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
518bdbe7-3227-5785-b18f-70bed117b511 | note | Ensure compaction of fill materials is to specifications & Australian Standards.
624b0c8e-0f8c-558c-b2f4-f8a7e7938844 | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
| checkpoint | All Stormwater Work completed to specification/drawings & Area left clean/tidy & excess material stored away.
| section | Handover
| checkpoint | Update As Built drawing immediately - Confirm IL of pipework. Attach with ITP submission.
| checkpoint | CCTV completed pipework to ensure no defects before concrete Pour to prevent future problems.
| checkpoint | Pictures of works completed - Attached below.
| checklist | Inground Pressure Services Installation. |  | Inground Pressure Services Installation. | d9d84a34-04fa-4786-afc4-f50fabc1563c
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
c62903a4-46d0-5185-85f1-da18a643d3f2 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools, welding equipment & deburring machine ready for use..
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
13c7cc2a-7b00-59c2-8c3c-4f7cd924e717 | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
1026c20c-e947-5218-82e2-88f5d8f90ead | button | Witness marks on all press Fittings checked. | Yes,No
9631cf3d-3096-57c2-b9f1-a123fe1788f8 | note | Photograph inspection booking.
| checkpoint | Fire services installed correctly as per workshop drawings.
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
| checkpoint | Backfill trenches with materials as per Australian standards & project requirements.
71cef6c0-798d-55cf-9e09-3de15f9289fe | note | Ensure trace tape is installed
33a63c37-1ffe-5a12-8e10-602c2a4cb3ed | note | Ensure compaction of fill materials is to specifications & Australian Standards.
5f01d6b6-397e-55b0-a3ea-10f6b13c2081 | button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | Yes,No
e73b5677-0532-555d-813e-58abd2e4c966 | note | All services left under pressure during construction.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Laundry |  | Laundry | 7fa7e8b0-4193-40c7-aa4b-60ea84a89533
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
| checkpoint | Pressure and drainage services installed as per workshop drawings and AS3500.
d16c315d-b520-57ad-a924-6567bfb4e77b | button | Thermal lagging as per project requirements. | Yes,No
| checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications.
| checkpoint | Hose taps installed at correct heights.
| checkpoint | Bucket trap or floor wastes installed and grate secured.
| checkpoint | Clear out debris from bucket trap or floor wastes.
| checkpoint | Tundish points installed as required.
| checkpoint | Fit out of cleaners room hydraulic PC items
05fffce4-38cc-5c83-9140-630403c5bfba | button | Commision PC items and set Temp valve to 49 degrees | Yes,No
| checkpoint | All tests completed as per AS3500.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Managers Office Work - Bathroom |  | Managers Office Work - Bathroom | 74c27e08-93d4-490d-a175-16145b4cc626
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
b5faaddf-596f-55d2-9ea7-12b4918e7e00 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
6ecd16c6-7ce7-5db4-8ae1-7bc95bb92f1a | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
860299f8-d910-5eba-99b0-acb4789026d9 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
b14e62d9-52fb-57f6-859b-7a487dc1bfda | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
2f6eaf01-97f0-5305-85ac-7ed44c8c74de | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
6b12c9c4-be0f-5da5-908e-07d39951d40f | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
f3e9a6d2-975a-5697-957d-89fb3390d4f1 | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
090fff10-9f64-5281-a78a-696cb673feab | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
f6cdda20-d84f-50be-a52a-0dde83de36d1 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
31b8edc1-531c-58ea-81a1-4b70a010675a | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Oil Separator Install |  | Oil Separator Install | 89e0ad3e-ca66-41c1-b462-2195cae3b437
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set. Tank to be a minimum 1500mm away from pump.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | Oil Separator installed in correct orientation (inlet/outlet).
| checkpoint | Ensure all items including oil drum are with oil Separator
| checkpoint | Ensure all venting requirements are met
| checkpoint | Take photo of serial number and tank.
3a461702-15fe-5868-9d6e-880e329b44e5 | note | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
| checklist | Parents Room Rough In |  | Parents Room Rough In | 10a841e6-f14d-46e4-b6f4-b8f4bece9167
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
37594a85-8ca7-55c7-940b-80a405cb0f40 | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
fe1f82af-fac9-5cc7-9ccc-5b1c5fb776e1 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
67df085c-0810-55c2-b5f8-058e5962fabc | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| section | Fit out and Commissioning
| checkpoint | Bathroom fixtures installed at correct height/ clearance. Comply with Architectural drawings and Australian standards.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED.
| checkpoint | toilet, Toilet seat's, Cistern and flush button installed and water tested.
d4622edb-7ac1-5394-a25a-86f1fec77220 | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed.
280fd0dc-0f4d-5684-aa86-e03c5f0a5f07 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
54b6bef6-aa41-5e11-a8c2-299bf5166970 | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
e7e20a86-d92a-5734-9026-fdf050218a1c | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | HW heater installed as per drawings and specification, purged and tested.
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
c41ecefd-ae5c-5541-8612-f105702976e0 | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
2e9f102c-2426-5753-beb5-2a8b6f39ab95 | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
9b45fc24-9ca3-5826-a1c5-687c0870b89c | note | General photos, comments & observations during Fit out stage (Add below).
| checklist | Pressure Services Installation |  | Pressure Services Installation | 86bba10a-e98d-4e62-a9df-0130de6d3702
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
c0f340f2-7d84-52ff-972f-c1d1275f2573 | note | Check scope of works/specification & ensure all documents are current.
44db676e-b2c6-5cc8-92a6-b7fbd73c23cb | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
345edf91-90d1-5257-b298-ca215e0ee944 | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
| checkpoint | Fire services installed correctly as per workshop drawings.
21bdeb88-b5a1-5d97-8581-6e61bc796d6c | button | Gal pipe grooves checked with a groove tape. | Yes,No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
b0745ea3-8d4d-59a1-b5b8-ba2a4e2acb62 | button | Pipe spacers installed to avoid electrofusion. | Yes,No
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
eebf01a6-84d6-5305-914a-0ff70f543b8a | note | All services left under pressure during construction.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
b9cb5516-6021-5b85-8855-37e7863f1af2 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards and tested.
| checkpoint | Fire hose reel tagged.
| checkpoint | RPZD valve installed as per AS3500.
7dc4f13e-020f-5d4c-b468-bdff1760263a | button | RPZD drain installed & tested. | Yes,No
78def243-02ef-5216-a14f-1015ead7ef9f | note | Please attach photo of serial number and valve.
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
| checklist | Pressure services on apartments/ Hotel or commercial floors. |  | Pressure services on apartments/ Hotel or commercial floors. | 99a5a303-d0af-4610-8005-14e4060f4928
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
5cef7b60-840f-54a0-b89d-96166fad1f40 | note | Check scope of works/specification & ensure all documents are current.
09b4be86-1880-5036-8712-3bc0533eefc4 | note | Check working pressures & ensure material can cater for those pressures.
| checkpoint | Calibration of crimp tools & deburring machine onsite complete.
| checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics.
7ae0e218-8ade-52e8-a3b8-07a3786b8f86 | note | Ensure to keep separation between NPCW & other services as per Australian Standards.
2367ce80-2ed3-5b86-bc19-24ae6175516e | button | Witness marks on all press Fittings checked. | Yes,No
| checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications.
9b81088f-a45a-543f-8542-189dc02938e8 | button | Pipe spacers installed to avoid electrofusion. | Yes,No
| checkpoint | Water services tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes.
a43aaa04-6942-5e9f-b1fe-b09063373b15 | note | All services left under pressure during construction.
| checkpoint | Isolation lever shut off valves and PRV,s installed.
b1ff144a-582f-5195-bd09-0c98606ff089 | button | Tempering valve or Thermostatic mixing valve installed in the correct orientation. | Yes,No
e7f1ce36-3f8e-5fdb-9a3b-d2f6f1fa3de5 | button | Cold water, Hot water and or meter bars installed and labelled. | Yes,No
a562c128-9fbf-5db9-b28f-a07951dac6e1 | button | Connection of all reticulated cold, hot, Gas & NPCW PEX pipes to points of connections from manifold setups. | Yes,No
| checkpoint | Floor waste grate installed.
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc.
97b7f132-2b95-5a83-80c3-f67b2a0db125 | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | Pipes labelled as per AS3500.
| checkpoint | Thermal lagging as per project requirements & AS3500.
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE).
| checkpoint | Garbage Chute RPZD installed and tested. (IF APPLICABLE).
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary).
| checklist | Project finalisation |  | Project finalisation | e2de959d-e199-414f-8fe3-a631d773e616
| checkpoint | CCTV completed throughout
| checkpoint | Fire doc finalised and submitted
| checkpoint | SSD produced by designer.
| checkpoint | As Builts completed and issued to builder.
| checkpoint | O&M manual completed and sent to builder.
| checkpoint | RPZ test completed and issued to Sydney water.
| checkpoint | DDCV test completed and issued to Sydney water.
| checkpoint | TMV's tested throughout.
| checkpoint | Gas final inspection completed and certificates sent.
| checkpoint | Certification of everything required issued to builder.
| checkpoint | Trade waste final inspection and certified.
| checkpoint | Maintenance manual created and locked in.
| checkpoint | FHR flow test completed and issued.
| checklist | Rainwater Pressure Pump and filtration |  | Rainwater Pressure Pump and filtration | 0b37a89b-2a27-4df1-bfee-e7cd781d831d
| checkpoint | RW pump and filtration installed as per AS3500 and workshop drawings.
| checkpoint | Plinth Poured and vibration mounts installed.
| checkpoint | Ensure all connections are sound and secure.
| checkpoint | Ensure all clips & fixings installed as required.
| checkpoint | Pump and filtration panel to have electrical wired up
| checkpoint | Pump supplier to commission . Purge pump set and set pressures correctly.
c2123be0-fa83-5760-b64f-3010a03a0f7f | textbox | Date of commission
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Roof work |  | Roof work | a9ae6ebe-64fc-4793-99a2-90b729755af1
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
b8f59814-64ec-5347-9ed9-ea3b53cb1063 | note | Check scope of works/specification & ensure all documents are current.
| checkpoint | Builder has overflows installed.
| checkpoint | Sewer vents terminated as per AS3500.
44980fcd-bc3e-5629-897b-35525809f1e1 | button | CCTV of sewer completed | Yes,No
| checkpoint | RWO cleared of debri and CCTV completed.
| checkpoint | RWO grates installed and secured.
f0499058-ed8b-5d48-8458-397643b50baf | note | Ensure protection screen installed so no pebbles block drains
| checkpoint | Pressure services installed.
| checkpoint | Provisions for other services installed. (IF APPLICABLE)
| checkpoint | UV thermal lagging installed.
| checkpoint | All hydraulic works completed to specification/drawings & Area left clean/tidy.
5cb7bc11-2268-5b85-907e-a508787b8ba2 | note | Pictures of works completed if applicable.
| checklist | Set out and Penetration installation (Retail, Commercial and car park areas) |  | Set out and Penetration installation (Retail, Commercial and car park areas) | 0f23efb0-6b42-4817-9394-19075f1c09c5
| checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained.
| checkpoint | Wall Penetrations for pressure and drainage services complete? Installed at correct Invert levels?
| checkpoint | Downpipes with columns installed and capped off with DWV caps ONLY.
| checkpoint | Sewer, stormwater and pressure penetration points installed. Check off Hydraulic plans.
| checkpoint | Cast in services installed at correct grades (as per AS3500) and locations. Check off Hydraulic plans.
22b74fcb-71c8-594a-93a2-80470f667ebe | note | Photograph inspection booking.
| checkpoint | Correct fire collars installed with test reports on file.
a22d4738-f50b-52c3-9b53-2f3463f18765 | note | Hour rating to meet slab FRL.
| checkpoint | Puddle flanges installed for floor wastes and balconies at minimum concrete height stated on structural drawings.
| checkpoint | Car park drains,RWO's , trench drains and risers installed. Trafficable grates to be class D only.
aefceb67-1146-5d89-9d40-87e5ad3c26ce | note | Correct grade of drain to be installed.
| checkpoint | Miscellaneous penetrations installed.
| checkpoint | All pipe risers to be protected with pipe caps and or duck tape.
| checkpoint | Top up water on the morning prior concrete Pour for major casting.
| checklist | Sewer Connection |  | Sewer Connection | c2fac71e-76c5-4984-88ed-bcce58a53052
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Fair trading inspection complete.
| checklist | Sewer Pump Station |  | Sewer Pump Station | 1279b146-fa5c-4143-aaa8-ca62c9880370
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Storm Water Pump Station |  | Storm Water Pump Station | a90776c0-3c31-4537-aa3a-57285913aa06
| checkpoint | Check Tank, Clean and flush out.
| checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY.
| checkpoint | Check all connections are secured and sound,
| checkpoint | Ensure power has been connected to pump set.
| checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision.
| checkpoint | Check for leaks as fill outlet line with water.
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
| checklist | Stormwater Connection |  | Stormwater Connection | afdd0aa5-076e-459d-ad27-b07c13edf292
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checkpoint | Council inspection complete.
| checklist | Tenancy Works |  | Tenancy Works | dd17f22a-5876-4572-ba44-e465e726e9d1
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards.
| checkpoint | Sewer and trade waste Provisions installed in correct locations and capped off.
| checkpoint | Vent provisions and AAVS installed as per documentation and AS3500.
| checkpoint | Cold Water Gas Point Provision Installed in correct locations and capped off.
629088ec-ceff-51b3-a949-33a99ea6a256 | button | Sydney water meter installed if applicable. | Yes,No
| checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE)
| checkpoint | CCTV all lines to ensure clear
| checklist | Variation |  | Variation | afc3ef96-b93f-4333-b4d3-cf454f1caa41
| checkpoint | Variation Details Approved
314db6d5-8009-5a8e-b1a0-fe9b0cae797f | textbox | Reference/Drawing/Instruction Number
71435da6-2fd0-5587-b492-2731a8a9f8e3 | textbox | Variation Area
672cfe03-c10f-5a8c-828b-64dbe51dbebf | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
| checkpoint | Variation Completed
| checklist | Water Connection |  | Water Connection | e91b1d7e-59c3-4b63-b170-88b31915aad2
| checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required.
| checkpoint | Services scan within area completed
| checkpoint | Opening permits from authorities complete. Traffic control booked in.
| checkpoint | Non destructive excavation if many services are within the footpath or road.
| checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary)
| checklist | Water Meter Install & RPZD |  | Water Meter Install & RPZD | 4cff4de2-a07e-463d-9aca-263a97b253e9
| checkpoint | Water meter installed as per Sydney water guidelines.
| checkpoint | check for leaks and also bracketing as per AS3500.
| checkpoint | Take photos of device & ensure to get all serial numbers
| checkpoint | Test & commission device as required by certified persons
| checkpoint | RPZD valve installed as per AS3500.
82b37660-b036-57d4-a570-18a8b211f6f8 | button | RPZD drain installed & tested. | Yes,No
da267a46-6382-5df8-9965-a2c6c6c60d6b | note | Please attach photo of serial number and valve.
| checklist | Water Storage Tank |  | Water Storage Tank | 1b17017b-42d3-4e0e-8322-4559af2e8a7e
| checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved.
| checkpoint | Slab or plinth Poured and waterproofed.
| checkpoint | Tank installers to install tank only.
68fc8854-cf8e-5daf-9ce3-33c42ba0445b | button | Tank supplier issues certificates and authorisation to fill tank. | Yes,No
| checkpoint | All valves, overflows , tank top up and sludge drains installed to tank.
| checkpoint | Fill tank up in 500 mm increments. Inspect tank for any leaks and continue till you reach desired level design.
| checkpoint | Dump tank and ensure sludge drain and pipe work is operational.
| checkpoint | Set float valve as per manufacturer's specification.
| checkpoint | Once tank is commissioned book in Chlorination by tank supplier.
| checkpoint | Tank level indicator installed and connected to BMS
| checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)