## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | Apartment / Hotel |  | Apartment / Hotel |  | b040c888-dfc8-4c03-bbcc-9057b1dc2764
| section | Rough In
| checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans.
b9998647-e221-5a69-a076-77b228b4128a | note | Check scope of works/specification & ensure all documents are current
| checkpoint | CW,HW,WW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and schematics
| checkpoint | Check for any cross connections.
| checkpoint | Balcony gas bayonet or water taps installed as per AS5601 and AS3500. Check foothold requirements
| checkpoint | Basin wastes and toilet waste offset and tested with water if required.
| checkpoint | Internal cistern installed and tested. Ensure cistern is installed as far forward.
| checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward.
| checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications.
511ec95f-3e53-5e56-82d7-e44d280e35d1 | button | separation of services as per AS3500 | Yes,No
| checkpoint | All setouts ok and run eyes over crimps
| checkpoint | HOLD POINT - Inspections if required by relevant authorised persons.
| checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own.
| checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes
| checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc
903d117e-83b3-58dd-a19d-fc39f572527e | button | Smoke seal applied to all penetrations required. | Yes,No
| checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy
| section | Apartment Fit Off & Commissioning
| checkpoint | Bathroom, Kitchen and Laundry set out off current Architectural drawings.
| checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED, Laundry,bathroom, ensuite and balcony.
| checkpoint | Kitchen mixer and sink installation complete.
aeb2d544-ff61-5608-b39a-883051160c21 | button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexi & trap and check mini cock for leaks. | Yes,No
b40aa3dd-6fb7-5083-b190-ef1899f21a93 | button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes,No
| checkpoint | Dishwasher installed with hoses, Power lead not kinked and dishwasher plum. (cover plate for hoses must be installed)
78de3ef8-c4bd-5eaf-87f0-b24e7159512e | button | Run full dishwashing cycle and inspect for faults. | Yes,No
| checkpoint | Cooktop installed and power plugged in.
4ccfdca0-9c60-5f8b-90b8-ac4a523ac036 | button | Once gas is on, purge gas safely and ignite cooktop for its operation. Confirm yes once complete. | Yes,No
a605e4f6-4c23-57b1-833d-2248e53e63eb | textbox | Hot water delivery to kitchen sink.
| checkpoint | Laundry tub and mixer installed?
a41a5f5b-12db-5580-9685-183da902a527 | note | Tub door to swing the correct way.
827f9631-1a8b-50d5-910e-4a2a4f662db3 | button | Clean aerator, Remove Trap & Clean Out (Tighten Trap) & Test Floor Waste - Clean Out | Yes,No
3005fcb2-38a7-575f-9a96-67078f6e7698 | button | Laundry mixer solid, check for cross connection, run tap, tighten flexi & trap and check mini cock and trap for leaks. | Yes,No
ea11b372-b23c-504f-ae94-74618de8faa6 | button | A/C Tundish(Cap if there is no Tundish by AC). Ensure 25mm air gap achieved. | Yes,No
b17063b9-ee5c-584c-939b-eddfaba7eed8 | button | Washing Machine taps Installed Under Tub/Opp Tub, cover plates installed and AAV installed if applicable. | Yes,No
| checkpoint | Toilet, Toilet seat's, Cistern and flush button installed and water tested.
218c9f52-28a0-5c28-8b04-f0aa211e66dd | button | Flush toilet 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes,No
| checkpoint | Basin mixer and basin installed. (photo)
80e0f647-3952-5616-8641-319f9f411453 | button | Basin mixer solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes,No
a9e8af0d-855d-5424-87e8-1bef9fa438ef | button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes,No
| checkpoint | Shower mixer cover plate/handle and shower rail or rose installed.
9d2b370e-67ca-5d2b-aab9-2d508aa9105e | button | Run Shower for 15 min, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
d3ab7a81-d946-579e-b24d-8e83455bb020 | textbox | Hot water delivery to Shower.
| checkpoint | Bath installed, Cement grouted in, fill tested and water tested for any pipe or plug and waste leaks.
| checkpoint | Bath mixer cover plate/handle and bath spout installed.
7a0bcf21-7fcf-533f-86a8-4050c5c0251e | button | Bath fill test and water run test, inspect for cross connections, floor waste blockages and ensure aerators are cleared. | Yes,No
| checkpoint | Balcony drains clear, overflows in place?
| checkpoint | Balcony gas bayonet and or water taps installed as per AS5601 and AS3500. Test for leaks and operation.
| checkpoint | Gas valves tagged, CW meter installed and tagged, Hw meter installed and tagged and NPCW installed if applicable.
| checkpoint | Gas Tested with Manometer - on hold for 10 minutes. Ensure absolutely no leaks!
| checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250 kpa or more than 450 Kpa (clear filters)
| checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters).
64c29fc9-71e1-5d07-ac4f-d086c47cb21c | button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes,No
ed8cd412-11f7-5118-9ad4-b8299c748bff | textbox | Pressure Reading and temperature within apartment or hotel.
| checkpoint | All Fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary)
f77937fd-d8c2-540d-85d4-c4f16d0441bf | note | General photos, comments & observations during Fit out stage (Add below).