## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
1707a231-9c5c-4aaa-99a5-2c3f6b0bf8b4 | checklist | 35.18.1 SPWB Trenching Works |  | 35.18.1 SPWB Trenching Works |  | e6909865-cb55-48d6-be7e-a863bc0073cc
bc7c653e-19d9-4347-9aeb-45e04373c9ce | section | Form 35.18.1 SPWB Trenching
0ecab601-705a-4e61-9cc7-c19677447736 | checkpoint-no-value | Details
01d1372c-1450-5e85-8fad-38d77ca748de | textbox | Lot
706acd9a-31d8-52b9-bc2d-b1044604247f | date | Date of Works Commencement
d59b5141-c209-4e4d-8325-9a38a357d4fa | section | Pre Construction
4447150d-1b61-4400-becb-21577da5cb6b | checkpoint | Dial Before you dig completed and understood? This is a Hold Point.
198a11bb-234d-4a85-a12d-acb73e4a82d7 | signoff | HOLD POINT
5910e9ca-5ff3-464d-9c50-1fc9f906706c | checkpoint | Are there any Services
5186b1ca-cc11-4c3d-9c5c-63243f9e9dd2 | checkpoint | Survey Setout for portion of the works completed. Hold Point
7461ffd8-48fa-46c5-9ea1-b0ca5fc421f9 | signoff | HOLD POINT
9b4470eb-c70e-4a3c-9408-083f69516749 | checkpoint | Tree Protection in place. Hold Points X3
e52170fd-b72c-4ab8-a223-65b17a32493e | signoff | HOLD POINT
469e9122-eb85-4033-9d44-6a024c0a6835 | checkpoint | Excavation Permit Completed
5b78aa7b-f3e0-46ea-acae-ec3b6b0db545 | section | Construction
cbf33034-2696-4d4c-a0a5-90f56c1c371b | checkpoint | Preliminary Approvals Completed. Site Engineer check
5c9df9f6-d117-40ae-89ee-3932d4c26f3d | checkpoint | Clearing & Grubbing completed. Hold Point to inspect cleared Site
09820c21-fd8d-4db8-8c4b-87609659e3bd | signoff | HOLD POINT
bed8a912-4f15-4cfd-80ed-638588e6bc6a | checkpoint | Topsoil Removed
809d7086-c81c-44c2-8071-a24daf1aa526 | checkpoint | Location of Vertical bores marked
a2d22b7d-f4ee-433f-b768-4f4054083d5b | checkpoint | Trench Excavation Completed
aff5095b-1e6f-4236-b52b-cd6b4a344793 | checkpoint | Depth of Trench Every 10m Over 100m Lot
f7d26228-121b-59d9-81a0-1d0225a63541 | textbox | 0-10 (Meters)
cfb079a2-41d8-5062-8310-bd5265a85e31 | textbox | 10-20 (Meters)
35c775fb-e248-5469-8737-e9e030a3f012 | textbox | 20-30 (Meters)
32ef87d9-1d80-534b-a470-ddebff9f90a4 | textbox | 30-40 (Meters)
68c060a8-6f01-59e0-a4d8-a2fec4fe1698 | textbox | 40-50 (Meters)
f29ff198-05bd-53d1-bde9-b7d62b646b2c | textbox | 50-60 (Meters)
fba9abe2-0a30-55ac-bea1-176f868013fb | textbox | 60-70 (Meters)
59713e25-bc2c-5ddf-b744-e5b4bac460ff | textbox | 70-80 (Meters)
c66a7a05-0d37-57dc-aaa6-8b732659ca18 | textbox | 80-90 (Meters)
b8ba37ef-5a46-524b-9a93-41ccb0f1b2dc | textbox | 90-100 (Meters)
5745e4d8-f8de-420f-b3a6-242dad558aa7 | checkpoint | Excavation Sign Off (Hold Point)
c87c202b-61b6-4422-a7ac-6c058aac2cec | signoff | HOLD POINT
991a42b9-cb25-4e55-bbf9-557a82c7973e | checkpoint | Sleeve placed for Vertical Bore
16813735-2ada-4e97-8fe7-db3aeb52acc6 | checkpoint | Trench backfilling with coarse gravel (>40mm) to design height of trench pipework? Hold Point (check against Design Height Register)
4aef6c39-0c6c-4daf-bba1-d08c02c5f691 | signoff | HOLD POINT
3bcaaba6-41b5-4cb3-863d-b3f1ed07d02b | checkpoint | Gravel Sign off prior to pipework (Hold Point)
c8a47acf-ae53-44e3-bd59-0f1d039c5a66 | signoff | HOLD POINT
8dc9179b-e6c5-41c4-8116-875f2ed25b43 | checkpoint | Vertical Bore ITC completed?
4b701f47-46e2-403f-aeac-8d3c0f5a49aa | checkpoint | Inspection of completed Gas interception Pipework. Hold Point
0dcbbca7-0a44-4e0b-a7a1-c69a7d3d7331 | signoff | HOLD POINT
6d09533f-694f-4135-a306-e0ac4083eec4 | checkpoint | Pipe Work Sign Off (Hold Point)
3bdfbd24-898a-4e07-ad95-3d142edd12f5 | signoff | HOLD POINT
bd05ecf3-0a99-4996-837e-2d43b6106bf2 | checkpoint | Trench backfilling with coarse gravel (>40mm) to finished design height. Hold Point.
880f1862-e47a-464a-aa3c-d238a1b772f3 | signoff | HOLD POINT
eb58953c-8608-41d0-a7d7-10c9091b3194 | checkpoint | Completed Gravel Sign Off (Hold Point)
208b6496-b9de-427b-a4e8-d978f5d60406 | signoff | HOLD POINT
8dccdd8e-574a-47dd-9b81-23479fab6860 | checkpoint | Testing of Coarse gravel. Plan with Site Engineer.
1761e615-00f3-4199-88c4-5522cd464fdc | checkpoint | Installation of vertical risers. As per jointing methodology with Site Engineer.
db2ea843-274f-4357-b05e-274f35952854 | checkpoint | Geotextile installation completed. Hold Point
91a239a3-c593-4ac9-a95f-3034b648add2 | signoff | HOLD POINT
4dbb535b-9895-40e2-a28c-52f9807d8560 | checkpoint | Geotextile Sign Off (Hold Point)
335e6b0c-e210-4c4a-8011-1829b4dc9fdd | signoff | HOLD POINT
6cea3e05-fd97-48cc-b1fe-fbc97eda7387 | checkpoint | Survey completed for top of coarse gravel. Hold Point
d1a8b3be-9c64-4f36-9488-4a371d517559 | signoff | HOLD POINT
d808aae5-8689-4a6e-8cad-692bf034f4f6 | checkpoint | Survey Sign off
7d5b5c3f-6e61-49bc-8a12-3e0fd4ff14d4 | signoff | SURVEY Sign off
6a645e46-3470-446a-b499-1c6953fb5eb6 | checkpoint | Placement of capping material completed.
acf8eee8-90a0-4914-a8ff-821741eb7f1d | checkpoint | Testing of capping material completed. Refer to Testing Plan.
0274f5e6-89ea-449a-9065-0e8836b1ac5d | checkpoint | Survey of capping material.
5e9b09fc-91e5-49b4-ad06-82e25d01bcec | checkpoint | Capping Sign Off (Hold Point)
80951d67-d6d9-4ec2-8fda-72a8e60b6a8c | signoff | HOLD POINT
2d32225e-300a-44f9-9078-0868bb046603 | section | Daily Log and Notes from Trench Work
0bd40c25-509e-4a6e-8754-7b3ba16436eb | checkpoint-no-value | Details
a397e23d-e1d6-5c08-8398-dfd43a9e784c | number | How Many Days of Excavation per Lot
de45f1a4-ccea-42a7-a0b2-78d6fa63153a | checkpoint | Was there Weather that affected the trench
| checklist | Appendix A1 - Earthworks ITP | itp | ITP - Earthworks |  | 9a77da35-3033-44f5-ba97-1b4cc3c2e0c2
| section | 1 - Site clearing
| checkpoint | Area to be cleared Depth of grubbing, Removal of topsoil
df8b5a6f-482f-55a1-8bf4-800bb33b8d0a | note | STANDARD/REQUIREMENT - Refer to construction drawings
cb4b67bf-bda3-5ccf-8370-64fc94a37335 | note | ○ Approved method statement
d1bc8c71-9d92-527a-96a7-ea111b7fcb8c | note | TOOLS/EQUIPMENT - Survey equipment Tools to measure depth
1aca2537-66de-580f-ae2c-d6992711bc6f | note | STAGE/FREQUENCY - Entire site
35af0500-217e-57bb-bebc-23b848091606 | note | RESPONSIBILITY - Contractor
eb364ca5-74e7-59d4-b092-0f2eb29ecd07 | note | EVIDENCE - Setting out plan Survey plan
| section | 2 - Excavation
| checkpoint | Dimensional tolerance (depth)
5b4100d9-d872-525e-b958-356d8f893107 | note | STANDARD/REQUIREMENT - Width < 300mm than the dimensions shown on the drawings
0f1771b1-e2a9-56f6-a845-22664b5eb7d6 | note | TOOLS/EQUIPMENT - Tools to measure depth
56a8f12b-60b6-5d55-a8a3-ac1c75cea33d | note | STAGE/FREQUENCY - When required
d119ce2f-e717-5201-88c4-b5582c0644e5 | note | RESPONSIBILITY - Contractor/ Project Manager
85c637c7-1693-528a-b1e2-1854a35bf1a6 | note | EVIDENCE - Survey plan
| checkpoint | Unsuitable material (If any)
c0d071cc-570a-5dd2-90ec-acdad86f1cc7 | note | STANDARD/REQUIREMENT - JKR/SPJ/2013-S2: Clause 2.2.1 (d) or JKR 20800-0183-14 Section B Cl. 5.2.3
b2a2c9ec-b487-5cc1-bd36-dab593043716 | note | TOOLS/EQUIPMENT - Trial pit
1402b521-b26e-5283-98d2-051913c370dd | note | STAGE/FREQUENCY - When required
43147bb9-8788-5c64-9969-83a617a73c9a | note | RESPONSIBILITY - Contractor/ Project Manager
7e5b227d-4c56-51f2-9297-1752ffa03a5e | note | EVIDENCE - Material laboratory test
| checkpoint | Grading of replacement materials
2a24057f-0e1b-5254-955e-4daec1e188a0 | note | STANDARD/REQUIREMENT - JKR/SPJ/2013-S2: Table 2.1 or JKR 20800-0183-14 Section B Cl. 5.7, Table B1
160564d4-e2c4-5848-bc66-cd566ce5f7fa | note | TOOLS/EQUIPMENT - Particle Size Distribution (Gradation analysis)
1207ede1-9900-5624-88dd-1f803d964619 | note | STAGE/FREQUENCY - When required
e63148b3-87d3-5a3e-896f-3400890a9398 | note | RESPONSIBILITY - Contractor/ Project Manager
a4f38773-9b20-5a4c-9055-ddda8395800e | note | EVIDENCE - Material laboratory test
| checkpoint | Excavation of hard materials/ rock
2e3e376d-3055-5b2c-9f35-3dd4bf5a5090 | note | STANDARD/REQUIREMENT - JKR/SPJ/2013-S2: Clause 2.2.1 (f) and (g) or JKR 20800-0183-14 Section B Cl. 5.2.5,
98eb4235-6d2e-5036-ba0a-a4527dae9181 | note | TOOLS/EQUIPMENT - Trial excavation
9baed192-2b9d-53d9-917e-781644d6c5cd | note | STAGE/FREQUENCY - When required
c12f0c55-c356-5338-a84a-e2893c261c59 | note | RESPONSIBILITY - Contractor/ Project Manager
2a603903-4a0d-54e2-9d08-ab02d527d122 | note | EVIDENCE - Trial excavation record
| checkpoint | Rock blasting
e6adc855-87e0-5028-b662-41c227b410f1 | note | STANDARD/REQUIREMENT - JKR/SPJ/2013-S2: Clause 2.2.3.8 or JKR 20800-0183-14 Section B Cl. 5.1.2
177c469a-1687-5c4f-8f65-e1abb7a432a0 | note | TOOLS/EQUIPMENT - Trial blasting
abbc7252-24b2-5082-a82f-8a0b10c0f1e1 | note | STAGE/FREQUENCY - When required
b9b9caf5-ef58-58dd-b113-64e002cfb2dd | note | RESPONSIBILITY - Contractor/ Project Manager
da66d564-abe1-5d34-a9f1-d60b972200c7 | note | EVIDENCE - Trial blasting record
| section | 3 - Fill materials
| checkpoint | Suitability of materials (1)
ef590eaa-de68-5bc7-8a54-772399b62676 | note | STANDARD/REQUIREMENT - JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205
66cef0f8-2099-5e77-81e4-7109f9f38dff | note | TOOLS/EQUIPMENT - Atterberg limit test
ed8ba0b7-c2e2-5d1d-bc06-1a81931101f8 | note | STAGE/FREQUENCY - One test/ 1500 m3 of the material to be used
857bc559-c129-547b-a824-143a992aedc5 | note | RESPONSIBILITY - Contractor/ Project Manager
364da8bf-22f4-5e81-816f-4818a14c2e46 | note | EVIDENCE - Material laboratory test
| checkpoint | Suitability of materials (2)
32d36692-0e61-58d2-8017-242c70ddb461 | note | STANDARD/REQUIREMENT - JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205
4e43c2e6-3640-5977-814f-781dc2615327 | note | TOOLS/EQUIPMENT - Gradation analysis
46c971f3-5e08-5312-ab2a-7d9b736e0f6c | note | STAGE/FREQUENCY - One test/ 1500 m3 of the material to be used
9f6042c4-43e9-5d61-ab3a-6a9934f318bf | note | RESPONSIBILITY - Contractor/ Project Manager
c675b83b-f98e-5cf7-8259-646c1d99c594 | note | EVIDENCE - Material laboratory test
| checkpoint | Suitability of materials (3)
e5dc96c2-b15f-5c6b-88f0-19092f42687d | note | STANDARD/REQUIREMENT - JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205
8644730d-b639-50df-93ef-eb9f33a6b667 | note | TOOLS/EQUIPMENT - Compaction test (MS 1056)
fab3731f-5c1c-5942-a945-09d072a40fc9 | note | STAGE/FREQUENCY - One test/ 1500 m3 of the material to be used
868e1cb0-fcc3-5b2e-ae85-b78e00d9add7 | note | RESPONSIBILITY - Contractor/ Project Manager
6a93ac9f-35d1-5653-8d37-4856388ab870 | note | EVIDENCE - Material laboratory test
| checkpoint | Suitability of materials (4)
e7a04a42-15c9-542a-8b37-4324a4599f40 | note | STANDARD/REQUIREMENT - JKR/SPJ/2013 - Cl. 2.2.4.1 and 2.2.4.2 or JKR 20800-0183-14 Section B Cl. 5.2.4 or Federal Aviation Administration (FAA) AC 150/5320-6E CI 205
3202479b-9685-516b-973e-5275015ce226 | note | TOOLS/EQUIPMENT - Soaked CBR test
3c7bce0e-0a3c-5520-bb35-aafe773c8242 | note | STAGE/FREQUENCY - One test/ 1500 m3 of the material to be used
15ddee7b-2d86-5636-ae4b-273254f317a7 | note | RESPONSIBILITY - Contractor/ Project Manager
ae074236-cc68-58e3-868b-73fe03a3979e | note | EVIDENCE - Material laboratory test
| checkpoint | Suitability of materials (5)
ad77fc0d-7ac0-5622-91e2-22dca13b619f | note | STANDARD/REQUIREMENT - Federal Aviation Administration (FAA) AC 150/5320-6E CI 205 & ICAO A. Manual Part
60a80963-c90a-55f2-88e9-f927eb578f34 | note | TOOLS/EQUIPMENT - Plate Bearing Test
ad24b05c-c324-5ec3-b493-1ed2fdbd9f79 | note | RESPONSIBILITY - Contractor/ Project Manager
26af3b73-535e-5eb3-9777-67997d5834dd | note | EVIDENCE - Material laboratory test
| section | 4 - Slope Cutting
| checkpoint | Area to be cut and trim
f4fdb17d-9ee2-5ea4-86fe-351b9af1f250 | note | STANDARD/REQUIREMENT - Refer to construction drawing
6bf5f5ee-6573-50bf-979a-12ba31e3e71c | note | TOOLS/EQUIPMENT - Survey equipment, Measuring tape
1ec57a18-5617-5ad0-9832-2dd224098330 | note | STAGE/FREQUENCY - Before slope cutting
792b3e89-19e6-58e2-94af-d49da7742d3d | note | RESPONSIBILITY - Surveyor / Contractor
0722ccb7-41fc-578e-885b-702347e1e157 | note | EVIDENCE - Setting out plan, Surveyor peg point
| checkpoint | Safety Precaution
9a3aabb2-1520-5d05-bcc6-ba9226318e65 | note | STANDARD/REQUIREMENT - JKR specification for occupational safety & Health in engineering construction
69160b70-1a52-59db-8052-88472b3e18b6 | note | TOOLS/EQUIPMENT - Visual checking
a7c8ef81-40eb-52dd-a50e-cef2b62aa3da | note | STAGE/FREQUENCY - Before slope cutting
9a52e403-4d1c-5c3e-8c48-8eaa125bac06 | note | RESPONSIBILITY - Contractor
| checkpoint | Excavation
0bc0c4bf-cbeb-5d6a-9fd1-579d32f529e8 | note | STANDARD/REQUIREMENT - Refer to construction drawing
43a73325-66c9-5ecf-8062-ddb124c61342 | note | TOOLS/EQUIPMENT - Survey equipment
c5adc0a6-f5b3-5284-bfa4-0d1efe3d61e8 | note | STAGE/FREQUENCY - Once slope cutting completed
8f558548-a111-5e0d-a486-950bf6720daa | note | RESPONSIBILITY - Contrator / Surveyor
65f33a0d-3154-5f4b-a8eb-9fabff40b26c | note | EVIDENCE - Request for Inspection Form
6382f4db-70a2-530e-a527-755d0b3248f7 | note | REMARKS - Ensure nobody or property at the downstream of slope cutting
| checkpoint | Dimension / Level / Line / Profile
766b8296-b1b5-5f20-a5fd-bb6cdce5f4d9 | note | STANDARD/REQUIREMENT - Refer to construction drawing
a25048ea-7918-5f53-8b6b-12c0772e335e | note | TOOLS/EQUIPMENT - Measuring devices
99b67442-099d-5798-843b-7ad7a2a37888 | note | STAGE/FREQUENCY - Once slope cutting completed
2592aea4-ad66-5d20-9d4b-932b898728da | note | RESPONSIBILITY - Consultant
8b3df2be-ce41-5d8e-b36c-188b116d891e | note | EVIDENCE - Request for Inspection Form
| checkpoint | Compaction
678d16e1-b956-53e3-a1a4-a56fdbd099c1 | note | STANDARD/REQUIREMENT - Refer to construction drawing, Visual inspection
82d960af-fd92-5670-8d40-deeffcdf58dd | note | TOOLS/EQUIPMENT - Excavator
41829e8b-46e8-52c9-818f-7090d3e55e48 | note | STAGE/FREQUENCY - Once after work completed
a4de4b4f-2d7d-5c9c-ab52-543c6ffb59d1 | note | RESPONSIBILITY - Contractor / Consultant
7477d9c6-dfbc-5eea-95ef-9f4863567730 | note | EVIDENCE - Request for Inspection Form Compaction record
| section | 5 - Drainage
| checkpoint | Drainage route
572d9612-efd2-5f1a-8402-6c8b2c117a5a | note | STANDARD/REQUIREMENT - Refer to construction drawing
a61796f5-7672-59af-ba6b-c93f80340013 | note | TOOLS/EQUIPMENT - survey equipment Measuring tape
e63a2c40-f188-5ee4-9721-1687ae1e2cdd | note | STAGE/FREQUENCY - Before start work
621f6114-dfde-59c9-a8ae-45362263cec8 | note | RESPONSIBILITY - Surveyor / Contractor
52d0a515-7518-5753-89fc-6b2158b08408 | note | EVIDENCE - Setting our plan
| checkpoint | Drain excavation and Slope alignment
6dd8b665-1951-5233-9cb6-f487a2f71e77 | note | STANDARD/REQUIREMENT - Refer to construction drawing
67fc14a3-d75c-57a1-8801-618ec31c95c7 | note | TOOLS/EQUIPMENT - survey equipment Measuring tape
e3676f46-8065-5fe2-bd9e-3e699f74274b | note | STAGE/FREQUENCY - Before start work
c97a288d-883d-50d5-ac8c-024d69cebbba | note | RESPONSIBILITY - Surveyor / Contractor
f43e294f-bc24-5b4c-8ee2-9b0f819d2296 | note | EVIDENCE - Setting our plan
| checkpoint | Drain invet level
53acedb0-6f64-5a5d-b5e2-7a5aedcb142b | note | STANDARD/REQUIREMENT - Refer to construction drawing, Site Layout plan
6cee8939-f960-5fef-82ff-51af441176d6 | note | TOOLS/EQUIPMENT - Survey equipment, Level measuring devices
22128db9-ed5b-5c8c-a375-60b1ccc3aedd | note | EVIDENCE - Request for Inspection Form
| checkpoint | Belian pile
cb713857-8e13-5e2d-b62b-996ef2a948da | note | STANDARD/REQUIREMENT - Refer to construction drawing
94639fe8-63c4-5618-8568-c66ad1658b43 | note | TOOLS/EQUIPMENT - Excavator Measuring tape
b7e7bd85-e8bb-5948-a8c0-1f4076dc728c | note | STAGE/FREQUENCY - once during piling work
16d889f9-291b-5167-9f07-237e9b380b7b | note | RESPONSIBILITY - Contractor Consultant
9fbdb40a-7927-5b1b-86fb-892cdce8b4d0 | note | EVIDENCE - Pile Material inspection form Request for Inspection Form for piling work
| checkpoint | Cutting and bending of steel reinforcement
498f25fc-ce75-5a9c-b833-c47ae825f35e | note | STANDARD/REQUIREMENT - Refer to construction drawing BS4449
6be5da25-75a0-56ec-b472-1b6f57cc0b87 | note | STAGE/FREQUENCY - Before fixing concreting
e60e4ab7-0df0-58c6-bbb6-66ee4eea8d83 | note | RESPONSIBILITY - Contractor
| checkpoint | Fixing of steel reinforcement to formwork
1ac6a498-6ddd-5290-b08e-18829ae68f80 | note | STANDARD/REQUIREMENT - Refer to construction drawing
fbd71c48-ac49-5f44-bef0-629b6bc2c826 | note | ○ Comply design concrete cover Comply design drain width and depth
803314c8-8d65-59e6-a5b5-b0fe44f83cdc | note | TOOLS/EQUIPMENT - Measuring tape
9c349815-9833-5db1-a205-6c5345a923c4 | note | RESPONSIBILITY - Contractor / Consultant
1164c3de-787e-5fb5-8273-1800da4d96ee | note | EVIDENCE - Request for Inspection Form
| section | 6 - Slope Protection
| checkpoint | Preparation of site Compaction
5ed9d3e5-520b-5d96-a870-eeb9c906eb65 | note | STANDARD/REQUIREMENT - Refer to construction drawing MS1056
a41d89b4-f1ec-51c0-81ca-ee6b608e6287 | note | ○ SO approval
3ad4161d-eddd-5727-ac93-f5d60f208947 | note | TOOLS/EQUIPMENT - Compaction and CBR test equipment
75ad352a-2868-5b95-85ea-b51b3b2f371f | note | STAGE/FREQUENCY - once upon work done
4c649b1a-bf78-5d98-a177-b884369fc074 | note | EVIDENCE - Request for inspection form
| checkpoint | Placement of Gabions Material
20699e30-f353-57be-9708-4d6ad1ceb8ed | note | STANDARD/REQUIREMENT - BS1052:1980
4781b7fc-a34d-5619-9dd8-d90fe1bcc124 | note | ○ JKR/SPJ/1988 sub-Section 3.6.2.1
a7e0e7be-8fdd-5015-8f14-436317322ecb | note | RESPONSIBILITY - Contractor / Consultant
a14371b4-85d0-5a58-83a0-e3a4b21574e2 | note | EVIDENCE - Material inspection form
| checkpoint | Installation of Gabion
509d8b77-f721-5b9a-9a70-7f342a6c545a | note | STANDARD/REQUIREMENT - refer to construction drawing
dea1e87e-148e-58af-85cc-37c789ab62f5 | note | RESPONSIBILITY - Contractor / Consultant
9c3aa55b-5e3f-5d7a-a0e1-d3f2a9691c44 | note | EVIDENCE - Request for inspection form
| checkpoint | Stone
1f22e6ad-7ed0-5309-ac3d-650dbc50e433 | note | STANDARD/REQUIREMENT - refer to construction drawing
004affe6-76f1-5d37-bed7-29184741e7d0 | note | RESPONSIBILITY - Consultant
ac46c184-9015-5ae2-acb3-12afc64a8e2d | note | EVIDENCE - Request for inspection form
26110dc7-388e-4486-9102-521084911bd7 | checklist | CC515-ITP-18a - SPWB Ventilation System Pre Construction Works Rev1 | itp | CC515-ITP-18a - SPWB Ventilation System Pre Construction Works |  | 385484f4-7f1d-4a64-9b08-90a835489a37
435d5f71-9792-435c-86fe-5f895b648b62 | section | Pre-construction
76e9fd19-73bc-4078-b64e-332fa1e902d9 | checkpoint | 01 - SPWB Ventilation System
ad4b98eb-073a-52d0-b027-e4c0da9ace0f | note | Type - Document Submission
16fc7f54-22a4-56fd-86aa-b11863645765 | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs Table 4
a189e88f-969e-5b4c-833c-b438cefb1e62 | note | Clause Title - TransGrid approvals
e163c235-542d-5195-802e-1cd246213a8d | note | Requirement - Provide copy of approval to Principal
ae6a6395-c59e-5ce9-930f-6f3487d94cfc | note | Notice for Inspection - Prior to work commencment
b47b2d39-c22c-56b2-98c1-927928ccdb7e | note | Lot Sizes & Test Frequency - Contract
24af8440-2558-575e-8372-028620c161b0 | note | Release by - Complex Co
b22e5710-46ca-4ada-8d35-1fa6d0ee9e11 | checkpoint | 02 - SPWB Ventilation System
1e7654be-a7fe-52bb-9918-a38d5dcdd4e8 | note | Type - Surveillance
c0209909-ceab-5e53-8077-4a5fa074287c | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs Table 4
aaf7955d-e9b6-5d68-9b9e-ec977f70e026 | note | Clause Title - Clearing of vegetation along alignment
ca29de5b-c1b3-5ae6-8104-a395ca9b82d0 | note | Requirement - Provide copy of clearing approval to Principal
9af37909-2c21-5646-8446-5bc335c86cf3 | note | Lot Sizes & Test Frequency - Contract
ec3b514b-b08a-5dfe-97cd-2e1e184ce6ea | note | Release by - Complex Co
fe391dd9-0ae5-42c5-839e-875e116b652f | checkpoint | 03 - SPWB Ventilation System
816ef178-4676-54e6-89a3-998825908b34 | note | Type - Survey
26098d0d-3659-5781-893c-a91e9611a56a | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs Table 4
c6840766-bc2f-525d-b48e-3231785fb5c4 | note | Clause Title - Survey of lateral extents of alignment
ab7feeba-4739-522e-9b9e-e81add714a87 | note | Requirement - Provide copy of survey report to Principal/Environmental Engineer prior to commencement of trench excavation works.
91db1cd9-b685-56de-b74c-c8f20f28a8b1 | note | Lot Sizes & Test Frequency - Contract
171832ff-81e9-5bd3-947c-a176ee5d5b69 | note | Release by - Complex Co
f5051a0e-e115-46a5-9084-3665925c14b1 | checkpoint | SPWB Ventilation System
42e41f84-dcc9-52ee-a406-d574b67a5927 | note | Type - HP
7c661957-6a87-5bd7-861a-c24ec7eff19a | note | Applicable Standard / Specification / Reference - MITS Specification Clause 1.2.9.1 OA.3
21637c2f-b216-59d5-9140-f773e3c44c5b | note | Clause Title - Utilities and Authorities – Existing services
b9fca959-6323-5384-8a79-c18312c1305a | note | Requirement - Before starting earthworks, locate and mark existing underground services in the areas which will be affected by the works including clearing, excavating and trenching.
7fa28aa3-01c6-5af9-9ec2-d33dd21cee08 | note | Notice for Inspection - 1 working day before new work
76acbe0e-03d3-5da8-990c-77705dac75df | note | Lot Sizes & Test Frequency - Site
53ad41d2-cfc6-5d04-85ff-d7663ac551a6 | note | Release by - Authorised Person
dcea6641-3055-4f78-a1d7-cee79ffce7ec | signoff | HOLD POINT
cac92bef-46ea-48b8-90e9-ac8df547c333 | checkpoint | SPWB Ventilation System
debbedd6-cf65-5e93-a390-c0f5e9105e27 | note | Type - Document Submission
f47bd3f1-526b-5371-a20a-abee821a2bf4 | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs
09632be2-0978-502c-9eb6-c1389f3254dd | note | Clause Title - Trench excavation woks
92cb9090-a79f-5dcf-b6ca-ebc15fee8a4d | note | Requirement - Provide trench excavation procedure to Environmental Engineer and LUA for review and approval prior to commencement. Provide copy of trench dimensions/ base survey to Environmental Engineer. Contractor and Environmental Engineer notes.
d2b04486-bded-552d-8e82-ad66719552bf | note | Notice for Inspection - Prior to work commencment
a00f2d66-015f-5f6f-93f9-d868156b2025 | note | Lot Sizes & Test Frequency - Contract
14a5842c-de1a-5636-acb8-6c2e875b74ba | note | Release by - Enviromental Engineer
abd34030-bc68-4af5-81d4-7c539590cb30 | checkpoint | SPWB Ventilation System
e52d5a06-5a7b-552c-bb85-c5a600d09e50 | note | Type - Document Submission
61f4b754-c26d-5c90-992a-687d39284e0a | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs
69f74e72-4561-57d0-ad44-7831b7befd3e | note | Clause Title - Drilling and Installation procedure
0a875388-7bae-5020-b2ec-ed923dca102e | note | Requirement - Provide bore drilling/vertical pipe installation procedure to Environmental Engineer and LUA for review and approval prior to commencement.
8c62305a-7a38-50fa-8392-ea11123cd9c4 | note | Notice for Inspection - Prior to work commencment
0c1d34df-cbe7-51a8-aa09-24088c265cf0 | note | Lot Sizes & Test Frequency - Contract
b07f452d-47fe-5787-8c7d-028ce59111db | note | Release by - Enviromental Engineer
a915b33b-c5a1-47c7-8b1b-6c1047fb58ba | checkpoint | SPWB Ventilation System
004b8632-9096-5528-aec7-387e3053f27f | note | Type - Document Submission
a00be806-c568-5d7d-80d8-cef4cc5f724b | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs
ca789bae-de92-5168-b53b-efdf4e9502aa | note | Clause Title - Pipe Connection Procedure
d77033b2-03b8-555d-86f1-e73ab802c055 | note | Requirement - Provide pipe connection procedure to Environmental Engineer and LUA for review and approval prior to commencement.
6c49dba0-c68f-56af-ac26-c828ea3d83d2 | note | Notice for Inspection - Prior to work commencment
3375858b-15e0-56ac-8306-65fd5efd307f | note | Lot Sizes & Test Frequency - Contract
06f8053a-2905-55c1-85b9-a96270ab4361 | note | Release by - Enviromental Engineer
1d0a3265-a001-4ef8-9639-0e1f9569372d | checkpoint | SPWB Ventilation System
d8fea33b-a0a4-543c-9eb6-5de37d25a1c0 | note | Type - Document Submission
91d761e4-5a3e-541c-81e8-bd767a2490f1 | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs
873ba4c4-1b7b-5587-90e1-107478904d7e | note | Clause Title - Backfilling Procedure
0d5773e1-c0e4-56db-ba12-d14a5abab27b | note | Requirement - Provide backfilling procedure to Environmental Engineer and LUA for review and approval prior to commencement.
1dd20543-028a-5f87-a542-26e626e0cc22 | note | Notice for Inspection - Prior to work commencment
5e76cf79-e4f9-5ddb-84f6-045e57b0dcb9 | note | Lot Sizes & Test Frequency - Contract
a9f39cc0-ba20-5f48-875a-df858df46d9b | note | Release by - Enviromental Engineer
03ade1c9-9162-42a2-b5ee-0ba4e79b49fa | checkpoint | SPWB Ventilation System
c7fe7979-d98f-57ad-89cb-0c5e21e8675b | note | Type - Document Submission
abffe3f4-deb8-5e8a-82b3-8aaf8a8c8e55 | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs Section C3.6.1.
fc64caa7-ceb8-5478-a23c-c9757480d507 | note | Clause Title - Geotextile Installation Manual
5f7ef172-eb76-527a-8092-9c7dbffade29 | note | Requirement - Installation Quality Assurance Manual to be provided by contractor to Environmental Engineer and LUA for review and approval prior to commencement of any
34589e57-8149-59c5-9b63-331bf3a1e634 | note | Notice for Inspection - Prior to work commencment
416590fa-6932-55df-8920-33d89606abca | note | Lot Sizes & Test Frequency - Contract
5451c6d5-c666-5901-97bd-8567679dba08 | note | Release by - Enviromental Engineer
6eeebb0f-39c4-4528-ab32-33f065e6fb06 | checkpoint | SPWB Ventilation System
f4319d10-9616-56c3-9f2b-c62619e34542 | note | Type - Document Submission
49205d6b-379c-5a8a-9ca5-028d9807c788 | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs per Sections C3.6.2 and C3.6.3.
7bde16fe-d1ce-52eb-9a27-ac9010b67c0d | note | Clause Title - Capping Material
9ab9cfc5-9d21-571d-8ba1-e05efa28865b | note | Requirement - Provide caping material placement procedure to Environmental Engineer and LUA for review and approval prior to commencement.
4f1658ad-5c67-56c2-8c6e-868fa22dba52 | note | Notice for Inspection - Prior to work commencment
4a658c7f-5ba8-5c2d-ba69-5452cb041b2d | note | Lot Sizes & Test Frequency - Contract
b3d9eec2-1c0a-5cbe-9ed0-7b8f5bab0c8f | note | Release by - Enviromental Engineer
dc587dbd-2c5e-400b-bf9f-c5a13bfe40e1 | section | Materials
950baaa9-8d5f-49e5-b4dc-820492417257 | checkpoint | 04 - SPWB Ventilation System
bd39e725-b8b9-5ea6-8eda-ca2d3978e0c2 | note | Type - HP, Document Submission Product Conformance
06c45fcf-6021-5c34-9458-86f229f685fd | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs C3.3 and C3.5.
6e848cb1-4239-5f6c-90c3-371d01e4e2ae | note | Clause Title - Prior to importation of gravel for vertical bores and/or trench backfill
12ce1b53-5c5f-578a-8694-3aa8b2b13cd5 | note | Requirement - Review manufacturer specifications are in accordance with Sections C3.3 and C3.5. Independent testing of each material as per Sections C3.3 and C3.5.
44787507-dfe0-519e-b46c-ab6038a3b99a | note | ○ Manufacturer’s data specification sheets. Independent conformance test results at frequencies specified in C3.3 and C3.5.
b375011d-ca6c-50dc-a2a4-62dd2538e798 | note | Lot Sizes & Test Frequency - Contract / Material Changed 2 per 5000m3 of material.
9a97e0b5-cee0-56a9-afe2-a14d9bf33dff | note | Release by - Enviromental Engineer
86e078fd-3ac1-45de-a36f-8b3e17397597 | signoff | HOLD POINT
2df57954-913f-4707-9cac-d10019dd09fb | checkpoint | 05 - SPWB Ventilation System
7578fa70-740c-5814-8949-5a9406c44850 | note | Type - HP, Document Submission Product Conformance
597cc5c3-b90a-5aef-9f66-71dffdc9578a | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs Section C3.4
941f6a53-2c32-5277-ac6e-f9b3bbbe9a78 | note | Clause Title - Prior to delivery of perforated and blank HDPE pipes, joints/elbows/conne ctors, vertical riser and rotating cowls
7ba6037f-7098-55b2-b63c-5b668b51acb3 | note | Requirement - Manufacturer’s data specification sheets. Independent conformance test results at frequencies specified in C3.4. Prior to importation, review manufacturer specifications are in accordance with Section C3.4. Independent testing of each material as per Section C3.4.
3539bfaf-6dd6-5c6e-ab40-adc323902988 | note | Lot Sizes & Test Frequency - Contract
875b929f-953d-5fc9-aa9f-305e3148ba55 | note | Release by - Enviromental Engineer
044e277c-e7b4-4b2f-9756-3a1f8d810de4 | signoff | HOLD POINT
f27670b5-8c8a-4124-ba54-162aa241008e | checkpoint | 06 - SPWB Ventilation System
6f28c5fa-1099-5218-b6df-ea29faaa1922 | note | Type - Document Submission Product Conformance
cad14b64-ee50-5bf5-91ed-3e3bbbf8836a | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs Section C3.6.1.
f3007929-8479-5709-ac94-4cdd59411c22 | note | Clause Title - Prior to delivery of Separation Geotextile
7f5f073c-93f7-5707-9729-78495d9da452 | note | Requirement - Review manufacturer specifications are in accordance with Section C3.6.1. Independent testing of each material as per Section C3.6.1.
e9ece2fc-245e-5187-8227-98f1e00abb51 | note | Lot Sizes & Test Frequency - Contract
9bbffed0-ae91-5a30-85ab-0d7a4049b9e2 | note | Release by - Enviromental Engineer
2818a393-8f02-4d16-9dfe-a25f6b038ae5 | checkpoint | 07 - SPWB Ventilation System
ae8bd164-8f5f-5bb1-b5c7-8b222d6752f0 | note | Type - Visual Inspection
e37482bd-252c-5b92-a31d-0551858985e9 | note | Applicable Standard / Specification / Reference - Douglas Partners CQA Docs
24a579af-1553-5b83-8efb-0bf6792f9ce9 | note | Clause Title - Material Delivery, Storage and Handling
150b7e60-6ff1-50cc-8618-c149846daa77 | note | Requirement - Visual inspections during delivery, storage and handling Managed in a manner to avoid damage/deterioration of material.
92d46f00-ac65-52dd-992f-10f8c08ca6f7 | note | ○ Confirmation of as delivered material properties (each material). Delivery dockets. Contractor and Environmental Engineer notes and observations.
033764b7-b49d-576b-b6bb-d3a49101638e | note | Notice for Inspection - Give Notice of recieved Material
1ace271e-c71f-5bdc-a6e8-82a8d3c54459 | note | Lot Sizes & Test Frequency - For all Materials and Products recieved
d8c011dd-692f-56a4-a08c-af6fdd741646 | note | Release by - Enviromental Engineer
| checklist | ITP 001 - Excavation, Fill & Subgrade Prep |  | ITP 001 - Excavation, Fill & Subgrade Prep |  | 5363ab8d-811c-488c-8dff-ccd9af08f74e
| section | Procurement
| checkpoint | Physically located all utility locations
0daff645-d77f-5e5f-8ae5-f411aed6172a | note | Detail of Activity - Permit to work around services (Gas, Power, Fibre, etc.)
790dc180-5645-5084-a8c4-a22bf2c89834 | note | Minimum Test Frequency - as required per section of works
2c5f1451-8f23-59a0-9c63-785caedc4715 | note | Inspection/Test Method - Document Review
8ff9b370-8869-5522-9ab8-3c28a604406b | note | Acceptance Criteria - All services physically located
1e6d17e5-46ae-5c6d-a840-465ef7281693 | note | Verifying Documentation - Permit attached or permit number noted
3d409afa-978a-5c67-9287-77e2e9480ef6 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.2 - Contract Document Signed
d0298961-4e45-5241-ab49-845e45af843c | note | Detail of Activity - Ensure Contract is signed
9559d1b5-6aac-5990-8287-e5b27f6f45b5 | note | Minimum Test Frequency - at the Contract kickoff meeting
947d960e-9ddc-53d9-8fee-4ce45ecbdcc7 | note | Inspection/Test Method - Document Issue
537f443b-dd10-5eeb-b374-11aeef8be586 | note | Acceptance Criteria - N/A
4d7fd03c-5476-538b-be98-52a9bb8ab4b2 | note | Verifying Documentation - Issued with a NTC
a27f370a-4985-5a59-bdcd-c60f8213b18b | note | Responsibility - Downer / BBO's Rep.
| checkpoint | 100.3 - For Construction Drawings Issued
d22e0be1-6309-519e-bcc9-9bbb230b4401 | note | Detail of Activity - Ensure "For Construction" drawings are issued
b650208e-5868-5afa-816c-c8913530ce35 | note | Ensure Contract is signed
8c18305e-4208-5e18-95be-819718766c8b | note | Minimum Test Frequency - at the Contract kickoff meeting
321dab2c-f953-556d-b8d2-3a0b4305fede | note | Inspection/Test Method - Document Issue
8a14e99c-6410-5c82-b1a8-d19727f66166 | note | Acceptance Criteria - N/A
25298f71-bd79-55f9-8a30-c433517fd933 | note | Verifying Documentation - Issued with a NTC
e9f3a47b-a013-5984-8433-46ae84d2f9fc | note | Responsibility - Downer/BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| section | Construction
| checkpoint | 100.4 - Traffic Management Plan
210e46cb-cdfa-5f93-be1c-1e2fd143393f | note | Detail of Activity - Ensure TMP is approved and check that the requirements are fully understood by the STMS
4ce22e44-7555-5522-9cb1-ff1d40e40dc7 | note | Minimum Test Frequency - every morning and/or when the TMP changes
3e84efe5-c91c-5a52-ba4b-2c23c1e4f1e3 | note | Inspection/Test Method - Document and Physical works review
33ce09a2-c19e-5bc5-819c-ad56b7e1bc25 | note | Acceptance Criteria - COPTTM
278143c5-eb28-5532-ab2e-718d946d706e | note | Verifying Documentation - TMP from contractor
df50b5c4-5f65-5d56-8486-dbce00fe3e3b | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.5 - Design
0617a8d1-51f1-5796-a611-435081b2b57f | note | Detail of Activity - Ensure that Design is approved and Drawings are the latest version
eb9005d0-be3a-518b-a6e2-03ca080e4ff9 | note | Minimum Test Frequency - Prior to commencement
f3e53d47-b28b-5b3e-ae75-ded800153bbe | note | Inspection/Test Method - TNZ M/20; TNZ M/7; TNZ M/24
8f366595-4886-52f0-b53f-df93c6afac5a | note | Acceptance Criteria - Is a copy of approved consent(s) available on site
faf13066-3a58-524b-a8c5-43f92c1b9700 | note | Verifying Documentation - Check Drawing register
166a8de3-7214-54a2-86a9-f7a3ddf4eb7e | note | Responsibility - Contractor
| checkpoint | 100.6 - Approved Consents
2f603023-5ab2-5723-82cb-f9bf7a6687af | note | Detail of Activity - Is a copy of approved consent(s) available on site
ae372bcc-bb1f-5c46-94ed-0a233d343311 | note | Minimum Test Frequency - Prior to commencement
24364bae-3324-5d55-813e-b06b4b650b25 | note | Prior to commencement
ba7759a3-89e5-5112-91e0-877a6cd46a76 | note | Inspection/Test Method - Visual Inspection
cefa0a2d-6b52-5271-ad8c-756fb1afcddd | note | Acceptance Criteria -
8b075374-2d38-59d9-a074-c116e019d5b7 | note | Verifying Documentation - This ITP
7cc1053a-3069-5fec-8843-04dd2e2ab24c | note | Responsibility - BBO's Rep.
| checkpoint | 100.7 - Pre-start meeting
e6ec85c6-7b20-59f9-bdea-e479f3f5e675 | note | Detail of Activity - Pre-start meeting to confirm work strategy and safety measures
e40ab7bd-33a7-5bc9-93e1-18954150789b | note | Minimum Test Frequency - Before commencing work each day
c0b8cf65-dcdd-55e7-9d15-c4caea5a2197 | note | Inspection/Test Method - N/A
9641704d-dffb-54ce-92a8-575b25013732 | note | Acceptance Criteria - 100% attendance
3bc84022-89c8-5b7e-bc59-81b437b0460d | note | Verifying Documentation - Pre-start sign on register / site diary
e92f511e-ba3c-5f9b-a00b-56bc06545e63 | note | Responsibility - BBO
| checkpoint | 100.8 - Contractor's methodology
019ade75-5865-55d2-afa3-3d3013593698 | note | Detail of Activity - Site inspection
06eef761-6df4-5ad8-9c39-df1f74f824f7 | note | Minimum Test Frequency - Prior to commencement
3ce1571e-81ab-5587-b623-50775ec16861 | note | Inspection/Test Method - Document review
f19428ef-6587-53f1-ab6e-16bddd43d482 | note | Acceptance Criteria - Methodology conforms with all relevant specifications
2260e019-8ae1-51aa-9f6b-0bde354b35a3 | note | Verifying Documentation - Methodology submitted via NTE
19c5002e-9438-5229-a19d-cbc4ba50d9bb | note | Responsibility - BBO's Rep.
| section | Post Work
| checkpoint | 100.9 - Laydown area / stockpile sites
cfcb6ca8-deab-5f6d-a9e5-7f004ea4a9cc | note | Detail of Activity - Site inspection
dad93464-1605-5ea6-9a76-ca3e6ed70d37 | note | Minimum Test Frequency - Prior to commencement
0775bd7b-7ee7-5cb3-ae03-6ff9002c241b | note | Inspection/Test Method - Visual Inspection
0ac9edfb-0cfd-54d3-bec1-44430bc11d01 | note | Acceptance Criteria - Approved by NZTA
7455835d-ee0a-5c1c-94e6-1e5ce2ba5114 | note | Verifying Documentation - Request for approval (RFA) via NTE
2d9a3402-767f-5a21-af6c-1e1e4583fdad | note | Responsibility - BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.1 - Weather
052808d9-18b7-58a7-ab9a-eb6137fd0c06 | note | Detail of Activity - Assessment of forecast
9ca2e115-efaa-5280-9d60-0a60c8c3eb6c | note | Minimum Test Frequency - Daily prior to and during works
9b0657ee-b009-5bb0-a572-be0a7b760002 | note | Inspection/Test Method - Check local and national weather forcast services
c7af84f2-c3b5-5d35-be93-977004935b67 | note | Acceptance Criteria - No imminent rain or adverse weather conditions. Consideration of wind and project location/environment
1b15eed5-445a-5a67-8dab-4d5972011f82 | note | Verifying Documentation - Contractor's site diary
2b74f64c-d587-5e4b-a956-581b76f9c1dd | note | Responsibility - Contractor
| checkpoint | 101.2 - Environmental Protection
d1ff1df5-6bf7-5556-a880-eb4748cda0f3 | note | Detail of Activity - Site evaluation
475446ea-ba66-5a4e-8ef0-03b15a5631ea | note | Minimum Test Frequency - Prior to commencement
f31cf18d-1e93-56c1-b93f-c88909627801 | note | Inspection/Test Method - Inspection
c89cd882-712a-51a6-acd9-f9bd2420e281 | note | Acceptance Criteria - Supervisor assessment of conformance
e202d083-2f84-5050-a59c-4795f620bc5d | note | Verifying Documentation - Contractor's site diary
f630990b-8c36-5ea0-87ab-7e5c4e8a0e6e | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.3 - Precondition Survey
3aa69012-5ec8-53fa-9a2d-084df0778df7 | note | Detail of Activity - Examine extent of the site
b7025122-0e1a-58f8-bb31-f7124823168e | note | Minimum Test Frequency - Prior to commencement
f8e08d1a-7614-56e6-bff0-261e6d3141be | note | Inspection/Test Method - Inspection
6ef3e200-1e73-50d9-bc27-a71f0d11fced | note | Acceptance Criteria - Supervisor assessment of conformance
a0341198-cd71-541b-b8b7-830e52fd1350 | note | Verifying Documentation - Contractor's site diary
5064aab6-5d22-5e1f-a5a2-3155534f8a64 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP 002 - Capping Layer |  | ITP 002 - Capping Layer |  | 0baf8a97-f864-420f-bebc-3bf9ba4a7c93
| section | Procurement
| checkpoint | Physically located all utility locations
6864abb3-9df0-5f84-8fff-277f3573ae2d | note | Detail of Activity - Permit to work around services (Gas, Power, Fibre, etc.)
f96506b3-ab10-5739-8b82-60e3a5cfe483 | note | Minimum Test Frequency - as required per section of works
1a576b75-5b06-5fae-a49b-24a50f59771a | note | Inspection/Test Method - Document Review
b26bedb5-e360-5ff5-9f54-62b28affd2bd | note | Acceptance Criteria - All services physically located
6ecad2c3-8e2d-57e6-ba43-91aca82b5348 | note | Verifying Documentation - Permit attached or permit number noted
22518f1d-32ca-5f0e-bca8-1e94ae566e69 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.2 - Contract Document Signed
8ef9deaa-91b6-5e50-8883-431ce7f92f3e | note | Detail of Activity - Ensure Contract is signed
80ecb48a-6c96-5999-a7a7-cf44036bc0cb | note | Minimum Test Frequency - at the Contract kickoff meeting
edcb6a82-54a5-5d6f-99ac-be6fdaa7a369 | note | Inspection/Test Method - Document Issue
78798a09-7b46-5c50-8e77-b1baba650ec7 | note | Acceptance Criteria - N/A
c24d467a-57f9-50f4-99ca-4a0d854fbe3c | note | Verifying Documentation - Issued with a NTC
c4d58cd1-177a-5371-acc5-89c9c9eba13b | note | Responsibility - Downer / BBO's Rep.
| checkpoint | 100.3 - For Construction Drawings Issued
a3831201-4855-5d4e-b568-cb7e7aa6fa62 | note | Detail of Activity - Ensure "For Construction" drawings are issued
8f6be392-4d68-5533-b98b-68105e180846 | note | Ensure Contract is signed
b16016d8-e64c-5a0c-a208-5b6407a1b383 | note | Minimum Test Frequency - at the Contract kickoff meeting
76cdc54e-877b-5f86-8b51-7a4f2f618169 | note | Inspection/Test Method - Document Issue
eb8ac336-7c40-57b6-8169-ee0e29dfdc51 | note | Acceptance Criteria - N/A
0724fb78-69bb-5215-ae26-224920b18fcf | note | Verifying Documentation - Issued with a NTC
c98573c5-9bb5-5d61-9c36-2bf747c23b97 | note | Responsibility - Downer/BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| section | Construction
| checkpoint | 100.4 - Traffic Management Plan
84b0c8f4-09da-559f-a544-6d9aa677edd1 | note | Detail of Activity - Ensure TMP is approved and check that the requirements are fully understood by the STMS
a58b12ca-93f8-5fca-830f-475cc8ea50de | note | Minimum Test Frequency - every morning and/or when the TMP changes
bfbfa7ea-e5f1-5846-a5b9-d3439f8e2da9 | note | Inspection/Test Method - Document and Physical works review
0d3ab922-999b-53b6-96b1-2293de6a2a95 | note | Acceptance Criteria - COPTTM
e84146f6-e813-5590-8158-42646c90d8ce | note | Verifying Documentation - TMP from contractor
60121b19-a2b9-5fc7-b1c5-4b28b0be31b0 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.5 - Design
4805c05e-058d-5ec2-9f65-71dff8a5d3e3 | note | Detail of Activity - Ensure that Design is approved and Drawings are the latest version
9c647a57-f512-52da-b051-59acd87a1ebb | note | Minimum Test Frequency - Prior to commencement
2927b4ed-7b1e-51db-88f5-17b1f7c4a928 | note | Inspection/Test Method - TNZ M/20; TNZ M/7; TNZ M/24
a168b25f-e3de-5f8c-a2f6-c629e2d02471 | note | Acceptance Criteria - Is a copy of approved consent(s) available on site
f957a63d-d785-53dd-967e-7e73543455f3 | note | Verifying Documentation - Check Drawing register
1d1b10e9-bb37-52e5-a6cd-1ea9a11b05a4 | note | Responsibility - Contractor
| checkpoint | 100.6 - Approved Consents
c1cca32e-ab0d-5fa6-9203-92235ba039e9 | note | Detail of Activity - Is a copy of approved consent(s) available on site
4c6fbe48-6447-5455-92d0-bcbabe8787d0 | note | Minimum Test Frequency - Prior to commencement
8094a0f5-8173-5f5e-912a-d1eb6c1eb6ba | note | Prior to commencement
5ed48067-2ad2-57db-9c31-8da04baefe46 | note | Inspection/Test Method - Visual Inspection
9525406d-0172-599a-9c1e-dcdc9600354f | note | Acceptance Criteria -
47f3b81a-8379-566a-8f8e-59b9be60ac82 | note | Verifying Documentation - This ITP
ac17e8f2-8c41-5c5f-85cf-b7ccef556caa | note | Responsibility - BBO's Rep.
| checkpoint | 100.7 - Pre-start meeting
ace4ff17-0643-5535-80ac-cd324f7c19d1 | note | Detail of Activity - Pre-start meeting to confirm work strategy and safety measures
b612c74c-7450-54bb-a169-959fb3615c1d | note | Minimum Test Frequency - Before commencing work each day
0b4eea31-d4de-5b54-ae3e-2c0a28083e97 | note | Inspection/Test Method - N/A
a58cc459-f633-563c-b23b-3ec6230a5cbf | note | Acceptance Criteria - 100% attendance
8c8c30d2-f3ea-5786-8655-bb0a1e758511 | note | Verifying Documentation - Pre-start sign on register / site diary
ecc389b8-2a78-52b0-b92c-1f4d1bdc4208 | note | Responsibility - BBO
| checkpoint | 100.8 - Contractor's methodology
9f91cb1e-a77d-585d-863c-bdbce0f15bd5 | note | Detail of Activity - Site inspection
f5cc98ba-cd74-5a48-b917-28516ff35db6 | note | Minimum Test Frequency - Prior to commencement
a7278459-d6a7-57fa-bd65-c21b51001134 | note | Inspection/Test Method - Document review
3c0d404a-cea6-54ef-aa10-7d835c404372 | note | Acceptance Criteria - Methodology conforms with all relevant specifications
f7a78c1c-ed9d-5f0a-b15f-7cb4405a8d6a | note | Verifying Documentation - Methodology submitted via NTE
fa47d607-4c76-5ed3-9841-0cf83472637d | note | Responsibility - BBO's Rep.
| section | Post Work
| checkpoint | 100.9 - Laydown area / stockpile sites
13bf4188-5a93-5ef5-bcd4-73f66b3b42a3 | note | Detail of Activity - Site inspection
e4dfa1d4-312f-5535-a482-d3b6277b1571 | note | Minimum Test Frequency - Prior to commencement
3e668999-5d00-5f71-aab1-a8a4225fcf2f | note | Inspection/Test Method - Visual Inspection
354347c7-33eb-51b6-9743-2fb66c5e1b44 | note | Acceptance Criteria - Approved by NZTA
5edf3e24-5235-5c79-b967-2e902d927062 | note | Verifying Documentation - Request for approval (RFA) via NTE
1d68918e-3c4f-599f-9439-3ac7b627e746 | note | Responsibility - BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.1 - Weather
be400cd3-252d-553f-9eaf-7c6fd44a73b1 | note | Detail of Activity - Assessment of forecast
dcc211c8-2dc1-5f0f-8dbe-2b3792e233fe | note | Minimum Test Frequency - Daily prior to and during works
79bb2a07-313f-5dae-971e-d98f18b0a506 | note | Inspection/Test Method - Check local and national weather forcast services
10731880-499f-51c2-9700-72dbdf2350b4 | note | Acceptance Criteria - No imminent rain or adverse weather conditions. Consideration of wind and project location/environment
040da5ef-033c-5850-9f86-1d11d6dc9d4d | note | Verifying Documentation - Contractor's site diary
c1a4688a-3e0c-52ed-85fa-ba5bfe3780bb | note | Responsibility - Contractor
| checkpoint | 101.2 - Environmental Protection
6373a627-af35-5fa0-9d92-9d170241e5ce | note | Detail of Activity - Site evaluation
3d87c19b-7294-5177-b6d9-d5091c1d2d6a | note | Minimum Test Frequency - Prior to commencement
68aa1a74-7384-5c9c-bf47-3f2840f6c2fa | note | Inspection/Test Method - Inspection
1622f9d5-52f3-5d48-98f7-6da1f4d606b3 | note | Acceptance Criteria - Supervisor assessment of conformance
c8ee7dca-8060-502b-9c85-eb4fdbbdf818 | note | Verifying Documentation - Contractor's site diary
b7d2586e-4e75-5364-9e6e-faad24205065 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.3 - Precondition Survey
d7a05c90-7831-56de-98ff-fa073d87d141 | note | Detail of Activity - Examine extent of the site
215530e9-f1ea-560a-8834-f33dbd8f3d00 | note | Minimum Test Frequency - Prior to commencement
f4447c99-baf8-59bd-b861-3089814e614f | note | Inspection/Test Method - Inspection
38325e46-d99a-5556-9f82-66cdb48a953b | note | Acceptance Criteria - Supervisor assessment of conformance
34cb80b0-b912-5bea-a08e-1f20160184ed | note | Verifying Documentation - Contractor's site diary
23ba5dc9-55bc-54ea-b589-49f9d46bcd75 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP 003 - Subbase Layer |  | ITP 003 - Subbase Layer |  | 30a2d497-448a-4aee-b7df-6ce4ad1aa4ce
| section | Procurement
| checkpoint | Physically located all utility locations
a8ae8054-4f60-56f4-97a4-88c4ef6b36e5 | note | Detail of Activity - Permit to work around services (Gas, Power, Fibre, etc.)
5eeba223-7907-5cde-b793-a1c47898ec32 | note | Minimum Test Frequency - as required per section of works
5585a794-9266-54d6-b142-d0211e28eae5 | note | Inspection/Test Method - Document Review
a429cc36-1b2d-5ef7-99b0-d8d21447b9e5 | note | Acceptance Criteria - All services physically located
346977ff-d8d8-59d5-8302-8afabeb7ba62 | note | Verifying Documentation - Permit attached or permit number noted
b3000fb5-331e-5422-9672-454c40880074 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.2 - Contract Document Signed
88b65d94-da50-5c73-b711-3f4343c497cc | note | Detail of Activity - Ensure Contract is signed
ef266196-1b31-5a8b-b9c1-5df424264a4e | note | Minimum Test Frequency - at the Contract kickoff meeting
de1a60ee-a4c0-54de-9228-39a1b58bbb00 | note | Inspection/Test Method - Document Issue
1ed99eee-83e2-570d-87ec-f4a06fe2913f | note | Acceptance Criteria - N/A
43c37d3c-ffa6-5501-baf7-16e975943fd8 | note | Verifying Documentation - Issued with a NTC
0bd32e80-a110-5aa1-8441-f6daa545802b | note | Responsibility - Downer / BBO's Rep.
| checkpoint | 100.3 - For Construction Drawings Issued
a727d340-b25c-58bb-8973-a63e492e8da6 | note | Detail of Activity - Ensure "For Construction" drawings are issued
b7b3626c-dbd8-56e6-8647-5ed678084e2d | note | Ensure Contract is signed
3dc8e932-25a4-5a5f-96ac-1a15d592e776 | note | Minimum Test Frequency - at the Contract kickoff meeting
19dbad00-7d5a-5ad2-9bba-68a7a9266896 | note | Inspection/Test Method - Document Issue
68560b8d-7d7a-5937-a5c8-330c4e30d22b | note | Acceptance Criteria - N/A
4e68f7fe-2757-5533-ba4a-d1a0dcb1e06e | note | Verifying Documentation - Issued with a NTC
35162dc3-5e24-59dd-b385-b84e31f6fb4c | note | Responsibility - Downer/BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| section | Construction
| checkpoint | 100.4 - Traffic Management Plan
c5272bf1-7036-5552-b848-b0d14c03a1f7 | note | Detail of Activity - Ensure TMP is approved and check that the requirements are fully understood by the STMS
18437fe7-411c-52ae-a2b0-6dd0171fc278 | note | Minimum Test Frequency - every morning and/or when the TMP changes
a57353df-4e77-5d79-b87b-6cef5efe27c9 | note | Inspection/Test Method - Document and Physical works review
8113a43d-2289-5cb6-9d36-78d5ef5582b7 | note | Acceptance Criteria - COPTTM
08a80483-6820-56fe-93e7-58fbfd956000 | note | Verifying Documentation - TMP from contractor
c252e7dd-96d8-5cd5-a901-cef297dcbcfe | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 100.5 - Design
7f8c824e-9471-53dc-9c94-70d42d1d8d49 | note | Detail of Activity - Ensure that Design is approved and Drawings are the latest version
f6f88d38-0ae5-564c-ba91-01f02bebdf88 | note | Minimum Test Frequency - Prior to commencement
adcf8940-9a8a-57f4-9e3a-8de6ca51a884 | note | Inspection/Test Method - TNZ M/20; TNZ M/7; TNZ M/24
f7e4f64e-384f-598e-aff6-4a11f1e08612 | note | Acceptance Criteria - Is a copy of approved consent(s) available on site
b6392706-c9e4-5d1b-a35c-66dc8490c572 | note | Verifying Documentation - Check Drawing register
ff8c3e2f-2595-5e23-b539-dee94aca832f | note | Responsibility - Contractor
| checkpoint | 100.6 - Approved Consents
893ab715-dbeb-5391-b93a-f52de0364d2f | note | Detail of Activity - Is a copy of approved consent(s) available on site
96b705c7-af0f-55f4-9cc3-b1a3eadca622 | note | Minimum Test Frequency - Prior to commencement
3ce7721f-214c-5fa1-89b5-3cee7ed9e902 | note | Prior to commencement
8bb2dede-b652-520c-ae63-4ba595e9e09f | note | Inspection/Test Method - Visual Inspection
082310a9-9b26-5e87-b604-e9330ee85513 | note | Acceptance Criteria -
b37a98b9-9bb4-5946-8c90-666daa27d3c5 | note | Verifying Documentation - This ITP
0755237c-ef39-509f-91e7-05aba2a9cb15 | note | Responsibility - BBO's Rep.
| checkpoint | 100.7 - Pre-start meeting
f4d60d8a-712b-52e2-8a6c-a4bf3675bb09 | note | Detail of Activity - Pre-start meeting to confirm work strategy and safety measures
337e8f7b-b6bd-54f1-9e20-51c809e64ae7 | note | Minimum Test Frequency - Before commencing work each day
c96d407e-501c-54d3-af1e-b92f1b87aa14 | note | Inspection/Test Method - N/A
33387768-9757-5401-bc9c-6eb0e6ab63b8 | note | Acceptance Criteria - 100% attendance
d8fa4a21-611a-5569-8ea0-c09465569665 | note | Verifying Documentation - Pre-start sign on register / site diary
b9577ea6-e02a-598a-b2f0-7cf6d12c036b | note | Responsibility - BBO
| checkpoint | 100.8 - Contractor's methodology
62ce3b0d-bf72-5c96-a9f5-a6401b5131e9 | note | Detail of Activity - Site inspection
babc3379-1bcc-50a0-a224-4b11c3584293 | note | Minimum Test Frequency - Prior to commencement
9cb718bc-3428-5223-9ba0-e29c2d719be2 | note | Inspection/Test Method - Document review
380f9e3e-70d7-54cb-b817-035642aa98b6 | note | Acceptance Criteria - Methodology conforms with all relevant specifications
4dd46eb2-54b4-5753-af17-5418069013c1 | note | Verifying Documentation - Methodology submitted via NTE
fb44b67a-fbff-5b0b-83bc-e99993f79ff1 | note | Responsibility - BBO's Rep.
| section | Post Work
| checkpoint | 100.9 - Laydown area / stockpile sites
486e1e9e-a636-5c17-a5c8-ef0b3d5b3972 | note | Detail of Activity - Site inspection
fc6727cd-04c6-5f33-a63b-8cf3c0e1f52f | note | Minimum Test Frequency - Prior to commencement
c7ffa64e-713a-5c60-82b2-af7ecdad455c | note | Inspection/Test Method - Visual Inspection
1cab6316-a2ec-5fef-a2b2-9fd91343d388 | note | Acceptance Criteria - Approved by NZTA
c3994e4f-f3c4-5764-852b-23305d173e89 | note | Verifying Documentation - Request for approval (RFA) via NTE
874d2848-0020-598f-81e5-5b38597da69f | note | Responsibility - BBO's Rep.
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.1 - Weather
529587b4-1fee-55fd-847f-c964ede4cc46 | note | Detail of Activity - Assessment of forecast
0ac712ef-7ef1-5852-8878-0565394c8ca2 | note | Minimum Test Frequency - Daily prior to and during works
4e7612d2-e57f-59b0-8579-ee4b53d2a2e8 | note | Inspection/Test Method - Check local and national weather forcast services
500fc0db-a587-597d-9557-ed7c7b646ae0 | note | Acceptance Criteria - No imminent rain or adverse weather conditions. Consideration of wind and project location/environment
31d44841-95bf-5d94-9fdb-2cc21287d267 | note | Verifying Documentation - Contractor's site diary
74085e74-b59f-5319-9503-f14ac1043c79 | note | Responsibility - Contractor
| checkpoint | 101.2 - Environmental Protection
62ab42f5-d3ae-5448-b1c0-42cb5a387468 | note | Detail of Activity - Site evaluation
00f5c6e6-a48f-501e-af81-321668e70531 | note | Minimum Test Frequency - Prior to commencement
5349127e-dbce-5fe0-b20c-cba7f527c02a | note | Inspection/Test Method - Inspection
95db073b-1fd6-5b52-98ac-e4d272794975 | note | Acceptance Criteria - Supervisor assessment of conformance
5b6676f7-a145-59b7-aa2c-ba2be776d9e0 | note | Verifying Documentation - Contractor's site diary
598bb5b7-c4c4-54c9-85e9-56163e9db38e | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 101.3 - Precondition Survey
858ddd6a-10ee-5b6e-a6b9-3233eac4e048 | note | Detail of Activity - Examine extent of the site
e28589f6-27c4-50bc-bf28-e1e4610aed5c | note | Minimum Test Frequency - Prior to commencement
e62a4e2a-1879-537a-a007-b5857dd35deb | note | Inspection/Test Method - Inspection
4d9129bb-2359-5fc5-b959-6ff93206ef93 | note | Acceptance Criteria - Supervisor assessment of conformance
5e69f24e-1a90-5773-8a69-6959308d3674 | note | Verifying Documentation - Contractor's site diary
e17b059c-f8df-556b-9ff5-be93036ae551 | note | Responsibility - Contractor
| signoff | AUTHORITY HOLDPOINT
| checklist | ITP 004 - Basecourse Layer |  |  |  | 3405db9f-a6d8-45b7-9e73-c3a73b6f84ff
| checkpoint | Optional Document Upload Below
| checklist | ITP 005 - Asphalt Basecourse |  |  |  | ae5fb222-5661-4f7d-a88f-cda632ff4d55
| checkpoint | Optional Document Upload Below
| checklist | ITP 006 - Pavement |  |  |  | 486b41c4-b660-4542-b2b9-34624b095204
| checkpoint | Optional Document Upload Below
| checklist | ITP 007 - Footpath Pavement |  |  |  | ce3aff4a-22f0-4a6e-bdef-abdb8d18ca92
| checkpoint | Optional Document Upload Below
| checklist | ITP 008 - Clearing & Grubbing |  |  |  | c22579f5-cae6-40eb-b864-8056811e32f9
| checkpoint | Optional Document Upload Below
| checklist | ITP 009 - Subsoil Drainage |  |  |  | 24a486aa-178f-4a5e-a321-e578dd78d9af
| checkpoint | Optional Document Upload Below
| checklist | ITP 010 - Underground Stormwater Drainage |  | ITP 010 - Underground Stormwater Drainage |  | 9ab4e37b-4f41-4f82-a534-42eb9199adf8
| section | Setout, Materials and Preparation
| checkpoint | 300.1 - Mark out works
ece4a993-0bb5-562a-b1bf-b8fa47b360a3 | note | Detail of Activity: Set out and mark up proposed drainage features by surveyor
f4e675df-d71d-56c4-b116-a4879f22660b | note | Action: H
ee90696f-7f1d-5a69-a0d0-1ec1b47e3f8d | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage features
96dd21a1-6737-51d8-8089-e4682e79b659 | note | Inspection / Test Method: Visual Inspection
6bee180a-7189-5dfa-95f0-980e4380ab37 | note | Acceptance Criteria: N/A
25324f16-b857-580b-afd4-2b1084988f7e | note | Record Documents: Contractor's site diary
99e24245-b63f-5f6e-bd1d-76b3f87c4dc6 | note | Responsibility: Contractor
137e20e9-6926-5358-8ee9-d77f3c09eb18 | note | Comments: Treatment area marked up jointly by Contractor and Eng.Rep. Approved by Designer
| checkpoint | 300.2 - Underground services
ea2292c6-4fe6-5e13-8fed-66f689e45703 | note | Detail of Activity: Identify and positively locate services
c580f05c-56ed-59f9-b67f-3e34432d6cce | note | Action: H
d8995efe-868a-519d-805b-7342f06680a1 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage features
3f2bf0a8-b084-5b99-ad12-17d76caf21e6 | note | Inspection / Test Method: Hydoexcavation
76567db6-f696-5454-bae1-2c6818879a85 | note | Acceptance Criteria: N/A
c514a171-555a-5b34-b707-7c4469b62113 | note | Record Documents: Drawings
c59b730d-6f17-58e9-b8c3-f209d4261ac7 | note | Responsibility: Contractor
| checkpoint | 300.3 - Precast Concrete Pipes
2fcf6c27-0307-5ee1-be25-408ec52d9646 | note | Detail of Activity: Contract to provide manufacturer dwgs of the proposed design for approval
6f10ddb4-5be7-5df9-8398-e5a73432e320 | note | Action: H
63d72ed3-63d5-5935-943e-e26a558f2116 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per culvert size/type
10dba40b-a9a2-5f6b-ac6f-179e3ca9006a | note | Inspection / Test Method: Supplier Producer Statement
ba85e3b7-bcd8-51a2-acbc-1370c0116925 | note | Acceptance Criteria: NZS 4058:2007
44e2456f-1767-5fbf-9a6c-01c9f2a9847e | note | Record Documents: NTC / Site instruction
e2a98a02-b9a3-5515-abc0-383edb12665f | note | Responsibility: Contractor
| checkpoint | 300.4 - Precast headwall/wingwall units
b729bd87-7b22-55d5-8a4d-1e6ba63dfa50 | note | Detail of Activity: Contract to provide manufacturer dwgs of the proposed structure design for approval
92ea4182-55e1-5738-a8b9-cf687b4727b3 | note | Action: H
39ee7d85-21f9-5731-8742-62bba9ef4c4a | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per wingwall type
6ecb438f-87d9-5638-873a-516a543d6f3c | note | Inspection / Test Method: N/A
83bab304-2ccb-5b63-947b-135e07c7135d | note | Acceptance Criteria: Engineer to review and approve proposed design
f83a92a1-6400-5483-82db-90c001930e8e | note | Record Documents: NTC / Site instruction
007e4ed7-81fe-56a6-b131-65672e38ea21 | note | Responsibility: Contractor
17c79590-7e29-53d5-b51e-92b7d4922ec0 | note | Comments: This requirement acknowledges minor variances in manufacturer design details for precast wingwalls
| section | Construction and Finishing - Stormwater Line 1- Ch 225m Kopaki Rd; 750mm Dia
| checkpoint | 300.5 - Determine Subgrade Strength
eb9fbef6-eabb-5a94-8b5c-bf07938d25a0 | note | Detail of Activity: Determine bearing strength of subgrade
823614b7-7d25-5da8-ac23-8a144044a06c | note | Action: H
b3dafaf6-a809-5be7-8a85-d59aa237eab6 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
136a5e69-02eb-5202-9478-5f7f652c4213 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
b2417739-6da5-5573-8884-6276a38c2ae5 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
4cf9d084-6010-535d-b539-4f85cdde2175 | note | Record Documents: Contractor's site diary
73d25cc5-6a01-52c7-9e45-753eddca685d | note | Responsibility: Contractor
588f7f90-97e4-5b2a-840b-e5b34ba2595d | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.6 - Pipe bedding
547619a2-1cf1-5180-9bec-61fdfe922093 | note | Detail of Activity: Bedding
eebd8348-693c-5213-81e9-0aa2919c3cb8 | note | Action: M
64fcddb6-e7f9-5530-a66a-77b66dcadd3d | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
f8665f9a-ad3d-50e2-a1f5-fa445a6ee32f | note | Inspection / Test Method: NZS 3725:2007
9d55f0b1-9a87-55a8-9cdf-ec6200f67658 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
6ff9ab30-a3de-5e1d-8682-9575a85f394e | note | Record Documents: Contractor's site diary
7b6040d9-0335-5d68-9e27-77a1dbce2c49 | note | Responsibility: Contractor
fe2d1a0b-076d-5958-bf6a-d490740bfd87 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.7 - Jointing of pipes
6e745fff-a7ff-5256-bfc9-6f464cf871be | note | Detail of Activity: Jointing
6b4fee89-b502-510d-bdc5-f37e79ab294d | note | Action: M
8620e0c0-c8eb-5d7b-93ef-dd9ca491431b | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): Every Pipe Joint
24252ac5-1561-50c5-a41c-4d421ab4e43f | note | Inspection / Test Method: Visual Inspection
4290baa3-f707-50a1-b611-4af368e6c5b3 | note | Acceptance Criteria: In Accordance with section 5.2 of the Project Technical Spec.
7f81fd3b-41b7-5d33-bf46-d08759e869e5 | note | Record Documents: Contractor's site diary
4e84ac8c-221c-543c-9733-cf88bbd499a9 | note | Responsibility: Contractor
3ef338ec-8ebd-5961-a2a1-2d8bdaed6702 | note | Comments: Rubber rings to be mounted evenly and lined up truly concentric with pipe. Gap between spigot and shoulder to of pipes to be even and between 5mm and 10mm.
| checkpoint | 300.8 - Pipe haunching
f7744520-2318-5c0c-bc3d-c4c962c91142 | note | Detail of Activity: Haunching
2ef1a5ae-b4b7-5f38-9c14-17bed7804a8e | note | Action: M
80214caf-b984-5d25-a741-638024946214 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
56be8321-aee0-548f-a75d-4f64d8a320cd | note | Inspection / Test Method: NZS 3725:2007
ed4d4914-17c0-5f0c-bb05-abb7aa5ba9e3 | note | Acceptance Criteria: In Accordance with HS2, Minimum haunching depth of 0.3D, CIV Value on compacted haunching >25 (CBR = 30).
e59f7f5d-1e2a-5d7a-b20e-2899e16831f9 | note | Record Documents: Contractor's site diary
2c2c8dfa-829b-5f26-8833-de827341dbe7 | note | Responsibility: Contractor
437ee093-1f5f-5b33-ae27-eacccf784582 | note | Comments: PAP 7 material to be used.
| checkpoint | 300.9 - Trench backfill
dffb20f0-379f-5c02-b903-50e99aaa2be4 | note | Detail of Activity: Backfilling
70794d30-e6f9-597b-a49a-db5a154ef599 | note | Action: M
c68cc380-2a30-5790-bc39-74cd92e6474e | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
d9a1e1b4-3026-5581-ab38-1fcdd0fdad5d | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
ac50c1c5-1b40-54ec-be86-9c3f7190d895 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
e33c6276-0853-52e0-b190-72eca99ed2a0 | note | Record Documents: Contractor's site diary
507742bf-33d5-5614-86d2-76ba18a35fb2 | note | Responsibility: Contractor
f14a04a7-f97a-5379-a53d-65b823eb9895 | note | Comments: Clean Pumice Fill to be used
| checkpoint | 300.10 - Visual Structural Inspection
3d0c7a56-9b1b-5cb6-9e62-1f01209220b2 | note | Detail of Activity: Visual inspection of concrete components
14f7f6c0-45af-52ea-aed5-49f1901b5aa5 | note | Action: W
9d494c4c-593e-5ef8-b0ef-dc7fb278ad9d | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
4a5ef465-3d97-5ec3-8581-fe0a42c58dc7 | note | Inspection / Test Method: Visual Inspection
52c3ed27-e857-543e-ad2f-e3d46c0e6486 | note | Acceptance Criteria: No visible damage, especially around collars and spiggots
817b7ea4-52c0-59b5-94a2-c68b1ee9d51a | note | Record Documents: Contractor's site diary/Photos
6364df05-d7ba-596f-afb2-22761ee8e5d2 | note | Responsibility: Contractor
| checkpoint | 300.11 - CCTV Inspection
d8a8ad92-bb64-588b-b4f6-12e8afcfe575 | note | Detail of Activity: Visual record of Existing works
e4f58cfc-16e4-5211-bb69-9dbe9425edf9 | note | Action: W
77efd114-3a2b-5e39-805a-20339fc55877 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage pipelines
ab860684-2241-5a6d-b3bb-9fe653125f0c | note | Inspection / Test Method: CCTV Inspection
0e4c7c53-1549-52a0-8c75-9094534220a0 | note | Acceptance Criteria: No significant cracks, level deformation, faulty joints
e14e651e-1207-5fbd-a407-fa812f1b6225 | note | Record Documents: CCTV Footage
63c02250-fcc9-595c-b2cf-930ca1c4c93f | note | Responsibility: Contractor
d0970c56-07d8-5256-ab7e-b4773f555780 | note | Comments: CCTV footage to be reviewed by Engineers Representative and signed off via NTC / Site Instruction prior to Practicle Completion
| section | Construction and Finishing - Inlet 1-1 1400mmDia Standpipe with Scruffy Dome - Ch 220m Kopaki Rd
| checkpoint | 300.12 - Determine Subgrade Strength
0a64ea8f-7260-5b6d-8a0d-d623887a9eb0 | note | Detail of Activity: Determine bearing strength of subgrade
88b41596-7703-5c62-8d1f-7f9a08e9d972 | note | Action: H
9a74d470-694d-5856-b138-ec1987c4cadf | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
593dec1f-f899-54cc-9617-526dee3a0b8c | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
779d2171-dbd8-5f01-a2a8-2a14dd95c733 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
13e5798d-1455-5a40-80e5-737b0151ff23 | note | Record Documents: Contractor's site diary
e3a3f9c9-b269-53b9-9235-20be862b07a3 | note | Responsibility: Contractor
ef9800fb-6ba6-5597-ad22-3667a369d138 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.13 - Structures (manholes, head walls etc.)
629286e9-23a4-5f48-9dd8-2d6d8e556a17 | note | Detail of Activity: Visual inspection of concrete components
2fadf4dc-2111-5e5e-997c-721d4d64ef49 | note | Action: W
202b859f-1c8c-528a-b5c2-2c294d4fc726 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
429b847e-6438-5cc7-ac12-c0b6d9b515ec | note | Inspection / Test Method: Visual Inspection
7b3b6fd4-1209-52d8-8aa7-e06dd08f8b3c | note | Acceptance Criteria: No visible damage, especially around collars and joints
c8ff5357-4c95-5bca-a710-d049bbfdcaca | note | Record Documents: Contractor's site diary/Photos
1af4db62-a41c-54d3-98dd-4ea94f017f50 | note | Responsibility: Contractor
| checkpoint | 300.14 - Structures (manholes, head walls etc.)
df306cd3-fc84-5201-9691-e933a185dd89 | note | Detail of Activity: Bedding
92fe3efc-9219-5897-96e5-c8e6313a8879 | note | Action: M
8eb67411-9637-5cba-8972-c8d3a0891b71 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
061cfbe6-96d0-5a2d-8e7e-5c34c8cea865 | note | Inspection / Test Method: NZS 3725:2007
2b32e7e6-fc59-516e-a639-476340644826 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
e088c1ea-d929-5f4f-a3f7-0b62a7423081 | note | Record Documents: Contractor's site diary
89903dce-53e1-5c12-a0d5-bebd0c152785 | note | Responsibility: Contractor
70ddc005-9319-592a-9773-d28b3f9eabb1 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.15 - Structures (manholes, head walls etc.)
80b19db8-7614-5b6a-8de9-fe422e5a658e | note | Detail of Activity: Backfilling
307e871a-41b7-570d-ad97-d6a110c54c79 | note | Action: M
16a527d6-95a7-5b08-883e-0cb9392815a1 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
494cfe57-ae73-52b7-bf24-8fb3aa3656a8 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
7a7c4dd6-0fc2-5bfb-984d-34bd86de81e6 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
587fa8b6-a508-5a26-999d-b1addf95383a | note | Record Documents: Contractor's site diary
2f3691df-7faa-546c-81ee-8de120996060 | note | Responsibility: Contractor
966b154e-c756-5992-b0e3-2cdcd8c8caba | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Outlet 1-2 Precast Headwall- Ch 230m Kopaki Rd
| checkpoint | 300.16 - Determine Subgrade Strength
ec28ce8a-5ec2-55eb-86f4-1bc7eed09a0a | note | Detail of Activity: Determine bearing strength of subgrade
9868cd77-c82e-58ee-8d3b-446513032f69 | note | Action: H
fbb0ee79-fe9a-57c7-b477-c35e2bfb9c5d | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
8f75ed72-1ce5-5480-ade2-60213e0ce340 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
2dce6391-99c1-5ec1-88b2-748e2d535e97 | note | Acceptance Criteria: No target - Engineer to advise undercut requirements prior to installation
38b2f39e-1ccf-57ec-ace2-1b22ce1c3c2b | note | Record Documents: Contractor's site diary
0d4069f6-8672-5fcd-99e4-51caac471ac8 | note | Responsibility: Contractor
fa076e2a-d89e-5b4b-ba57-5ad22a6bc9b2 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.17 - Structures (manholes, head walls etc.)
86ac1474-c435-507b-a8dd-e65ab8203cd7 | note | Detail of Activity: Visual inspection of concrete components
3310c421-2b8a-5ae9-b1cf-4c1ea4286d6c | note | Action: W
4cfedee3-88ae-51ad-8061-38654ba39ce9 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
d0ed4fde-584b-5e14-a8c3-c4bfdec02f8e | note | Inspection / Test Method: Visual Inspection
5b55d84a-2279-54e0-815d-32d8edda8fb6 | note | Acceptance Criteria: No visible damage, especially around collars and joints
5b3011d7-6b5a-596f-8607-b1b9de70e5e1 | note | Record Documents: Contractor's site diary/Photos
2243ffc5-2a03-5b1c-9c7d-a530defc7a10 | note | Responsibility: Contractor
| checkpoint | 300.18 - Structures (manholes, head walls etc.)
c70a6900-0788-5758-9ae4-426698719682 | note | Detail of Activity: Bedding
2f403b02-0a39-58c9-b190-4226b5ef9847 | note | Action: M
82c0e993-1585-58f2-aaa7-3405f0597eea | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
c37b755e-4e74-57cb-bede-241fd59381a2 | note | Inspection / Test Method: NZS 3725:2007
61c1b957-ce1a-5566-9282-7b98023072ef | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >15 (CBR = 20).
bbb9406b-6e49-5b1f-b9b5-97be0be4302f | note | Record Documents: Contractor's site diary
956d201b-3512-510a-b8f9-fbfcb8e1015a | note | Responsibility: Contractor
e37aed33-2853-5555-a5a8-965bba5103db | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.19 - Structures (manholes, head walls etc.)
0809e035-be6a-5a82-a7f7-18b5cd95fb18 | note | Detail of Activity: Backfilling
9aa385d6-9ea8-5829-89f4-07f0b98cd3e8 | note | Action: M
fa485dd7-9562-5c8a-8e1c-09344f51dc1d | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
a5d312a3-ca3f-5429-8c01-febbf5a3559b | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
43411300-5532-5041-979d-3dcec4dbc417 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
1b7e858c-87a0-5b08-8e3a-27a875b26283 | note | Record Documents: Contractor's site diary
772131a3-a1dd-558c-a83b-5b46b5eb0715 | note | Responsibility: Contractor
4621de6d-f628-58ad-b5b8-d395ec5f55eb | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Stormwater Line 2- Inlet 2.1 to SD 2.2 @ CH65 Kopaki Road - Bradcock Access Track ( Ø900mm)
| checkpoint | 300.20 - Determine Subgrade Strength
a551ade8-4c7e-5dd6-a738-c170129e23d8 | note | Detail of Activity: Determine bearing strength of subgrade
d87c3764-00a8-5048-a5d3-43cf34dec362 | note | Action: H
06092731-c176-5ceb-8529-6e6893f8e753 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
696e0a3c-1517-5030-b736-a5ab47f14dec | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
fab23e36-5496-5551-88bc-5678593def38 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
cc68be3f-3b63-5754-9de1-87804a3b9024 | note | Record Documents: Contractor's site diary
75b88ef5-960d-55ed-800b-fad2ae5c2688 | note | Responsibility: Contractor
3fbdf450-5222-56ad-a4ce-b7b13762ce45 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.21 - Pipe bedding
464a7366-a8e6-53cb-b88a-a58fddf611cb | note | Detail of Activity: Bedding
af70221f-37e2-5e06-afff-6806825124ad | note | Action: M
242523cb-11e0-57c6-83cc-1fb101239ea9 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
44856705-47fc-51df-900a-730eaf5c6902 | note | Inspection / Test Method: NZS 3725:2007
6aec3aeb-2194-580d-8371-6f2509f6bacf | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
2886c041-c451-5dd4-b8bc-0d98bc607048 | note | Record Documents: Contractor's site diary
7732a7c6-3502-5347-b767-d09c83da0355 | note | Responsibility: Contractor
ab0f6c1a-b287-524a-99bc-5c17d04f2f1b | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.22 - Jointing of pipes
366f50fe-ef2e-5077-a752-642abf520b4f | note | Detail of Activity: Jointing
54e63045-1fe2-5cb1-8f95-9999f202e60e | note | Action: M
b41190c2-fd92-5153-ae20-de3df5f8d8c4 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): Every Pipe Joint
fac742c9-37be-548f-b70e-4dca73432dff | note | Inspection / Test Method: Visual Inspection
5894ef1a-2b28-54f1-920c-d391dd0411ff | note | Acceptance Criteria: In Accordance with section 5.2 of the Project Technical Spec.
ef63450f-e496-50cf-94ae-0b8502eac390 | note | Record Documents: Contractor's site diary
125d8832-50c8-5f55-a73c-f89777f55fc8 | note | Responsibility: Contractor
078de01b-a5b6-54af-8069-55281bb702f5 | note | Comments: Rubber rings to be mounted evenly and lined up truly concentric with pipe. Gap between spigot and shoulder to of pipes to be even and between 5mm and 10mm.
| checkpoint | 300.23 - Pipe haunching
be5b7a9b-4d32-531e-b386-584f618f4f7f | note | Detail of Activity: Haunching
85f25ccc-c7b8-5cde-80aa-329f554f1535 | note | Action: M
203b5ebf-42e4-5c52-857a-6751d72a66d2 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
b796a93f-11ca-56be-85e7-f78b53b9a885 | note | Inspection / Test Method: NZS 3725:2007
bd4b0ea2-5725-5646-a404-b09515e2f409 | note | Acceptance Criteria: In Accordance with HS2, Minimum haunching depth of 0.3D, CIV Value on compacted haunching >25 (CBR = 30).
fc11554c-7dcf-5f1c-b576-1972c9869729 | note | Record Documents: Contractor's site diary
e271f7e6-4c6d-51c6-8e2e-ad592a6f8145 | note | Responsibility: Contractor
b6f63c97-0a2a-5cb5-a6cd-c110e02059a6 | note | Comments: PAP 7 material to be used.
| checkpoint | 300.24 - Trench backfill
0781f62c-f5e3-5dbe-9621-b4399895e816 | note | Detail of Activity: Backfilling
bddfc49b-c243-569f-be63-e36e2b5d4d4c | note | Action: M
47d5f185-d10b-5541-9c96-b90703e878f0 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
af9e7465-e1ed-5f98-8c10-b2dd1c2569cf | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
4f6a6f23-1499-5d48-9a98-403c5b4a1bfb | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
817c48e5-f3be-55b7-bd16-d0661a0b4633 | note | Record Documents: Contractor's site diary
43c9bb5a-1e10-5779-af87-44b4cdfad172 | note | Responsibility: Contractor
ab1f7260-82cf-5b34-95a9-a02e6c6e8c3e | note | Comments: Clean Pumice Fill to be used
| checkpoint | 300.25 - Visual Structural Inspection
ceecf435-85d3-5325-a761-17b8397a2790 | note | Detail of Activity: Visual inspection of concrete components
972e4e23-7d9c-5656-9795-dc4a0074a207 | note | Action: W
b31a2a6e-d117-5539-b81b-85b2d904fc68 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
54b41bff-71c3-5053-8559-3b5c596307dd | note | Inspection / Test Method: Visual Inspection
87a6e7e2-8a53-547d-b9b3-91141472fbd4 | note | Acceptance Criteria: No visible damage, especially around collars and spiggots
92dd6cdd-b5ef-5445-87ed-71f728a0eb62 | note | Record Documents: Contractor's site diary/Photos
63e52dce-866a-5d02-a43d-2752e55a7315 | note | Responsibility: Contractor
| checkpoint | 300.26 - CCTV Inspection
fce25802-da77-514b-83a4-6557e19f0f6b | note | Detail of Activity: Visual record of Existing works
93995f4e-e8aa-5817-aebb-3ccbee27122e | note | Action: W
3171c9ae-04a2-50da-9e45-dc0b524ebde3 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage pipelines
beca50ce-dc44-5f71-af55-cb73af9c8068 | note | Inspection / Test Method: CCTV Inspection
886c5489-65ed-5045-a8f1-759e9977be67 | note | Acceptance Criteria: No significant cracks, level deformation, faulty joints
d10f9b81-0a5e-5b9d-a5f7-bc26c15f321b | note | Record Documents: CCTV Footage
82185ff5-9487-5267-9540-05811f1751f6 | note | Responsibility: Contractor
84870904-2027-57fc-90aa-672ec00d36da | note | Comments: CCTV footage to be reviewed by Engineers Representative and signed off via NTC / Site Instruction prior to Practicle Completion
| section | Construction and Finishing - Inlet 2-1 : Precast Headwall Bradcock Access Track ( Ø900mm)
| checkpoint | 300.27 - Determine Subgrade Strength
f3e17526-73de-5d9e-82ac-f6ea010b2d0a | note | Detail of Activity: Determine bearing strength of subgrade
09468573-5604-5a9e-8011-d9f6f0d326c8 | note | Action: H
40f42fec-3bd8-5114-a443-6f7198f7d1cc | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
c0049c8f-6016-52c7-a4bb-91936f4b37e3 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
0f06e0b9-52df-5fae-9f29-baa7196f3c19 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
c91f2db6-7f37-5117-a3f6-082bb7b729fb | note | Record Documents: Contractor's site diary
87952081-5cf5-5dcd-b0ed-7919158c6065 | note | Responsibility: Contractor
5b4996d2-9f8a-5dba-8408-48918451d4b5 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.28 - Structures (manholes, head walls etc.)
f732c435-49e6-5008-87f3-3c7a78982418 | note | Detail of Activity: Visual inspection of concrete components
2b617aab-c81c-5e26-9304-10d9920fea8d | note | Action: W
c0a48435-4be4-52ba-a1c8-11a2aa34f3d0 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
48e68c32-0645-57ee-9b6d-958508929639 | note | Inspection / Test Method: Visual Inspection
4120efdb-bc1e-5ac5-a9d4-a0893258295b | note | Acceptance Criteria: No visible damage, especially around collars and joints
a91b140c-4e94-5370-b798-65161468aa9a | note | Record Documents: Contractor's site diary/Photos
85c40a3c-4dd2-5a0a-8be2-e3f8c6907e47 | note | Responsibility: Contractor
| checkpoint | 300.29 - Structures (manholes, head walls etc.)
e83c028d-4b1d-5ca5-9897-894304beca4e | note | Detail of Activity: Bedding
33f770d0-0eb7-5a2d-9de6-255b7c1ee1a7 | note | Action: M
d98fd0c5-b062-5e93-83c4-5ac94c41ff08 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
442d1645-715e-5719-80e4-1ba7d5bca5bb | note | Inspection / Test Method: NZS 3725:2007
050a2083-1198-5187-b03d-95135c84f11b | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
fe06abed-577f-58dd-b88f-9edc8e891381 | note | Record Documents: Contractor's site diary
cd648be6-05fa-579d-96a9-3603a2909817 | note | Responsibility: Contractor
943fb758-d69a-5e93-b3c0-5529a06a60fc | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.30 - Structures (manholes, head walls etc.)
ccfece17-1e7a-57a2-8afb-6052b40ca35b | note | Detail of Activity: Backfilling
bfb8c379-50f0-56e5-b93b-3709e14cf951 | note | Action: M
92669232-8a8a-5c81-bad5-d907e03d12a0 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
3d5edbce-09e0-5511-8281-50194d114041 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
5b68350c-9d79-5597-a011-8dc1dc10d280 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
f58cc4e2-788b-5710-ad2a-54fd61234fdf | note | Record Documents: Contractor's site diary
dee9dfc8-087a-5321-992b-454c23647253 | note | Responsibility: Contractor
49cc8b78-72a5-5144-95da-6676b2b94e97 | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - SD2.2 Manhole/Standpipe with Scruffy Dome Bradcock Access Track ( Ø1650mm)
| checkpoint | 300.31 - Determine Subgrade Strength
82cab35c-a1d8-54e2-a654-7db4c2b72b4c | note | Detail of Activity: Determine bearing strength of subgrade
faad82c5-bffb-5a74-aa25-45c16b3e04aa | note | Action: H
1f4f9192-bb26-5197-9ab7-a06599ec11b7 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
89abd8dc-6096-5668-a874-a46b89599ac2 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
46ad1238-68ab-5cbc-9023-972f77ac178d | note | Acceptance Criteria: No target - Engineer to advise undercut requirements prior to installation
be842af1-cd55-525c-8736-093b6531e69a | note | Record Documents: Contractor's site diary
41319a4c-9a93-5c42-adee-878f7797d74a | note | Responsibility: Contractor
e84ca942-80f6-5359-9951-474b045233b5 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.32 - Structures (manholes, head walls etc.)
ee255cc5-3fc1-5ac4-a7e6-88ecdd097db5 | note | Detail of Activity: Visual inspection of concrete components
cc7c9f15-c34a-5ae7-a41c-6dbea2256eb4 | note | Action: W
5ff563c5-4d40-501c-a31d-58ff5ce09f9a | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
0f2d62de-9484-5947-b23c-4c39875a8657 | note | Inspection / Test Method: Visual Inspection
ca919e66-ebd9-50a3-b36f-0be5dd0484d9 | note | Acceptance Criteria: No visible damage, especially around collars and joints
bb47772d-f1e3-506e-ac5f-952aff73fdaf | note | Record Documents: Contractor's site diary/Photos
b8b36854-86de-541c-9367-d3d0d6053763 | note | Responsibility: Contractor
| checkpoint | 300.33 - Structures (manholes, head walls etc.)
eeb759b7-3676-530f-811a-b4338d6ba044 | note | Detail of Activity: Bedding
3091c5c6-d8cb-504b-8ac6-5ef7279094ab | note | Action: M
bf882ad5-5804-5ce4-aa7c-6dabe46a6a8f | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
0d1db9c0-d63d-5f9f-b9d4-bd4fa61734ef | note | Inspection / Test Method: NZS 3725:2007
e7c81df3-4c13-5f79-bf5d-6417c1703837 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >15 (CBR = 20).
ed9ab2aa-0469-5a3f-9ef7-201bb68fad55 | note | Record Documents: Contractor's site diary
c608d733-2a0f-5b90-a0f1-011d7e71c8ba | note | Responsibility: Contractor
b7a52e2c-71a2-542a-b87a-f29d4a6e8f62 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.34 - Structures (manholes, head walls etc.)
7c8fbc55-811c-57ab-b733-23826b659d8a | note | Detail of Activity: Backfilling
cbeca5da-4ada-5834-8d3d-fb365287db3b | note | Action: M
df49c710-a18d-54dc-abea-eece8f2b8977 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
9aa7864b-b42b-54b6-96b1-6201072d8fc6 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
f9248d55-6afa-5b4c-a741-8094b05d4d63 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
410653b2-7642-5424-b60b-84f4703907fc | note | Record Documents: Contractor's site diary
5729cd9b-1ab7-5623-8df0-bf15d1b5e4cb | note | Responsibility: Contractor
6189300a-04f6-597b-9797-af2c791026cd | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Stormwater Line 2 - SD 2-2 to Outlet 2-3 Kopaki Road (Ø900mm)
| checkpoint | 300.35 - Determine Subgrade Strength
e62a7a1d-8bc0-5411-b8b8-d31ab73c4d71 | note | Detail of Activity: Determine bearing strength of subgrade
a130738f-4dc2-54c9-ab86-3084401aff35 | note | Action: H
462386f1-9e81-565b-a789-634c4db077b7 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
6900c3c5-9401-5bc6-a913-955f73ea6f6a | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
b56af196-d840-559d-a455-d9311cad9da5 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
21079baf-d9e4-5ee7-ae08-fc011ace1b51 | note | Record Documents: Contractor's site diary
2dc8bc14-fb2a-5039-9ca3-3e37b53ba746 | note | Responsibility: Contractor
5b2c8d36-a21f-5356-b0ca-cb81a6dffbb4 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.36 - Pipe bedding
e46b235e-87f4-583f-992c-7cdafbd6acd6 | note | Detail of Activity: Bedding
07ce8bf3-4f36-5820-84b5-e083d561284a | note | Action: M
8a5a5812-1fec-5631-847a-6171dfed7e19 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
ecfbef21-6931-57ad-aa8c-91475fb5cf4a | note | Inspection / Test Method: NZS 3725:2007
6abbe4f2-1501-5782-8f27-8243901739e0 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
b28b1558-34cf-589b-8350-50ca84dfae2f | note | Record Documents: Contractor's site diary
ded2593c-4d56-5472-8e29-38549d067f27 | note | Responsibility: Contractor
811ed986-9025-5ef3-bcf1-ab29605b3558 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.37 - Jointing of pipes
cfeea789-928e-5e7c-ac04-70f83ea5b09f | note | Detail of Activity: Jointing
53654a1e-10a1-5570-8c90-ce808e827671 | note | Action: M
eefb4c61-c3e0-5222-9e8d-1d81918d0b13 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): Every Pipe Joint
e5ffacee-d62c-55a5-b860-7820b5c7495e | note | Inspection / Test Method: Visual Inspection
c92bcc8d-9c93-5525-958d-e205e3c1475a | note | Acceptance Criteria: In Accordance with section 5.2 of the Project Technical Spec.
39337bad-b528-5848-b584-8c446764001e | note | Record Documents: Contractor's site diary
92c62f6e-15fe-5bf8-bd9d-ee3dc492216f | note | Responsibility: Contractor
48e8516f-6c3c-5247-9edf-0b2b8c3a78a9 | note | Comments: Rubber rings to be mounted evenly and lined up truly concentric with pipe. Gap between spigot and shoulder to of pipes to be even and between 5mm and 10mm.
| checkpoint | 300.38 - Pipe haunching
47595875-8bf1-5eae-a820-695df1e9a6f1 | note | Detail of Activity: Haunching
454eea90-ab6c-546e-a93b-c808579bf762 | note | Action: M
8b59236c-2b0e-5845-8386-a54850c3bfaa | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
649fd7aa-75a9-5017-bf16-666dcd38609d | note | Inspection / Test Method: NZS 3725:2007
b620dd2d-11f5-548a-a6f5-cc08633e158c | note | Acceptance Criteria: In Accordance with HS2, Minimum haunching depth of 0.3D, CIV Value on compacted haunching >25 (CBR = 30).
e55bd942-947d-5939-83cd-60f254e32196 | note | Record Documents: Contractor's site diary
c5544100-6dcb-5397-9e42-3f9ccadacbc9 | note | Responsibility: Contractor
6d2916b5-3de9-531b-8039-d9cc2f4554fb | note | Comments: PAP 7 material to be used.
| checkpoint | 300.39 - Trench backfill
8be20c8f-de31-5bde-83ca-f65f0256f042 | note | Detail of Activity: Backfilling
c3797c54-30e3-5e1a-aa68-1a72134c3043 | note | Action: M
1701d65d-2b8f-516a-ba3e-671735799927 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
91f1e075-4ec0-552b-a99e-8b7049b25bef | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
4cfb4367-ab9f-5ffa-86be-b0cd67c70dbc | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
c04a0114-66f4-567b-8592-bdde171e1cc4 | note | Record Documents: Contractor's site diary
98fef729-ff83-5924-b6de-31ddcd9ad046 | note | Responsibility: Contractor
daa57fb0-cf4a-58eb-859b-228838f29448 | note | Comments: Clean Pumice Fill to be used
| checkpoint | 300.40 - Visual Structural Inspection
8778a6d9-c3c4-5595-a9a0-afde7525b131 | note | Detail of Activity: Visual inspection of concrete components
e5ce56dc-3c8d-5b4f-af59-b8ceda441ee8 | note | Action: W
13158716-ef61-54ce-9b24-dcc7f39d0280 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
3a8e15fa-abc0-5209-9a38-b76b925da55a | note | Inspection / Test Method: Visual Inspection
b1ca22aa-c6f7-56c0-ac0a-65b2957a0983 | note | Acceptance Criteria: No visible damage, especially around collars and spiggots
8f59bb98-bc34-5f65-b9be-bbff04dfc67e | note | Record Documents: Contractor's site diary/Photos
dc375a5b-46d5-55d9-8cff-a5d807bff5db | note | Responsibility: Contractor
| checkpoint | 300.41 - CCTV Inspection
f0c46c41-72eb-57df-a3de-ca3a860992ac | note | Detail of Activity: Visual record of Existing works
9a671fa2-e7a4-50dc-8c66-8aa9d98cc549 | note | Action: W
ae0e77ab-fab9-5b5b-9ba2-2fb85450ced1 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage pipelines
239df559-39eb-56c6-8823-5df21bb01acb | note | Inspection / Test Method: CCTV Inspection
e600f208-811e-538a-8d22-77f8b3885a46 | note | Acceptance Criteria: No significant cracks, level deformation, faulty joints
1cdaf91d-cfdd-5f13-9847-b5df0e8dae9b | note | Record Documents: CCTV Footage
7cb14bf0-84a6-57e3-ba95-2e45bd5a8ade | note | Responsibility: Contractor
846f8af4-1aad-507b-a134-e8cc0dab8d9b | note | Comments: CCTV footage to be reviewed by Engineers Representative and signed off via NTC / Site Instruction prior to Practicle Completion
| section | Construction and Finishing - Outlet 2-3 : Precast Headwall Kopaki Road ( Ø900mm)
| checkpoint | 300.42 - Determine Subgrade Strength
c710e810-7546-596e-bd8b-b1509cd93c16 | note | Detail of Activity: Determine bearing strength of subgrade
a0183614-26bf-54cc-b59a-f395aa7983ff | note | Action: H
3484fa9d-f9b7-540e-b26b-06dbf82a597f | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
9daf94e4-8092-5f3d-8606-1f81b05d028f | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
45c515f0-a977-516a-9b5f-1cf5deb0f213 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
797c81e1-5f32-5a2e-bf5b-649de1d33b3f | note | Record Documents: Contractor's site diary
2653f39e-09d6-5d5e-9e88-b268f44de079 | note | Responsibility: Contractor
5433b69c-3ddb-515e-87e1-3f318c256b39 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.43 - Structures (manholes, head walls etc.)
c9b36131-cabb-5bd1-b5c6-c463974e52df | note | Detail of Activity: Visual inspection of concrete components
40848ce7-46fb-55d6-ac82-a9f679cefdc6 | note | Action: W
1351d2f6-bbe0-576e-ba09-a825ee052d5f | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
5ebc7ce4-6d95-5e61-9ab9-544974f6347a | note | Inspection / Test Method: Visual Inspection
eca544d8-6747-51a6-8cd6-ace628d7244f | note | Acceptance Criteria: No visible damage, especially around collars and joints
5fe805f8-e730-5e96-9819-996cb2b1345e | note | Record Documents: Contractor's site diary/Photos
a0e41c38-b3a5-5d43-8bf4-711c5c6e6075 | note | Responsibility: Contractor
| checkpoint | 300.44 - Structures (manholes, head walls etc.)
9f3e44c5-f4b4-5fc0-9ed5-a0d1aec7f3a4 | note | Detail of Activity: Bedding
2b7fd318-fc80-5e85-bbb6-22263bc7bb02 | note | Action: M
d65dd2cc-3c13-5e28-82d6-016620e99ab3 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
8375878a-25e2-5943-9679-47a6ca60ad57 | note | Inspection / Test Method: NZS 3725:2007
92d78725-93b0-5843-bf32-fdcb331daedb | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
b99a53df-6bac-560b-8180-569b64c4e1c6 | note | Record Documents: Contractor's site diary
e1945b14-e8a3-5474-8869-6d7aaac6ddc5 | note | Responsibility: Contractor
5124a3fe-fe67-5a6f-8cbd-4b02502df4c5 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.45 - Structures (manholes, head walls etc.)
f2465cab-03a2-5d5d-a042-3482df1205da | note | Detail of Activity: Backfilling
8b5c716e-9438-5832-801c-29921b58a3c0 | note | Action: M
86391dbd-3564-542b-82f9-d2140f192d70 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
e9fbb215-6a21-594c-8c4b-e5dc861764f1 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
665d0412-997f-59a8-a0d5-624db2f7f9b0 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
20e868e2-550c-527d-aae0-0fb3561f3821 | note | Record Documents: Contractor's site diary
eefd2637-1eea-510d-b0b4-4b8479b0ceaf | note | Responsibility: Contractor
a378081f-7538-5826-83c6-76765695088d | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Inlet 2-4 : Precast headwall/wingwall - CH 290 State Highway 30 (Ø1050mm)
| checkpoint | 300.46 - Determine Subgrade Strength
e06a220a-8fca-526d-b374-520325982ef0 | note | Detail of Activity: Determine bearing strength of subgrade
6b96314c-5e13-5478-ac96-616957ed48a0 | note | Action: H
ea9e818c-e8ac-5540-9e63-c08ae103c4f8 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
c719bb6d-b363-5062-b414-380dc5a35af5 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
6155f655-c5fc-5f3a-988e-6c3003bf54aa | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
46fcf5de-9ab6-5d9b-8875-edd72bc8bab8 | note | Record Documents: Contractor's site diary
aa597012-b1a3-5970-959c-9ce37a50a14a | note | Responsibility: Contractor
c9034910-c5c2-5b80-82dd-216277b0226c | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.47 - Structures (manholes, head walls etc.)
8b442316-f051-5453-9f54-d4e9d3d38a18 | note | Detail of Activity: Visual inspection of concrete components
3a333a4c-294d-588c-b59a-945a19de5f0b | note | Action: W
f38236d6-ce75-500c-858d-e7154e3d9564 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
cec8562d-e3d5-5603-8661-3b730d8021fd | note | Inspection / Test Method: Visual Inspection
9bc4ae90-4ea0-53e1-bc60-79a9d65aa42d | note | Acceptance Criteria: No visible damage, especially around collars and joints
435df944-a745-5ec2-b966-5e2d313d11eb | note | Record Documents: Contractor's site diary/Photos
ee07da0c-5ba4-583c-bea0-b7fd0e26d2a7 | note | Responsibility: Contractor
| checkpoint | 300.48 - Structures (manholes, head walls etc.)
827db2d1-e230-59b3-8391-0585200b5d2a | note | Detail of Activity: Bedding
c2ada11b-2b33-521a-80df-4b41c1e17f07 | note | Action: M
b78c88f5-199d-5542-90d6-26531da2390b | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
9fe8985f-8c9b-5b42-9358-49fb71f6a3b8 | note | Inspection / Test Method: NZS 3725:2007
2fae9a1c-fe38-59cc-ae2b-a2f78c66a299 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
ef323d32-f279-5f9d-a8cd-b7f604c9b0cb | note | Record Documents: Contractor's site diary
1d1e9277-f3f9-537c-9a6c-42d81a012b6e | note | Responsibility: Contractor
dd30a8bf-2891-585a-94a4-113d855f3f88 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.49 - Structures (manholes, head walls etc.)
388ce5d0-3f1e-5a43-8845-9ff857245b32 | note | Detail of Activity: Backfilling
74ba4df9-40be-5b82-9c0e-b98b1f704a41 | note | Action: M
d440617d-6ce8-5f46-a145-081b38f9e98a | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
29b16c2b-3024-5223-94fd-e0ee07a6ddad | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
60f39f31-1e06-53de-bbf9-d5a379857649 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
2aaa76a3-4177-5ce0-b9e5-1b8afe89bb5c | note | Record Documents: Contractor's site diary
e7281509-f9bf-58ae-8534-992ea64d8e32 | note | Responsibility: Contractor
2c22ad5b-80fc-55c4-9640-68ccc27e0aa3 | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Stormwater Line 2 - Inlet 2-4 to Outlet 2-5 : Statehighway 30 (Ø1050mm)
| checkpoint | 300.50 - Determine Subgrade Strength
dbdcda89-6382-5b4f-bc6a-7c369c072c0f | note | Detail of Activity: Determine bearing strength of subgrade
32828512-21c1-5b1e-a9e7-e8e83d13067d | note | Action: H
48a88cbb-6618-5236-bb25-d5c209f2ba94 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
7548ff3a-0962-516b-a790-8c6e1a72636a | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
8d5860c6-ae74-5675-bbaf-cb2b4ef4f031 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
2f75562d-4cde-53ee-b3ff-94d9fef96ce3 | note | Record Documents: Contractor's site diary
e9981e0c-6779-5c60-8513-17be04c74dfc | note | Responsibility: Contractor
1e80823c-715d-597d-bb9b-92313d36312c | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.51 - Pipe bedding
79f5e172-11da-5a72-a746-ca3e15647cf8 | note | Detail of Activity: Bedding
7f00c230-f87d-5fa8-be84-9edd0d2b57b8 | note | Action: M
d8e07324-5e77-5e49-b646-49325e43bcb7 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
1415eb66-c87b-5459-b5df-82019070577c | note | Inspection / Test Method: NZS 3725:2007
f5b6ebda-f77a-5beb-8654-bcdbacdda33d | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
4455ba10-bce8-5437-8990-e44b451cbc0f | note | Record Documents: Contractor's site diary
3b29712f-2e45-5db8-855c-38d0dc6378b0 | note | Responsibility: Contractor
f2bc473a-99a4-5d0c-8a6e-66909c95c0da | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.52 - Jointing of pipes
79711d62-b049-58bc-b650-ee39d3047c8f | note | Detail of Activity: Jointing
2cb71cec-7181-5dba-929c-9cb65588f393 | note | Action: M
a7e29960-d337-5ed2-add7-22cfa70c8ab0 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): Every Pipe Joint
16a5808e-465c-59d8-a545-e0d690822bf3 | note | Inspection / Test Method: Visual Inspection
54b25422-4590-514a-8eb3-e7bf43b6dc7f | note | Acceptance Criteria: In Accordance with section 5.2 of the Project Technical Spec.
2c99e850-f584-55ab-abc2-fb24066d476c | note | Record Documents: Contractor's site diary
7d33601d-0e7b-539a-a66e-bab0552ce2ad | note | Responsibility: Contractor
51dfdc74-9320-564b-aa21-6173448944af | note | Comments: Rubber rings to be mounted evenly and lined up truly concentric with pipe. Gap between spigot and shoulder to of pipes to be even and between 5mm and 10mm.
| checkpoint | 300.53 - Pipe haunching
250613d3-20de-5853-a2eb-54a983a2405f | note | Detail of Activity: Haunching
9eab8494-b99d-5d19-ae83-37e3ff786e35 | note | Action: M
564b3876-424b-52be-a778-f7441b9b767a | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
a4eba41e-d097-5130-9510-8ddf4f2cb07d | note | Inspection / Test Method: NZS 3725:2007
1e261869-af57-5f58-b335-371ffd97631d | note | Acceptance Criteria: In Accordance with HS2, Minimum haunching depth of 0.3D, CIV Value on compacted haunching >25 (CBR = 30).
4f58d5a6-5c74-5760-9acf-c9884ae9fe40 | note | Record Documents: Contractor's site diary
6ed477d5-e376-5a3d-9853-50cd9f281c22 | note | Responsibility: Contractor
f778a771-786c-5efc-8515-e65db40f91d3 | note | Comments: PAP 7 material to be used.
| checkpoint | 300.54 - Trench backfill
1f3bea28-9715-540f-a840-1b5df579caa9 | note | Detail of Activity: Backfilling
2c3c7011-d8c5-5256-b262-fa3b61dbf9ac | note | Action: M
b4138d79-e646-536a-8640-0805efe02b9c | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
135d6687-9b27-5894-89c8-6e3c30cf80b1 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
44caec41-585f-5ed7-b3b3-67dcdef9b40c | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
6e51abbc-c7fc-5961-b9ff-53c15b31e4b8 | note | Record Documents: Contractor's site diary
d7c55b88-dae5-5be2-8a25-d6a6e36a94c4 | note | Responsibility: Contractor
ef8fb887-9eca-5a08-a8c2-ec34190e49f4 | note | Comments: Clean Pumice Fill to be used
| checkpoint | 300.55 - Visual Structural Inspection
fb23d105-45d6-5641-9231-42ee136fb67f | note | Detail of Activity: Visual inspection of concrete components
ae971849-fee4-5b07-9e23-7be2940bc16c | note | Action: W
f508f8b6-c7a9-5396-8978-a49f52e28f09 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
fa17e889-1c0c-52a7-81c9-f5659b70e092 | note | Inspection / Test Method: Visual Inspection
434cfa88-d749-58a7-a280-04ad532ee394 | note | Acceptance Criteria: No visible damage, especially around collars and spiggots
dd48d700-a9e1-597a-a450-9e5d8642773c | note | Record Documents: Contractor's site diary/Photos
2c536688-c43f-53ac-8005-f7ac4d569b65 | note | Responsibility: Contractor
| checkpoint | 300.56 - CCTV Inspection
cda20009-e9d1-57eb-ba01-5af349d40aaa | note | Detail of Activity: Visual record of Existing works
99ad31fe-8f50-518d-9457-315aca1ac7fb | note | Action: W
15a2a3a9-1753-5cae-a0ec-33418133721d | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage pipelines
7b8feac7-9dae-5507-ae76-33f80171678c | note | Inspection / Test Method: CCTV Inspection
10f0f7c9-5e12-5a96-b1fe-137a05504a8e | note | Acceptance Criteria: No significant cracks, level deformation, faulty joints
06564585-6c59-51b9-ab14-6a51f964e7c1 | note | Record Documents: CCTV Footage
a1fdc620-c76a-5754-861b-c5af44e4bb23 | note | Responsibility: Contractor
0ce25917-122b-5cf3-8660-932e680a8151 | note | Comments: CCTV footage to be reviewed by Engineers Representative and signed off via NTC / Site Instruction prior to Practicle Completion
| section | Construction and Finishing - Outlet 2-5 Precast headwall/wingwall : Statehighway 30 (Ø1050mm)
| checkpoint | 300.57 - Determine Subgrade Strength
43234a41-6338-5194-8901-cdf7c523b938 | note | Detail of Activity: Determine bearing strength of subgrade
3692895c-4063-5600-84ac-0916cd01238d | note | Action: H
b844c143-3e58-5917-a7fb-520543345cb5 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
5638113d-21cc-5dcf-b92e-2328b094e1cf | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
1863b104-d398-5daf-88bf-d59e929d4eb5 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
76120239-ea2d-5b33-be0e-92b5c1c226bb | note | Record Documents: Contractor's site diary
d6142747-3670-5a7f-913f-a24c1eca0b00 | note | Responsibility: Contractor
c5a4f7aa-65b4-5535-baab-57fce8603363 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.58 - Structures (manholes, head walls etc.)
20ae46f3-8216-5923-add7-33bdc358bc4d | note | Detail of Activity: Visual inspection of concrete components
6d047be5-755a-5264-b926-7e92a6dcc869 | note | Action: W
716185a3-c342-5e7e-a5c7-c76a176540f7 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
37ab3339-59df-5943-9ca3-da2b8cc4beff | note | Inspection / Test Method: Visual Inspection
49e4baa9-18a6-5eb0-9ec1-a65fa89422ec | note | Acceptance Criteria: No visible damage, especially around collars and joints
5fbfd90a-738a-5b57-a870-35324b4625fd | note | Record Documents: Contractor's site diary/Photos
945b34b1-db0c-5186-aa13-a7f0aaa821c5 | note | Responsibility: Contractor
| checkpoint | 300.59 - Structures (manholes, head walls etc.)
00231d93-eb5f-58d3-b73b-9078c23577f2 | note | Detail of Activity: Bedding
8040a041-d85a-51b8-bb12-f18c2644972b | note | Action: M
5e376528-ae4e-53b1-acd4-c807c646d97a | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
f9c66b0a-5c63-59c0-98a0-0ae4cd41df82 | note | Inspection / Test Method: NZS 3725:2007
2544b655-1132-5dfa-b1af-0da143b7b4d8 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
a9a9f852-1baa-536c-9eea-0b61dc2d52a8 | note | Record Documents: Contractor's site diary
140ed6c3-50ff-5953-ac05-7af3789a65ff | note | Responsibility: Contractor
5fb3713a-58cf-56f1-acce-105764c38d57 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.60 - Structures (manholes, head walls etc.)
5fe83458-1721-5d3b-a2a5-fe2a2863561e | note | Detail of Activity: Backfilling
784f37b2-e940-542b-801b-cc30bba97e39 | note | Action: M
091a8ea1-ff01-5e84-ae53-59b52c13aba4 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
417ab375-d87c-5fc9-8ae8-b9e7c007e5fc | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
eb21f44c-df3c-56c4-a871-6545b1408ecf | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
e0ae6fae-d5f6-53a9-bcfd-f891a2df37a0 | note | Record Documents: Contractor's site diary
b8ef8fc2-c96a-55c6-b5d8-85490b763514 | note | Responsibility: Contractor
547ed107-4c0b-545e-ba39-d0b67feeb587 | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Stormwater Line 3 : Inlet 3-1 to SD 3 -2 @ CH 410 Statehighway 30 (Ø750mm)
| checkpoint | 300.61 - Determine Subgrade Strength
f02af9ab-85f1-5d89-ab81-789b74dcc926 | note | Detail of Activity: Determine bearing strength of subgrade
a95bd3eb-ee28-5952-9d81-fcc0464097bc | note | Action: H
97af8504-f54a-5fbf-b8cc-9bd5258c5677 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
d85e7a95-f5d7-5815-ba87-48f0e79a6dd7 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
acaaaf51-bcc3-56e0-a3e4-10dcee156b09 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
ae1e7e42-0dc3-50ca-84c5-bb4365d4b683 | note | Record Documents: Contractor's site diary
4be51685-e92e-52d9-a0ee-0711b9705d61 | note | Responsibility: Contractor
8883a3c4-70e3-525c-8c48-3aa66ea4a079 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.62 - Pipe bedding
1a044e55-324f-5886-927f-13b838eeafce | note | Detail of Activity: Bedding
909aa130-50cf-5917-b77e-9d14c282da4d | note | Action: M
c88bb1e8-8923-5e2f-b73c-109482a1ea31 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
b54d3900-a418-5156-a9d5-1fa0cfa81823 | note | Inspection / Test Method: NZS 3725:2007
ee010012-b141-5434-b386-5e5b03fb504b | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
a463e3e1-12ed-5629-a007-3f6a2fc1ea12 | note | Record Documents: Contractor's site diary
bb39d057-47eb-583a-b006-1727db549d1f | note | Responsibility: Contractor
9a84e1a9-b515-55e6-b957-c7a56d819a5e | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.63 - Jointing of pipes
f87ba462-24ce-596c-be02-589653fad26f | note | Detail of Activity: Jointing
68e87a6a-5b8e-525f-b342-a81f3c1267d5 | note | Action: M
0c4cc371-d6bb-536c-ac3d-7bb8b2ae301f | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): Every Pipe Joint
6a7229c8-528c-58b6-a166-b8f835fa9a76 | note | Inspection / Test Method: Visual Inspection
f290f9d2-4d4b-595b-a86b-09aca6dc4feb | note | Acceptance Criteria: In Accordance with section 5.2 of the Project Technical Spec.
b5739f1d-d0f8-5f07-90ce-594e00bd695a | note | Record Documents: Contractor's site diary
34683dd5-b295-58d0-a152-3918d461a26f | note | Responsibility: Contractor
de711f17-9205-5417-b7e1-b61609e53f6f | note | Comments: Rubber rings to be mounted evenly and lined up truly concentric with pipe. Gap between spigot and shoulder to of pipes to be even and between 5mm and 10mm.
| checkpoint | 300.64 - Pipe haunching
a4067e83-b6eb-5be3-a46a-05767bc020c6 | note | Detail of Activity: Haunching
e22c422a-c93e-5814-813a-e1b73787d1b1 | note | Action: M
92c013ca-98ff-593e-b89a-0be5d571099e | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
11d2e6c7-9ff7-5e65-886e-77c9d5b4f5a1 | note | Inspection / Test Method: NZS 3725:2007
75406d6d-4daf-5b0f-b7b3-0348c2fcb614 | note | Acceptance Criteria: In Accordance with HS2, Minimum haunching depth of 0.3D, CIV Value on compacted haunching >25 (CBR = 30).
5b4c2077-1272-55c2-80a7-702e6f3bbde6 | note | Record Documents: Contractor's site diary
e29755fc-7067-5d52-8d6d-40bb094c985d | note | Responsibility: Contractor
da8af49a-2cf4-56b7-9b22-9d717fbfbb51 | note | Comments: PAP 7 material to be used.
| checkpoint | 300.66 - Trench backfill
658d96d9-6951-5b9d-94f1-98df864e8bd0 | note | Detail of Activity: Backfilling
065fdebc-2ac8-5886-9ab8-8276fd914bee | note | Action: M
62cf0f2e-8e89-58c1-b1a9-b1ea03d60bac | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
d8551f03-a86f-547e-a40e-0d2fd4a7c812 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
9192f0e4-229e-51e5-9c9b-485008c966dc | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
f4f1fa57-8edb-5560-a771-d2391e13d23a | note | Record Documents: Contractor's site diary
8949a1f2-fc10-57f9-96fb-d4adfcb75e3e | note | Responsibility: Contractor
b2ec7d92-9c0d-55d5-85ba-704dc9c1b67c | note | Comments: Clean Pumice Fill to be used
| checkpoint | 300.65 - Visual Structural Inspection
9bb8111b-5421-5f9d-8260-230b600d65f4 | note | Detail of Activity: Visual inspection of concrete components
a2e2a2d2-7ee8-550f-94c9-5f7ca033a5d8 | note | Action: W
658a3904-53ea-57b1-bc22-1efa73225913 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
48525d7e-0d04-5cbd-8a9b-6c622a2abe13 | note | Inspection / Test Method: Visual Inspection
d888264e-d23c-5e65-bf92-5f0caf600690 | note | Acceptance Criteria: No visible damage, especially around collars and spiggots
8e30f97a-1821-5f2a-a007-5003da60587a | note | Record Documents: Contractor's site diary/Photos
8b35d61c-ae22-56a6-981d-6327ad4f11fc | note | Responsibility: Contractor
| checkpoint | 300.67 - CCTV Inspection
765e91b4-e146-5d87-8586-81e32e1b9c88 | note | Detail of Activity: Visual record of Existing works
965a72e8-e2e8-5662-80ef-a9a1869b347d | note | Action: W
b2af7c33-17e4-51f6-81ae-f90d409697c9 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage pipelines
9ccf24eb-4fb8-55c9-9acd-b89b27bc0bce | note | Inspection / Test Method: CCTV Inspection
99ce831a-b822-522a-9ac2-343a223f05b8 | note | Acceptance Criteria: No significant cracks, level deformation, faulty joints
13670825-1c16-5f44-bb3c-32bb8a571b28 | note | Record Documents: CCTV Footage
40e7fdf2-3c45-5aa8-8da0-657285a8e340 | note | Responsibility: Contractor
39ab0faf-9a8f-5204-81ed-06f72d2aa196 | note | Comments: CCTV footage to be reviewed by Engineers Representative and signed off via NTC / Site Instruction prior to Practicle Completion
| section | Construction and Finishing - Inlet 3-1 : Precast headwall/wingwall - Statehiway 30 (Ø750mm)
| checkpoint | 300.68 - Determine Subgrade Strength
1f85c6e2-7340-5bc8-a759-6c2c51845bae | note | Detail of Activity: Determine bearing strength of subgrade
152d781e-3014-54d2-8a04-f231deefa921 | note | Action: H
cd613f77-e999-5236-a7f3-dad63b0ac6f7 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
59b77435-a453-568b-b6bc-1ae432e6733f | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
0dcb7c39-8286-5c13-a7f5-f35367da74fc | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
aabd8924-19de-5803-9968-2ddd2d9ecd02 | note | Record Documents: Contractor's site diary
9893f6a1-f9ab-505a-a958-d266b61ae1c4 | note | Responsibility: Contractor
1401ab34-fd49-506f-b0b9-10fa2fe2ff19 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.69 - Structures (manholes, head walls etc.)
6d711332-1693-56a3-b592-71585501e049 | note | Detail of Activity: Visual inspection of concrete components
d72259c5-0676-55ad-8645-409f6a8130bb | note | Action: W
d9d61c5b-e766-51b7-b664-8131e1ac36bc | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
27a9c469-7df5-5a58-840c-11ddeffae298 | note | Inspection / Test Method: Visual Inspection
38eb582c-8a57-563c-9287-96614e491d5c | note | Acceptance Criteria: No visible damage, especially around collars and joints
e28ccef0-4b07-504d-acba-357157bb3d89 | note | Record Documents: Contractor's site diary/Photos
e0b755f0-cbe5-5267-bfa4-a837cc8ffa03 | note | Responsibility: Contractor
| checkpoint | 300.70 - Structures (manholes, head walls etc.)
7ba90eab-e916-5549-99fc-4f00abb5d1fb | note | Detail of Activity: Bedding
4acc660d-8e0b-55b0-bb7a-15b2dcd521f3 | note | Action: M
7731b20d-0f1d-5388-b585-089ccb6a7f2c | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
30cbb894-60e5-5f58-a254-063e653f15ed | note | Inspection / Test Method: NZS 3725:2007
0ea56efd-d166-5095-8a9e-449b4c3a99e9 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
80eef0dd-252a-50c2-a5ce-8965694b5078 | note | Record Documents: Contractor's site diary
e38ee671-fd77-5c5f-a9ec-d4e88c6f8a68 | note | Responsibility: Contractor
6f903789-57b9-5509-b338-a7492c42d470 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.71 - Structures (manholes, head walls etc.)
cc35ce38-eb23-56dc-823a-3e3d96f17638 | note | Detail of Activity: Backfilling
8268c736-91e2-5491-9c2b-47dfe90f7dd2 | note | Action: M
d0d7e4a0-10e2-5a9c-a35a-14211233ded6 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
9326aa32-9032-5daa-96ee-598fdaf73882 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
7679c6eb-20e9-5412-b26b-2ad4ab4ab898 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
720d4d81-548e-53bd-8e50-c6a5f39b71e8 | note | Record Documents: Contractor's site diary
d8a417f3-ae1a-5a8f-822c-ac34761a306d | note | Responsibility: Contractor
4cda4971-d535-5d51-a791-b2d8bbd1965f | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Outlet 3-2 Precast headwall/wingwall : Statehighway 30 (Ø750mm)
| checkpoint | 300.72 - Determine Subgrade Strength
a214aeb4-0dd4-5d98-9d42-d64aa3c2f788 | note | Detail of Activity: Determine bearing strength of subgrade
40679453-0217-5f2f-86bd-4139b851bd59 | note | Action: H
4c1c19b6-8c05-5b39-bff7-086f4534f6ab | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
9307d4bf-29e2-580c-a142-0927ca20f5f0 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
f0df99ef-285b-5a91-b81a-d04db7317e9a | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
b5339ac1-6cdb-5046-9a79-63d7fa7cf505 | note | Record Documents: Contractor's site diary
a0b6923b-0f11-5801-9e16-97ed3bf93f7d | note | Responsibility: Contractor
adf4af1a-4d9d-5a66-bedc-61db13c0c137 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.73 - Structures (manholes, head walls etc.)
5e726772-05b2-56fc-83ed-4e63bb781283 | note | Detail of Activity: Visual inspection of concrete components
e54f927a-8f94-5486-b702-76f9e212da98 | note | Action: W
ea3876e2-c5ac-539a-b000-4758fbd2b462 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
559d0472-e09b-5aae-9d2c-e960f3ae8151 | note | Inspection / Test Method: Visual Inspection
daa2bc24-912d-57e3-bcc1-e7bb4066c485 | note | Acceptance Criteria: No visible damage, especially around collars and joints
57f175f2-783d-5d26-b8da-ba9bb2605aaf | note | Record Documents: Contractor's site diary/Photos
51e3554c-fbbb-5c07-8774-9134ff068bf0 | note | Responsibility: Contractor
| checkpoint | 300.74 - Structures (manholes, head walls etc.)
71a5fe0f-d1b6-53b5-a0d4-da8b2e58ef35 | note | Detail of Activity: Bedding
3c38fdb6-f60e-52f2-83fe-9e859cb0e46a | note | Action: M
96cc9214-e4ca-531f-998a-afe75fa8806d | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
cc947161-a278-5f1d-a6bc-fb80f0dc93c7 | note | Inspection / Test Method: NZS 3725:2007
07bc460f-3018-5a9f-912b-50be6d0e91bb | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
20c596e3-9846-55e3-b756-382f4b2dff8d | note | Record Documents: Contractor's site diary
c3149165-7397-5704-888e-a4995638573f | note | Responsibility: Contractor
b15b1bcf-7add-5ff2-9446-d6f7c488e481 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.75 - Structures (manholes, head walls etc.)
b53c71b1-5a6b-5b44-aaa7-0b6f35a04073 | note | Detail of Activity: Backfilling
b6b9eefe-d3c4-5377-8535-e9ea6d41989c | note | Action: M
aa768205-2d3b-5699-99eb-322664f232b8 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
a941b0a9-2215-5ea0-98b2-062e21942bcb | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
8f20df1c-190d-5b0a-8ae8-c39f6932ab3d | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
fd4322ad-dc07-5d72-bddf-2a7e0853e292 | note | Record Documents: Contractor's site diary
f322c3a8-870f-5516-83e1-4c43541cb75e | note | Responsibility: Contractor
096a207c-4422-5735-aae9-e05f427dd44b | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Stormwater Line 4 : SD 4-1 to Outlet 4-2 - Culvert to Wetland Access Track (Ø750mm)
| checkpoint | 300.76 - Determine Subgrade Strength
fd8d4dba-1e32-5f53-9208-33842c683685 | note | Detail of Activity: Determine bearing strength of subgrade
e85deb80-bb78-57c8-a63e-d173f30a9d33 | note | Action: H
11a04578-7cfb-597f-b04d-668f7768049e | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
9b1926e8-6898-5031-a954-f682bc4b59ce | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
9920e738-d567-55eb-b71c-c7a640b2add4 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
f0f311cf-03fe-57bd-a01a-cbd75763bc47 | note | Record Documents: Contractor's site diary
6602bcc9-128a-54d6-a92b-d36eea280989 | note | Responsibility: Contractor
dda758d2-d212-53c9-9602-5aeb9dce06cb | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.77 - Pipe bedding
87b59f6c-5e96-5201-b986-55dd93fee072 | note | Detail of Activity: Bedding
2c9b966b-3e6f-51b0-bb30-86608013f3b5 | note | Action: M
40e30c48-da02-5e48-a7db-6f16e5fc0390 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
fd4840bc-802e-5357-a79c-387c462228d5 | note | Inspection / Test Method: NZS 3725:2007
84e76fce-f450-5b4a-b790-303b1a44e299 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
1a0cb2e6-78b5-5c28-aee9-a67719f6235e | note | Record Documents: Contractor's site diary
59297346-520f-5cfa-ae70-86423710490c | note | Responsibility: Contractor
cae505af-c822-5519-8f04-4b7874f73af8 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.78 - Jointing of pipes
9aac73cd-dc2c-5ac6-a19b-9754a8d6a8f1 | note | Detail of Activity: Jointing
5daf5600-3aaa-52e9-8fa5-8ffb73c3ce24 | note | Action: M
f2f98ca5-fe59-5ea9-8d41-9aaaceca5b28 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): Every Pipe Joint
09ec3ce8-b5f6-53cc-abfe-5142ca12ca87 | note | Inspection / Test Method: Visual Inspection
14412853-1469-5501-b0af-f59741a9bacc | note | Acceptance Criteria: In Accordance with section 5.2 of the Project Technical Spec.
25b864d4-6e82-5bea-9e87-e9372ae55fd5 | note | Record Documents: Contractor's site diary
f8126818-d59f-5d54-a123-538e4c72a312 | note | Responsibility: Contractor
0b493c92-fb9f-53d1-87c4-081c0d730a36 | note | Comments: Rubber rings to be mounted evenly and lined up truly concentric with pipe. Gap between spigot and shoulder to of pipes to be even and between 5mm and 10mm.
| checkpoint | 300.79 - Pipe haunching
a5fc1110-24b7-580a-9158-4491f5b1ea9e | note | Detail of Activity: Haunching
fb0bad16-7e8e-5ba5-ab16-1235190172e7 | note | Action: M
dbebc92e-6f3c-5ccf-bc47-03d4ec885000 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
f84cb065-96a3-5e5b-a4a7-5e0b526edc18 | note | Inspection / Test Method: NZS 3725:2007
e7d383f6-c5b8-5fe2-b17a-5ea902e18c7c | note | Acceptance Criteria: In Accordance with HS2, Minimum haunching depth of 0.3D, CIV Value on compacted haunching >25 (CBR = 30).
de0a5307-59d6-5183-a7b1-93d90c0a16f7 | note | Record Documents: Contractor's site diary
129f0184-2437-5fa0-983f-a78f2581af51 | note | Responsibility: Contractor
9e640109-6ab2-5027-a4a8-afe3601b9a15 | note | Comments: PAP 7 material to be used.
| checkpoint | 300.80 - Trench backfill
5198db1d-d9b2-5725-ab62-6a9b8774bd94 | note | Detail of Activity: Backfilling
d9547e86-48e9-5d15-a920-728313928c30 | note | Action: M
ba3176c1-0dcb-506d-bc0c-04f5a9fc77f1 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
e33fafb7-b26f-5d18-b4c9-461262e8c6c0 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
fb85812b-913f-5e78-b4fe-2370d4d79058 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
bcba9816-eab7-515e-abc4-624f5036113e | note | Record Documents: Contractor's site diary
51a0887d-6578-580a-b676-c248c6554b52 | note | Responsibility: Contractor
ed396a12-fd5a-5880-8166-a4ecf14aecb3 | note | Comments: Clean Pumice Fill to be used
| checkpoint | 300.81 - Visual Structural Inspection
d9f9bd16-4f5a-5511-8c2f-7ffa91785390 | note | Detail of Activity: Visual inspection of concrete components
ba2a3b91-f6d3-5eb4-8c42-06ce2bd37e63 | note | Action: W
d9faddea-00ce-5945-9909-4287c1f3a76c | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
d0cdc50f-dcb4-53c3-9e41-b570ad3bd370 | note | Inspection / Test Method: Visual Inspection
73ba994c-d2bf-5a62-9b3f-6b17d5a353f1 | note | Acceptance Criteria: No visible damage, especially around collars and spiggots
ff0481b6-1a52-5506-800e-8b496edef0a4 | note | Record Documents: Contractor's site diary/Photos
82e930ae-06b2-5cea-a696-67cf41cfa1a8 | note | Responsibility: Contractor
| checkpoint | 300.82 - CCTV Inspection
5d452432-fc36-5c16-afa1-26f1ca414171 | note | Detail of Activity: Visual record of Existing works
fd616468-c9c2-5e85-8888-ac432767a722 | note | Action: W
5c5480ac-311a-5363-b94d-eda0e220fa8a | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage pipelines
2a52603f-1b49-5594-9288-1743433c65d4 | note | Inspection / Test Method: CCTV Inspection
34f0f60a-3fa5-5bb8-adbc-0475bdd5134b | note | Acceptance Criteria: No significant cracks, level deformation, faulty joints
376097ae-e23c-5cb4-9171-086e08d1cea7 | note | Record Documents: CCTV Footage
9817fe81-c13c-5b63-9f82-ad37f7181f11 | note | Responsibility: Contractor
c4d426a7-0ad8-5094-9a75-2960084bbb48 | note | Comments: CCTV footage to be reviewed by Engineers Representative and signed off via NTC / Site Instruction prior to Practicle Completion
| section | Construction and Finishing - SD 4-1 Manhole/Standpipe with Scruffy Dome ( Ø1400mm)
| checkpoint | 300.83 - Determine Subgrade Strength
d0be59d1-d50c-52bd-8770-9ee680cdb11f | note | Detail of Activity: Determine bearing strength of subgrade
4f3b2d38-460a-5989-aa2b-2d5cc9b5e98c | note | Action: H
0c9ca33b-b57e-5f83-ac40-10698ff08485 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
2dac36b2-67ca-5c93-9026-66551037c747 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
3a7b72cb-9605-566f-ad8e-21cfdcc9d9f7 | note | Acceptance Criteria: No target - Engineer to advise undercut requirements prior to installation
14f42eae-0fee-5c88-84f8-fc4e493d053a | note | Record Documents: Contractor's site diary
621d191f-1856-58a2-a867-c3c6282df189 | note | Responsibility: Contractor
53e13aa1-d5c7-569b-b92b-70ea7275a775 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.84 - Structures (manholes, head walls etc.)
2b6ff45f-b2de-5aec-b6a9-05765acfd495 | note | Detail of Activity: Visual inspection of concrete components
96cd2f12-8942-5b39-8a79-5e9ef002b448 | note | Action: W
67bbc882-b3e3-5dd3-855e-6189b8296ba2 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
990c5f08-0e80-5065-933e-cb7b6f4fa98e | note | Inspection / Test Method: Visual Inspection
f3ab0c69-7e05-5b62-9030-2adc98dddff5 | note | Acceptance Criteria: No visible damage, especially around collars and joints
c4d3bc20-38f8-5a06-9b2a-323b8583f995 | note | Record Documents: Contractor's site diary/Photos
d9ad2742-5119-5b5a-9034-afe6eba96e5a | note | Responsibility: Contractor
| checkpoint | 300.85 - Structures (manholes, head walls etc.)
c25c84d3-bcbd-5d98-be6b-ac20416dee49 | note | Detail of Activity: Bedding
305e9e2e-0fb0-5eea-a20e-8495abfc0700 | note | Action: M
da9bae69-f014-5245-b191-ae2db49848bd | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
5d42c303-01b1-56c0-9674-3f2d5a2faf70 | note | Inspection / Test Method: NZS 3725:2007
f6d08267-891e-5337-9e18-20417a06c6ca | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >15 (CBR = 20).
bcfd7257-e768-50f3-9abd-7eba901ca226 | note | Record Documents: Contractor's site diary
6fc3379a-e6f6-57aa-8b3f-6215970cf0e9 | note | Responsibility: Contractor
8632e267-d51a-560b-ba66-7702b05fa340 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.86 - Structures (manholes, head walls etc.)
d9a01a59-557d-52c4-8f80-8c5599f643cb | note | Detail of Activity: Backfilling
97bfbc42-95a1-54af-8de8-7848de5639b6 | note | Action: M
5ebd1a9f-0869-5e4f-ae84-ba0646cbc877 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
e76d6316-ede0-5f48-bddb-f12e646679ec | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
357a712b-3e8e-5074-814b-cc10a655715b | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
54bae1fe-e96e-53ad-934f-598b9a5f2dd8 | note | Record Documents: Contractor's site diary
475af32b-24c8-5ac3-9952-5c4eb5118582 | note | Responsibility: Contractor
3678ec58-f475-5cf7-88c0-5b9b936c06a7 | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Outlet 4-2 Precast headwall/wingwall : Access Track (Ø750mm)
| checkpoint | 300.87 - Determine Subgrade Strength
d1d60d37-a207-56a2-aaa5-31e90d67a1e5 | note | Detail of Activity: Determine bearing strength of subgrade
7880b4d1-5d2c-577c-b71b-5699322d1351 | note | Action: H
ba9a74dc-7264-500d-a53f-e592e7083b9b | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
33d897d8-b6a4-5f2f-b175-86cee2772aad | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
25edaaa3-5422-5651-92fa-215c56e7d412 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
41944388-e06b-5fac-b6d2-99d1f73f677e | note | Record Documents: Contractor's site diary
b2a2050f-1eba-52f8-bb2f-cf7c00ac9491 | note | Responsibility: Contractor
1a4e1068-ba06-58fd-8334-853a011cf9eb | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.88 - Structures (manholes, head walls etc.)
d4d43209-2b83-5024-9b47-4bb5c9fbf1ed | note | Detail of Activity: Visual inspection of concrete components
985b63c3-2fa0-5464-bd73-2359b4814f48 | note | Action: W
4c273dfc-431c-58bd-8794-27cbda925ccb | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
afe25c97-e990-5b02-ba81-089c3fd7a8fc | note | Inspection / Test Method: Visual Inspection
15d6d147-0af2-59ef-a9a4-1020b561f3d3 | note | Acceptance Criteria: No visible damage, especially around collars and joints
8700712c-24ac-5690-ac00-5c36741a2490 | note | Record Documents: Contractor's site diary/Photos
00bbd3d3-2067-564a-93cf-8ea5ed6b76b5 | note | Responsibility: Contractor
| checkpoint | 300.89 - Structures (manholes, head walls etc.)
1697bb38-41dc-5afe-81c1-fa445bdc684b | note | Detail of Activity: Bedding
c9122924-748f-597b-ad0b-399207631120 | note | Action: M
15d93576-c503-50c5-adfd-83c816cf134b | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
7040b1ec-f6ba-5851-8ce3-1c1f19817ac2 | note | Inspection / Test Method: NZS 3725:2007
693d3121-8335-50a4-b49b-900df300cf27 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
fb302ef6-52f4-5738-9a63-e460f379d5db | note | Record Documents: Contractor's site diary
35bd8321-86fe-5383-b517-2afd8cb7c6ac | note | Responsibility: Contractor
c8a3be88-2669-57b1-834c-653fabd1c323 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.90 - Structures (manholes, head walls etc.)
da496a5e-5ae9-5990-bcc3-5664ee24466e | note | Detail of Activity: Backfilling
1ea9bf27-620f-5a18-bee8-97713628258f | note | Action: M
25881757-c894-5651-8610-da8da782c3e8 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
ac4f2f5c-51c7-52f8-b7b5-5d2249a24122 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
76176c7c-cb41-580e-bc41-77151d64f7d4 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
ecb08540-a758-5ec8-a6ae-a124fe7dd897 | note | Record Documents: Contractor's site diary
6857445a-69ca-5af8-aae5-464936f655a4 | note | Responsibility: Contractor
ca64987c-68f7-547c-b086-964fe1f91fe5 | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Stormwater Line 5 : SD 5-1 to Outlet 5-2 Culvet to SW Treatment Wetland (Ø600mm)
| checkpoint | 300.91 - Determine Subgrade Strength
7949bbb0-77aa-504b-af57-df60752d3efd | note | Detail of Activity: Determine bearing strength of subgrade
84cc3564-a7cf-5b72-92fd-6d7185f078f9 | note | Action: H
a4c75da1-9514-5f77-92f8-2b07ce6bcd16 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
0d6414b8-b089-54db-b8ca-a0758c94cafd | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
4f2072b8-14b6-53d9-bf77-57296ef732bb | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
8f1743bf-6b49-5d5e-b05a-b95dd199ccea | note | Record Documents: Contractor's site diary
5890c0d2-efe7-507b-b662-a83d316dc968 | note | Responsibility: Contractor
7e862fea-7657-5f67-a706-6f9972d28535 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.92 - Pipe bedding
b047582f-959f-5bc0-ab27-140852ca75ef | note | Detail of Activity: Bedding
8a5cd3d0-7429-558e-967f-e566f7e3ccc2 | note | Action: M
2479752a-71ca-5d6d-b470-0904e4062d1f | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
37ea76d0-d6cf-59a3-ad3c-153179c553cf | note | Inspection / Test Method: NZS 3725:2007
f35d7d10-1377-50e6-9825-27de32f2da8f | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
6fdf3d57-0f70-5230-a3d0-5d20bac81d00 | note | Record Documents: Contractor's site diary
a81be3f5-7f44-5d46-82a2-717e76933865 | note | Responsibility: Contractor
1ec26400-fbbb-5692-ae5e-f223d9740e6a | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.94 - Pipe haunching
cc0a06ad-26d4-5803-a896-c4a09e80a8e1 | note | Detail of Activity: Haunching
1613dc9e-cfaf-5a57-8888-3bc1e26555ca | note | Action: M
dbbcb53b-f046-56bb-b81a-175002ce20d9 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
6654404a-90cc-5553-8317-71f2df79a5e7 | note | Inspection / Test Method: NZS 3725:2007
4fe423c4-e8f7-5050-bfa6-9e26e33b5d2d | note | Acceptance Criteria: In Accordance with HS2, Minimum haunching depth of 0.3D, CIV Value on compacted haunching >25 (CBR = 30).
207925bc-f734-5906-8797-fe980e1419ec | note | Record Documents: Contractor's site diary
7368cee6-cda5-5c6b-869d-d7b7dea62424 | note | Responsibility: Contractor
2b7dbd88-0aa3-5d8a-bcd4-c281b8541690 | note | Comments: PAP 7 material to be used.
| checkpoint | 300.95 - Trench backfill
79447b3e-9450-5a6b-9341-009cd4944be2 | note | Detail of Activity: Backfilling
973affbd-dbf8-5eda-8c76-85c0c16982e3 | note | Action: M
9f78ce67-1c6d-5cd2-a489-79d8f1b97a70 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
4d9cbfa1-a17c-5811-aa74-67569e3a512b | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
c486d077-4226-52ad-9805-ef43cc083e84 | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
84e60b68-a037-5116-a18d-21440ca2f685 | note | Record Documents: Contractor's site diary
d7b8e1c0-9016-52af-82bd-ebd9205a95be | note | Responsibility: Contractor
5bb36a27-7512-59e5-b15a-85324f762466 | note | Comments: Clean Pumice Fill to be used
| checkpoint | 300.96 - Visual Structural Inspection
85f04d32-7819-5ca0-b6cf-ddc703c42081 | note | Detail of Activity: Visual inspection of concrete components
3fd0ee3b-8f18-5195-818a-81a316c3bfdd | note | Action: W
d4b4a62d-1450-555e-a0b7-c282e5863f9b | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
e7109cd3-dd82-55b4-8f45-e9d951c614c6 | note | Inspection / Test Method: Visual Inspection
01a1f747-ed01-598e-a6eb-8b5b4f501d75 | note | Acceptance Criteria: No visible damage, especially around collars and spiggots
b19ddbfb-9cc3-5fb4-9eb6-280c54c7142a | note | Record Documents: Contractor's site diary/Photos
1c162a57-7772-5000-8637-90341b9ab3db | note | Responsibility: Contractor
| checkpoint | 300.97 - CCTV Inspection
ba26f38d-6b78-59fa-924b-4962e19b3a09 | note | Detail of Activity: Visual record of Existing works
57dc2340-e1ad-5b4a-8de4-b0c0ceaec034 | note | Action: W
78e5d61c-e041-52f0-a7fc-56ef8d5352f1 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage pipelines
6f959158-0c2d-5f2a-8ec4-b59202736e4c | note | Inspection / Test Method: CCTV Inspection
4ed5c643-58b6-5138-8e01-7d9181c66853 | note | Acceptance Criteria: No significant cracks, level deformation, faulty joints
eae5deb4-9a1a-51df-a4ec-58ffe0630827 | note | Record Documents: CCTV Footage
612c7840-46f7-58b9-add7-f1080b961b69 | note | Responsibility: Contractor
083af908-7c08-5b46-aebb-e5b4fb4961d5 | note | Comments: CCTV footage to be reviewed by Engineers Representative and signed off via NTC / Site Instruction prior to Practicle Completion
| section | Construction and Finishing - SD 5-1 Manhole/Standpipe with Scruffy Dome ( Ø1400mm)
| checkpoint | 300.98 - Determine Subgrade Strength
1d0dbe60-cda7-5aba-a1a9-68599a16bf01 | note | Detail of Activity: Determine bearing strength of subgrade
18a8f896-5743-55a6-9b85-b1b70387263a | note | Action: H
595f512b-2945-5a7f-9b30-b048ffacfa48 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
86e9dbf6-7e7a-5010-8e9b-8f4df1da1db0 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
1449f41a-1cf5-5498-9386-3c7df1e5600a | note | Acceptance Criteria: No target - Engineer to advise undercut requirements prior to installation
82a3ae94-7c04-5980-b4e9-d8b33c88e434 | note | Record Documents: Contractor's site diary
74ed40c0-f85f-5c67-81d9-dfb790b0d617 | note | Responsibility: Contractor
fa1e8094-78a8-5ab5-8415-c58cf7398bab | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.99 - Structures (manholes, head walls etc.)
a6ee0cad-2fa6-53d3-b232-4b2981b7443c | note | Detail of Activity: Visual inspection of concrete components
80dc56f3-ffc8-56da-92eb-d269e723f304 | note | Action: W
28efd7f8-9d15-5cbf-8014-1da3fa593872 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
b11c2156-1ffb-5d23-9eea-47c17e1f2bd8 | note | Inspection / Test Method: Visual Inspection
bf1c6a90-04ba-5c43-a742-d023c93a1dcf | note | Acceptance Criteria: No visible damage, especially around collars and joints
1b4415f3-2fe0-5611-b470-047246be7897 | note | Record Documents: Contractor's site diary/Photos
122cdda4-5cd3-5b20-982f-24ca720753a3 | note | Responsibility: Contractor
| checkpoint | 300.100 - Structures (manholes, head walls etc.)
9fd503a9-8878-5bad-b9e6-c0743bdc936b | note | Detail of Activity: Bedding
fd046982-4c9a-58ee-baa3-9fbfff0614a4 | note | Action: M
3280647e-dc89-562d-b560-3c8dfb333a03 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
f0ed9b06-513d-5334-b242-2968dab69687 | note | Inspection / Test Method: NZS 3725:2007
a0e0b54a-e352-5f17-98fe-58ca49ca2509 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >15 (CBR = 20).
94237cfc-a31f-57d6-b0c6-421d42c148ff | note | Record Documents: Contractor's site diary
35b2c7fb-1e1b-51f6-a5a1-393d44367da2 | note | Responsibility: Contractor
10dae104-b643-533b-a631-9f0bd113339a | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.101 - Structures (manholes, head walls etc.)
b0914cc6-2e92-5b21-9142-7c8dae1d1912 | note | Detail of Activity: Backfilling
80586d6a-55fb-5c71-9d3f-9de105f747c7 | note | Action: M
f6c609d1-1f8c-528f-8d9c-2ec361a1c712 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
d25f726b-2d1e-5e18-8f2c-f163524921bd | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
12d447bf-019a-5cd6-ae25-c9456511bf5d | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
2b726b0e-ce4b-54b7-8a49-7901cd96b6ae | note | Record Documents: Contractor's site diary
fc467b56-117a-5275-a9d0-b77b0b939e7d | note | Responsibility: Contractor
89282a9b-1fcf-5639-888b-b52fdd68044a | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Outlet 5-2 Precast headwall/wingwall : Swale line 1 (Ø600mm)
| checkpoint | 300.102 - Determine Subgrade Strength
abca7ced-9bc0-56ee-ac3b-c5f1e43fcb53 | note | Detail of Activity: Determine bearing strength of subgrade
ed105f51-41a7-513d-a2f3-846abaa0cfdb | note | Action: H
54a73bd4-e077-5115-b209-2bd082aa803e | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
e3117cd8-f47e-52b4-9c01-de61bd2f64a8 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
bc91ab93-a992-517b-be7d-15b743666ada | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
5bab5140-36a6-5d26-8f11-9a36ed6e932d | note | Record Documents: Contractor's site diary
df4cfbe8-9828-5068-8676-fd7dab3b0b45 | note | Responsibility: Contractor
3003be56-a5a4-597e-9c5c-866c9c493efc | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.103 - Structures (manholes, head walls etc.)
57abef47-30a3-5134-adf5-41faa7a93470 | note | Detail of Activity: Visual inspection of concrete components
1ac260d0-7c95-5f65-b7ab-e176d866c08c | note | Action: W
14f24e12-e4ea-5fc1-96fa-a09870a1170d | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
b19614fb-9bc0-54fe-83d0-56a6b607b4ab | note | Inspection / Test Method: Visual Inspection
d8df286f-5e8b-513e-8a70-58a60791069f | note | Acceptance Criteria: No visible damage, especially around collars and joints
09dd7723-fbc7-554c-a46e-3ea2557f0ad7 | note | Record Documents: Contractor's site diary/Photos
50d4fda1-3497-5af6-a88c-8442dd5bda85 | note | Responsibility: Contractor
| checkpoint | 300.104 - Structures (manholes, head walls etc.)
b9e0f72d-f5d8-54d5-8152-71b38fd56b29 | note | Detail of Activity: Bedding
dbd1cbf1-c1a9-5ec8-bd8c-356ed6a5e63b | note | Action: M
fa3a1bd0-20be-5c46-94fe-8727c59e54d1 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
3e029a7a-7664-5365-8e83-b9e1dfd381e7 | note | Inspection / Test Method: NZS 3725:2007
0136a966-4ac5-582e-925c-97bc6ddedf4e | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
27eee0ea-e74a-50f0-bbca-aaf0a313669d | note | Record Documents: Contractor's site diary
6dd406e9-470f-50a5-8b71-e9f716a1c7cc | note | Responsibility: Contractor
778871b8-5e85-55c7-9960-c09409f37608 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.105 - Structures (manholes, head walls etc.)
287d957a-feb4-52ef-bbb6-ebed71344377 | note | Detail of Activity: Backfilling
8ed0384e-0220-5baf-880d-f923b711db6c | note | Action: M
e5893628-e67c-5a9d-8d7a-5598c8ea3ae9 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
61e30b47-46ab-5466-8682-6f7d41d8318f | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
2bd4dc1d-02f1-5d87-9d7b-7d6d87fa2daa | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
573c8344-abee-5df9-bf79-017077f19fac | note | Record Documents: Contractor's site diary
beca671f-97cb-5439-a0c9-ffd2e0a93854 | note | Responsibility: Contractor
876e198b-172d-5bbc-92af-8565235cb1a3 | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Peers Adams /Kiwirail Access Culvert : (Ø450mm)
| checkpoint | 300.106 - Determine Subgrade Strength
53166b21-a56a-59bc-ab12-7cb85a5ec11b | note | Detail of Activity: Determine bearing strength of subgrade
2deb820c-509b-5210-8804-af9ee3702a39 | note | Action: H
f12e53a5-4a0e-53c2-aebe-67d17752b1a8 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
d11cadc9-a4d1-5e5e-ab9f-e7914f6ec94a | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
e6cb6b40-6a59-545e-8434-d670a44991f7 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
4a74fa7c-63bf-5ae8-96a8-f5b8ec9c42d2 | note | Record Documents: Contractor's site diary
99a66da6-e081-5b66-930e-0761024a8298 | note | Responsibility: Contractor
e8b16ef1-aa5b-50fe-b8e8-614f191d468d | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.107 - Pipe bedding
e7606fcc-d33f-560e-921a-da5ca1c8b3fb | note | Detail of Activity: Bedding
44ec0c23-da01-5379-9126-3a943d239409 | note | Action: M
474c8547-a2e3-52c3-ad5d-31a2d1611247 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
084a7d77-40e6-5225-a992-d197086c738c | note | Inspection / Test Method: NZS 3725:2007
85a14501-3203-5482-8a79-cfbb320df548 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
e3133146-8bbc-5892-b128-8e787aba98c4 | note | Record Documents: Contractor's site diary
eec45036-7e82-55a2-a0e5-7a73636d9577 | note | Responsibility: Contractor
36132039-40a1-5698-a6c0-259c46fe1327 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.108 - Jointing of pipes
3e50e489-57eb-5493-8065-14958c9fa8ed | note | Detail of Activity: Jointing
26b3fa57-88bc-50e7-82b6-20cac00396fc | note | Action: M
eb550275-84b4-5c8e-8566-64dd3255ffe7 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): Every Pipe Joint
806454dc-a07b-5690-87bb-60a2cab3d88f | note | Inspection / Test Method: Visual Inspection
0a273b0b-a0b2-570d-b834-5784fe8b097d | note | Acceptance Criteria: In Accordance with section 5.2 of the Project Technical Spec.
d6b1108e-e2d2-55a7-b78c-bdc2b94a73e6 | note | Record Documents: Contractor's site diary
8f441060-07a4-5edc-b323-ed852108c856 | note | Responsibility: Contractor
80df739a-78f5-57fe-87db-bf6dbe825ef8 | note | Comments: Rubber rings to be mounted evenly and lined up truly concentric with pipe. Gap between spigot and shoulder to of pipes to be even and between 5mm and 10mm.
| checkpoint | 300.109 - Pipe haunching
da36e203-2311-5f5f-89f4-02a3f7b4b04c | note | Detail of Activity: Haunching
8c69a82c-c9f8-58a5-bb74-696bc9febb8c | note | Action: M
e9b9d5e5-9767-5639-bccf-0b08031075b6 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench
3759b4cf-0cfb-5ba4-9cc9-bb7d381b5a4a | note | Inspection / Test Method: NZS 3725:2007
ba16d2d5-ebef-5018-bd81-7ed4bb5e624d | note | Acceptance Criteria: In Accordance with HS2, Minimum haunching depth of 0.3D, CIV Value on compacted haunching >25 (CBR = 30).
c410ac7f-4d51-5a16-bb08-1d4ae71f7085 | note | Record Documents: Contractor's site diary
0645d284-c88f-55b5-986a-099c107ebd4c | note | Responsibility: Contractor
f4933ada-f4fe-5440-94f0-e1524b0a1510 | note | Comments: PAP 7 material to be used.
| checkpoint | 300.110 - Trench backfill
a3bdfec9-a0da-5bf0-bc5c-321cfa73d839 | note | Detail of Activity: Backfilling
00533489-b301-572c-bc75-fad5f8f666bb | note | Action: M
839d5e5f-8a9d-5ced-9a56-9a2b44fef400 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
8419c135-8b4d-5fca-848a-a575a1f193cb | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
e8c7e71f-90e2-5142-94ce-dbd1801ff9ac | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
1add110c-8fd9-5409-ab0f-b6e85fb1aeb4 | note | Record Documents: Contractor's site diary
3f764777-bee7-59e3-9708-a46c577a250b | note | Responsibility: Contractor
d1799d2c-3579-540d-a3fa-0a89c9115dc7 | note | Comments: Clean Pumice Fill to be used
| checkpoint | 300.111 - Visual Structural Inspection
537574fe-590a-5d8d-bb3b-8ee3baa1337a | note | Detail of Activity: Visual inspection of concrete components
52b07492-b7da-5ce2-92dd-944556cb03b4 | note | Action: W
6198d896-2d46-5f84-b51d-10f4203e556e | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
3c0202d8-5b98-5732-b131-3b63caba022a | note | Inspection / Test Method: Visual Inspection
0a7de16a-4a1a-5fc5-92e2-d282e98ca74f | note | Acceptance Criteria: No visible damage, especially around collars and spiggots
52d128b8-bb44-515b-a82d-b53c277d690e | note | Record Documents: Contractor's site diary/Photos
e94ea371-4a0d-5fb9-831e-c61b84d923b3 | note | Responsibility: Contractor
| checkpoint | 300.112 - CCTV Inspection
e68e8695-e45b-56f3-9abc-1c3e3d69fd37 | note | Detail of Activity: Visual record of Existing works
f2887156-8368-5d05-bf91-1a54691e5a50 | note | Action: W
78350bed-6d80-586e-8ccc-fc1bd451db4f | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): All drainage pipelines
04e52377-0add-5f83-b507-aa6ac6d67c5b | note | Inspection / Test Method: CCTV Inspection
688e0399-85c6-522d-913e-9c71796f0c23 | note | Acceptance Criteria: No significant cracks, level deformation, faulty joints
fac4301e-9dfe-510c-9492-8c6cb40a2c18 | note | Record Documents: CCTV Footage
30b3301f-5313-50f7-b834-0e22849f835d | note | Responsibility: Contractor
b4848f2e-a934-5229-94cd-8b1fedc8fec7 | note | Comments: CCTV footage to be reviewed by Engineers Representative and signed off via NTC / Site Instruction prior to Practicle Completion
| section | Construction and Finishing - Intet : Precast headwall/wingwall unit for Ø450mm.
| checkpoint | 300.113 - Determine Subgrade Strength
4eeda5c3-f5a3-5898-b20d-f369f2cf73fa | note | Detail of Activity: Determine bearing strength of subgrade
a5b221f3-2ce6-51b9-bb15-a5f03aead663 | note | Action: H
7f40bea8-edba-5581-9dcd-ced33e1ad788 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
7523439e-eb76-5ad5-890a-e81a46abeed4 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
009e151d-2d83-5daf-8d43-560213ac64b2 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
1caaffa3-f2df-5082-8d8e-236ff4eeca7e | note | Record Documents: Contractor's site diary
fd12dfe4-ece0-56b8-8339-2fe1d532658b | note | Responsibility: Contractor
94adf3c3-6fda-5b9f-922c-9faabd962778 | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.114 - Structures (manholes, head walls etc.)
eb57a559-0b22-5a98-8ddf-29bba562f1b3 | note | Detail of Activity: Visual inspection of concrete components
473ed92f-5325-58d6-a713-046be3909f31 | note | Action: W
47e0a33b-dc6c-5da5-867f-c7477636ee6b | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
8eb33e42-781d-531b-bf34-009ada258d93 | note | Inspection / Test Method: Visual Inspection
67336c53-004f-571e-a435-d9e639f88cb6 | note | Acceptance Criteria: No visible damage, especially around collars and joints
2e878146-92d4-537f-8520-d56857d209e9 | note | Record Documents: Contractor's site diary/Photos
fb8237cb-f54a-586d-ab50-fc8aec0cca11 | note | Responsibility: Contractor
| checkpoint | 300.115 - Structures (manholes, head walls etc.)
bd868619-0412-56d4-9c98-8c41e9dc275a | note | Detail of Activity: Bedding
d974db16-30e8-5861-ba15-ce496bbf0785 | note | Action: M
152c48f7-b7ad-5a66-9af4-7e7ac27fd5b0 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
d225e066-eb89-5814-8e84-67138a6382b8 | note | Inspection / Test Method: NZS 3725:2007
6b5ec5b2-e0b8-528d-818a-1ea5b453fff6 | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
6664d137-e057-5c2b-a81a-6af4f2768a5c | note | Record Documents: Contractor's site diary
f9ac3533-677f-54f3-9894-e0e152702294 | note | Responsibility: Contractor
226fc02d-efdd-516f-b0d9-25bc5ece2db2 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.116 - Structures (manholes, head walls etc.)
7db1f143-483c-513f-a955-77a7c3081527 | note | Detail of Activity: Backfilling
8ab21e75-48cf-54d5-ab81-6ecd660ee106 | note | Action: M
79127a5a-8a27-5869-b636-7346bcfbe19e | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
dfd54a69-ba75-5df8-a790-2167d4a02bc7 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
5f0b2d5c-758d-5d6e-a54e-20038507078d | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
f64d9f7b-d8a5-50ed-942a-16ea46caf9d1 | note | Record Documents: Contractor's site diary
9d4f0b1e-2bc2-5b62-a238-c89ff2f7edf0 | note | Responsibility: Contractor
eea4dba4-9a3f-5928-95f6-b84ae5d59f1f | note | Comments: Clean Pumice Fill to be used
| section | Construction and Finishing - Outlet : Precast headwall/wingwall unit for Ø450mm.
| checkpoint | 300.117 - Determine Subgrade Strength
98ce840a-ddea-55a7-b940-57179bffd111 | note | Detail of Activity: Determine bearing strength of subgrade
23decbed-cb94-5f22-8def-478ce1b070a4 | note | Action: H
1d307f04-b40d-57c8-8ff3-b7f25a8989ad | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m length of trench base; or 1 per drainage structure
eb7fad40-d651-5a04-9dd6-ff0406f3d959 | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
6a53ca11-eb13-50ca-9436-ef0e9ec11f44 | note | Acceptance Criteria: No Specific target - Suggest Engineer to advise undercut requirements prior to installation for any scala readings less than 3 blows per 100mm.
1dcd70c2-bdc3-51b7-ba84-c8d9cad72478 | note | Record Documents: Contractor's site diary
ff572c85-2c6b-50d3-9331-ece648b464d0 | note | Responsibility: Contractor
cff34cd8-454f-5e55-89cc-25833eeacbdf | note | Comments: Seek design subgrade strength prior to commencement so expected subgrade strength is known.
| checkpoint | 300.118 - Structures (manholes, head walls etc.)
8cc3333d-14b5-529d-8e29-9dfd809901d7 | note | Detail of Activity: Visual inspection of concrete components
03a9be81-58ba-5190-a62f-80aa78ca4c9c | note | Action: W
4ec2f929-7cfb-50b6-a545-8d6ce0169462 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per structure
646f8973-daf3-5514-b1d2-7c5b1ca7a3fb | note | Inspection / Test Method: Visual Inspection
f905ab25-54a0-547f-9332-75604d881ddc | note | Acceptance Criteria: No visible damage, especially around collars and joints
7bc68ec8-be95-59a8-bdc2-3bc4b7e446e3 | note | Record Documents: Contractor's site diary/Photos
bf08e4b8-c8d8-5f24-8fdc-9b6256dad0d1 | note | Responsibility: Contractor
| checkpoint | 300.119 - Structures (manholes, head walls etc.)
51b04a0f-4f95-5eb9-b8f5-c047a6207376 | note | Detail of Activity: Bedding
4b54ca74-c045-51cc-9c97-8853db0925cd | note | Action: M
c7c3de51-0532-5840-8b26-b73ef5e96122 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
91dfdddf-276f-54a4-b321-a89d8ad5fa4b | note | Inspection / Test Method: NZS 3725:2007
daee94c7-f8ed-574a-a7ff-e150d179a75d | note | Acceptance Criteria: In Accordance with HS2, Minimum bedding depth of 150mm, CIV Value on top of compacted bedding >12 (CBR = 15).
9ffc36d7-e226-5831-86b5-fa162781cdd9 | note | Record Documents: Contractor's site diary
8f71cc33-9754-5e72-9756-db8fe1b5dd2b | note | Responsibility: Contractor
ab689edc-5b5b-507d-a2f8-2f5467cb7b80 | note | Comments: GAP 65 to be used with a leveling coarse of PAP 7.
| checkpoint | 300.120 - Structures (manholes, head walls etc.)
0926c65a-59a7-5fb3-8cf0-9e09c82ead68 | note | Detail of Activity: Backfilling
278d7694-23aa-5b5c-b546-4892791a9387 | note | Action: M
ad721d11-6a39-545f-9448-aa2e6352da27 | note | Minimum Test Frequency (Lot = 1 day’s production or 2,500m2): 1 per 5m trench per 1m lift
2f90763d-abb4-5ef1-aa5c-590c8c6f41be | note | Inspection / Test Method: Scala Penetrometer (NZS 4402.6.5.2).
3d28bae0-3a8a-5aaa-9846-061cb341a39f | note | Acceptance Criteria: In Accordance with section 6.2 of the Project Technical Spec. Scala no less than 18 blows/300mm (CBR = 15).
8368a0ca-88d2-540b-adf3-23d41349e8d5 | note | Record Documents: Contractor's site diary
490e7875-37e7-5a0b-b65b-c7ccaf54f055 | note | Responsibility: Contractor
bb9c8686-0d64-554e-9843-f58411bf21d0 | note | Comments: Clean Pumice Fill to be used
| checkpoint | Final Sign Off
8c9f8115-0604-5bab-8eaa-85d6213d7a89 | note | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with NZTA Specifications and verifies lot compliance.
004fd0a8-304f-51f7-9f31-22afe9763c63 | textbox | Contractor's Rep Name:
cc6fe7ec-474c-5953-acc1-77374b048d7e | textbox | BBO Engineers Rep Name:
| signoff | Add Sign Off
| checklist | ITP 011 - Electrical Conduit Installation |  |  |  | 0aca0d08-58a1-4605-9eb4-66918ac756b9
| checkpoint | Optional Document Upload Below
| checklist | ITP 012 - Watermain Construction |  |  |  | e3f09dab-6754-4c08-90dd-c616490c4d1a
| checkpoint | Optional Document Upload Below
| checklist | ITP No.2 Capping Beam |  | ITP No.2 Capping Beam |  | bba9a61c-066d-4592-bef5-69b4405e3b29
| section | Commencement of Works - Planning / Product Approvals
| checkpoint | Project Quality Plan conforming to requirements in specifications
| section | Preparation – Clean / Trim Piers
| checkpoint | Construction joint at top of pile shall cleaned and trimmed to the correct levels
| section | Formwork
| checkpoint | Capping Beam dimensions are per the drawings
| checkpoint | Complete formwork before concrete placing
| checkpoint | Inspect Formwork prior to placing reinforcement
| section | Steel Fixing / Reinforcement
| checkpoint | Specifications, shape, size and grade as per drawings
| checkpoint | Surface condition – free of loose mill scale, rust, oil, grease, mud or other material which would reduce the bond between the reinforcement and concrete.
| checkpoint | Starter bars cast into pile caps shall be accurately set out and securely held in correct position during concrete placement
| checkpoint | Inspect reinforcement prior to pouring concrete
| signoff | Signoff by Main Contractor
| section | Concrete Testing
| checkpoint | Slump Test Approved:
| checkpoint | Strength grade/Characteristic compressive strength to be submitted when available:
| section | Pour Concrete
| checkpoint | Before placing concrete, remove free water, dust, debris and stains from the forms and the formed space
| section | Formwork Stripping
| checkpoint | Remove formwork other than reinforcement
| checkpoint | Do not disturb forms until concrete is cured and hard enough to withstand it.
| section | Completed Capping Beam
| checkpoint | Inspect the capping beam and check the levels
| checkpoint | Rectify any defective works
| checkpoint | All / any non-conformances close out
| checklist | TOP ENTRY MIXER TEST FORM |  | TOP ENTRY MIXER TEST FORM |  | 4c243352-2bfa-4882-80fb-2690a0518d8a
| section | 1. Equipment Details
| checkpoint | MIXER
ad2f0538-af9e-5e00-b95e-638c4cee6a6c | note | Manufacturer: MIXTEC
dcb77e56-7eea-5734-b6e2-03e1e14b0b49 | textbox | Model
72485f17-c301-56e3-9c7e-2a68ffab5d62 | textbox | SerialL No.
a8a08419-96a4-5768-9f4f-ea9c45a4663d | textbox | Tank turnover
10edd2d9-aded-55ba-b44c-e7b0600d625f | textbox | Superficial velocity
| checkpoint | MOTOR
2f4a7337-b5dc-560f-89ce-432a69f5fa50 | textbox | Manufacturer:
d6773f06-e189-5cb0-969a-b9ce5f042ce2 | textbox | Serial No.
4335a3c2-13a1-53d7-8dd9-178bb7f54335 | textbox | Voltage/ Ph/ V
a588f1c2-a286-53d6-adae-0a5d607d9fda | textbox | Power |  |  | kW
ba0ac9cf-8437-5463-95d8-dbe08e13cdb7 | textbox | Current |  |  | Amp
4b2e7022-e299-5f5c-b613-6f0b86e32641 | textbox | Speed
| section | 2. Visual Inspection
| checkpoint | a) Mixer Frame mounting check
| checkpoint | b) Mixer shaft alignment check
| checkpoint | c) Rotation check
| checkpoint | d) Cable entry & termination
| checkpoint | e) Emergency stop
| checkpoint | f) Local Start/Stop
| checkpoint | g) Operation protection
| checkpoint | h) Motor installed with shed? ( if applicable)
| section | 3. Cable Insulation Test
| checkpoint | Power Cable
9f31ad9b-c9b0-5ec2-95d1-d7ac23d446b7 | textbox | R-Y
5d0c1579-0eb3-5e76-89fd-9f906e8a3036 | textbox | R-B
1653aef3-dc9f-5144-82d7-2ed04452780c | textbox | Y-B
00927283-df67-5380-b99f-6fd67465b1b7 | textbox | R-E
b601757e-4b67-5c37-a5c1-eb707c9434d9 | textbox | Y-E
9cadfb78-8dea-5b55-869a-3715a759734e | textbox | B-E
| section | 4. Operational Test
| checkpoint | Mixer Stator Method:
523dc70d-7bfe-5482-852d-347d8dd38b8d | textbox | Variable Speed Drive
89ec95d1-ab00-5ca3-8c56-aefa4d0e4500 | textbox | DOL
141b92d8-3bb7-5977-a44a-efc15b87d2e6 | textbox | AT
| checkpoint | a) Manual operation test
| checkpoint | b) Auto operation test
| checkpoint | c) Remote operation test
| checkpoint | d) Emergency stop functionality test
| checkpoint | e) Low Water Level Start Prohibited Test
| checkpoint | f) Local Start/Stop
| checkpoint | g) Motor installed with Shed? (if applicable)
| section | 5. Operation Data
| checkpoint | Voltage (Vac)
e44aa3b0-14c3-5af0-95a8-25cb8d766191 | textbox | R-Y
030b8443-b785-5f6a-acd4-4ffc00fbd232 | textbox | R-B
ef88a17b-c63f-52bc-85e4-c27dddefefc4 | textbox | Y-B
| checkpoint | Current (Amp)
c8b666ca-d4c9-5666-aafe-ce51af305c9b | textbox | R
c7a9224e-91f2-52ec-800a-510310160348 | textbox | Y
ff446d1c-215a-5b12-be6f-26cc1aef90fd | textbox | B
| checkpoint-no-value | Regulated Speed (rpm/Hz)
b351f5a0-da2e-5e52-a375-679b4eed6a49 | textbox | rpm/Hz:
| section | Final Inspection
| checkpoint | Final Inspection
c34e847c-5403-5c7b-ab9e-d226950bea52 | note | Prepared By: Contractor Representative
83fd5cbc-552c-5524-a5ba-8494b861ff4f | textbox | Contractor - Name:
c389cd5d-00c9-57aa-a9d1-76745035f128 | date | Contractor - Date:
ffc25e2a-45cc-5782-b1b4-05a4e1ba7c6c | note | Witnessed By: Consultant Representative
37c96518-beff-5449-b9a5-0c555fa4ac60 | textbox | Consultant - Name:
7e60d7eb-d863-57d4-9054-3f19903f9dd3 | date | Consultant - Date:
b655da1f-2526-52a3-a14a-978024cbe139 | note | Witnessed By: Client Representative
7e73422e-b4ec-5add-bb11-20c6273e12c5 | textbox | Client - Name:
ef665bb0-c244-5b62-bd76-f25352bc9f86 | date | Client - Date:
| signoff | Add Signature