## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | GMF-019 - Tool Box Talks |  |  |  |  | Yes | GMF-019 - Tool Box Talks | 0c1a6e03-704f-4b04-8840-79a3fa0fa0fd
checkpoint-status |  |  | checkpoint | Tool Box Talk
text | e3272aff-5ad7-5584-9f05-601db13efeff |  | textbox | Project:
text | c4982672-0b0f-5087-ad36-2079a30053d4 |  | textbox | Tool Box By:
date | b862c72d-bb88-5890-9585-9eb1d66d73f3 |  | date | Date:
text | 201ee0d5-9875-55e5-a6b4-cf9a175f45ee |  | textbox | Attendees:
text | 09727941-c724-5f40-a85c-33083c7a9a50 |  | textbox | Built inducted:
text | 619b529c-5a01-5689-99a8-9fd70dc96bc0 |  | textbox | GM Fire Inducted:
text | c2f2817a-a7e9-5f58-93d6-ec4fd5050d8d |  | textbox | Items for Discussion:
text | 1fd593e8-0141-5f2f-911a-7a069dd2409f |  | textbox | Items for Review and discuss at next meeting:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | Incident Investigation Report |  |  |  |  | Yes | GMFORM-020 - Incident Investigation Report | 14f03151-c05b-400d-9088-2325403cfe50
checkpoint-group |  |  | section | Details
checkpoint-no-status |  |  | checkpoint | Incident Investigation Report
label | 26c7a877-82ff-5d4d-9964-4e831bec896a |  | note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
label | c7009061-5139-5526-a062-83adc69dbabf |  | note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
checkpoint-status |  |  | checkpoint | Class of Incident
boolean | 319b1c6b-9f44-55ea-b16c-b1a07631b0a3 |  | tickbox | Injury
boolean | 0adde8bb-4f35-5400-993c-c7d0180c2af2 |  | tickbox | Property/Plant Damage
boolean | 621668cf-7542-5404-a731-45e940e7d4ee |  | tickbox | Near Miss
boolean | 95d75d3d-669b-5354-b3b0-96b4a129a1c0 |  | tickbox | Environmental
text | 67776edd-303c-58ed-b6a4-4c93c3ad56de |  | textbox | Other
button | c5515547-5acf-5223-adaf-ff810432bbba |  | button | Reported | Yes,No
text | e433ee97-85b5-52fa-97a9-25ca60ea13bc |  | textbox | Details:
button | 857bb4fc-18cf-5306-a76e-802c247b752f |  | button | Further Action Required | Report to Authorities,Other:
text | e1d07f73-ecd2-514f-8842-5a2e0effd57f |  | textbox | Other (if applicable):
checkpoint-status |  |  | checkpoint | Details of Incident
date | 92284681-efd2-53d4-8e0b-d46de0d7e437 |  | date | Date of Incident
text | 673f8d24-ff72-5e07-b453-93880d52a9f4 |  | textbox | Time of Incident
button | 325ed646-43a2-5fc3-9425-0bef6e03fe7f |  | button | am/pm | am,pm
text | 4b70799d-acc0-5966-a907-0ef28ba3f126 |  | textbox | Witness Name
text | 541505a5-4428-5a09-a1c7-efa380a6cf43 |  | textbox | Witness Contact
text | fdfff4a4-8f76-588d-97bd-e1944521b0f4 |  | textbox | Nature of Incident
text | 725a55af-18c7-57c8-afe2-bfa092de1b6a |  | textbox | Location of Incident
text | 3f3be10a-9abd-53e3-82f0-2667d7e71aa8 |  | textbox | Description of Incident
text | b482344c-2e6d-577b-9ddb-70e3d053f88b |  | textbox | Details of damage to equipment/property?
checkpoint-status |  |  | checkpoint | Injured Person/s (if applicable)
text | 24e6a102-3cb8-5740-9562-2f6fcc5871ca |  | textbox | Name
text | c68b8d90-60e8-5111-8e35-d7857559c628 |  | textbox | Address
date | e678a59a-6b1f-5756-b6cf-2d17da084cb1 |  | date | Date of Birth
text | 66d64f8b-744b-59a5-8649-41a77a1b3902 |  | textbox | Occupation
text | f3631539-86a5-543a-ad2e-dad8be5e4b52 |  | textbox | Employer
text | df6586a3-039d-5599-8263-333b90fa2c9b |  | textbox | Referred/transferred to
checkpoint-group |  |  | section | What factors contributed to the incident?
checkpoint-status |  |  | checkpoint | Environment:
boolean | 5bebb027-96f0-5460-890a-132a143a47e3 |  | tickbox | Noise
boolean | 5e04e3c6-c511-54d9-855b-61b79ba33d83 |  | tickbox | Layout / design
boolean | be7367f6-b65c-5e31-9806-b57e064484b1 |  | tickbox | Lighting
boolean | b344a257-3875-58bf-9242-ae1b70d9c52a |  | tickbox | Dust / fume
boolean | c1b98094-8764-57ae-8d8f-23524f9f5e83 |  | tickbox | Vibration
boolean | c6079cb7-cfed-539d-a3de-4ffe5242c1a5 |  | tickbox | Slip / trip hazard
boolean | 85c76db0-7b13-5e0b-b320-9a0f6543aa2d |  | tickbox | Damaged / unstable floor
boolean | 1e95cef6-f5ed-5510-89c5-ba7214c48c16 |  | tickbox | Other
text | 7af769cf-fdc6-5763-a34f-36b7668432b1 |  | textbox | Other (if applicable):
checkpoint-status |  |  | checkpoint | Equipment/materials:
boolean | fe1e78dd-509e-5b53-8078-3c13e8d0020a |  | tickbox | Wrong equipment for the job
boolean | 48449b5b-94f5-56fd-aa68-28179f2a1234 |  | tickbox | Equipment failure
boolean | 34dbaa91-66eb-5b35-86e6-12b7080c0add |  | tickbox | Inadequate maintenance
boolean | 340c7cf0-23ea-5aaf-be3e-08341656325a |  | tickbox | Material / equipment too heavy / awkward
boolean | d44177e4-2535-597e-9309-931a3a8d12ee |  | tickbox | Inadequate guarding
boolean | 3d7d49b4-0c2b-5d53-bfdc-aa67787549d7 |  | tickbox | Inadequate training provided
boolean | 000690e7-a449-5a80-a869-a79c71c27c48 |  | tickbox | Other
text | e2a3d872-b06f-56d7-868a-7dfc157a60c7 |  | textbox | Other (if applicable):
checkpoint-status |  |  | checkpoint | Work systems:
boolean | 5dd9bf85-df05-50a5-9d39-ba8c92524aee |  | tickbox | Hazard not identified
boolean | 2fbf68fc-22c1-530f-9cb2-b87b25344ca7 |  | tickbox | No / inadequate risk assessment conducted
boolean | 0387a054-0cba-5d62-97d1-4479ebe8b41d |  | tickbox | No / inadequate safe work procedure
boolean | d37a698b-994a-54ae-81f2-b04aa7a1df63 |  | tickbox | No / inadequate controls implemented
boolean | c6ba7810-1a06-5766-8b22-30f4fdc6cfd1 |  | tickbox | Hazard not reported
boolean | 8f15171b-ea63-518f-a1d3-40a0cdb8bb86 |  | tickbox | Inadequate training / supervision
boolean | 22ddaef3-e684-5031-82f2-eabc39055e20 |  | tickbox | Other
text | df7a8e40-28bc-528b-b28a-0b6efe49c3d3 |  | textbox | Other (if applicable):
checkpoint-status |  |  | checkpoint | People:
boolean | 68c29607-73a8-59a9-918a-e8a1a7758f3b |  | tickbox | Procedure not followed / no procedure exists
boolean | f49a9eb6-f469-5486-a041-424512d20bb0 |  | tickbox | Drugs / alcohol
boolean | 315224a4-528b-59d0-b752-048abb08d4dc |  | tickbox | Fatigue
boolean | 2ed0f27c-86d8-5e84-a4f2-361debecd863 |  | tickbox | Time / production pressures
boolean | 1cf8af67-af67-5409-bca2-d1a6cdab08ea |  | tickbox | Change of routine
boolean | 91dc8070-c2b8-5f0c-bd24-be694c6f87a7 |  | tickbox | Distraction / personal issues / stress
boolean | 06712e9c-8051-58f7-8676-16be7955cabe |  | tickbox | Lack of communication
boolean | feefc030-bfe5-5354-a12e-104f9508da2b |  | tickbox | Other
text | c3685b47-7234-5973-bc9c-d337e162b8f6 |  | textbox | Other (if applicable):
checkpoint-group |  |  | section | Corrective actions:
checkpoint-status |  |  | checkpoint | Contributing factor
text | 34fb92e3-cc81-5b39-9cc4-3570d31ea806 |  | textbox | (from above list)
text | 73874509-bac9-555d-8853-d738436ac006 |  | textbox | What are we going to do to fix the problem?
text | da26fb44-6d60-52fb-870e-90b8c5ffd716 |  | textbox | Who
text | f5d8b083-01e8-5841-aea1-53e16258b921 |  | textbox | When
date | 585d5a57-d317-5a2c-8c86-399f10c406d3 |  | date | Completion date
checkpoint-status |  |  | checkpoint | Completed By
text | 11f31f0b-4a44-5a8b-8133-2e07b430d536 |  | textbox | Name
text | 9346513a-1500-5fae-b25b-d6e769dd31d7 |  | textbox | Position
date | 40b6d092-dcdd-58fd-840d-c4a54e7f5c2d |  | date | Date
holdpoint |  |  | signoff | Signature
checklist-sectioned |  |  | checklist | GM-ITPS-004 Fire Alarm and EWIS Installation | itp |  |  |  | Yes | GM-ITPS-004 Fire Alarm and EWIS Installation | 240de470-1e53-449f-802a-3a16674f79fd
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - CABLE TYPE & SIZE TO DESIGN CRITERIA
label | f8dac3cf-7f89-5d37-ac5a-830eb299096b |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018 Have a cross sectional area of no less than 0.75mm2 AS3000
label | d4373d7f-af63-53f4-a979-fa61ca335e8d |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | d4b4332c-6f0e-571c-9fe1-31055d8a0cee |  | radio | C5.4.0 Wiring | Pass
text | 42d19c37-5762-5c0f-ac35-42965e6d2d50 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 7916330e-e656-59e0-bd79-b9fcac35e5e4 |  | note | QUALITY CONTROL - I
text | 7c92011c-d24c-5d68-a321-a023538921c7 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | b8127666-6248-580a-b95a-b98f692a958b |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - CABLE HEIGHTS & LOCATION ADEQUATE FOR FIT OFF
label | 37dce47c-0b52-5092-8408-687735baf2d8 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: internal domestic and office situations where cabling is mounted on walls at heights above 1.5m AS3000
label | 0510b6fb-4554-5e2b-bb12-8eec866e7aaf |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 2d798dde-f905-5fca-9501-b4488b2c1ea1 |  | radio | C5.2.5 Control Loops | Pass
radio | 8de9f9f4-e686-5972-9525-dc9a28e69a6e |  | radio | C5.4.0 Wiring | Pass
text | f694ba28-9d02-5c3d-93cd-c0339d6a2315 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | ef303001-8313-5587-9acb-a1fa09239568 |  | note | QUALITY CONTROL - I
text | d395e679-61ed-5652-a0f4-dc6b26b8ffce |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 3e0e8337-864b-52be-8836-8d3f6fbc936d |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - CABLE FIXED TO SPECIFIED REQUIREMENTS
label | 439ba0eb-cf3a-5682-a2a8-d5c50d8a61fc |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
label | 6029b9f5-1f59-5de0-8a21-59db4883c7c2 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | a2dadb8c-68d5-5dcd-9fe4-7a491faeb967 |  | radio | C5.2.5 Control Loops | Pass
radio | 54fcb519-3d0d-5aa7-bccd-2bae4dcb3881 |  | radio | C5.4.0 Wiring | Pass
text | df2b80ad-27de-5ea1-aa43-fa27b60ae608 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | a7bb148e-2574-5f13-8cb2-b3771c7094d1 |  | note | QUALITY CONTROL - I
text | 5fbdcfd7-2fda-56cb-871f-51eb9e99b2e9 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 8aada611-b0ef-5e08-bf7b-fdbbcef047e5 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - DETECTOR BASES FITTED OFF
label | e1bf8b0e-4a84-5ff5-9d55-08b76af6ee91 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670, AS1668: Detectors that can be contaminated by construction works should not be fitted unless suitably protected until the construction works are completed.
label | 185b68d0-e0b5-55eb-ab56-21a77218f08c |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | 731b4a49-9cc1-5955-b38c-6ed20be93a3c |  | note | QUALITY CONTROL - I
text | 7ceb6321-a1f4-5377-bc5f-7e9eeb42c93b |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 46f68240-f238-5e60-8ade-f4a0bea6279a |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - DETECTOR HEADS INSTALLED & TYPE CHECKED
label | 49c12301-c269-5013-a07c-88bec9c32b42 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Detector type to appropriate location. Installed to Latest RCP
label | 44e5a26f-4e94-5507-978a-60874f10b71b |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | fae2daae-6af1-5dbe-9d92-9aabecbab1c4 |  | radio | C5.6.0 Sensors/Detectors | Pass
text | b8cc3abf-143d-5cef-b3b5-69662e3ece1b |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 1e6fb508-502c-5a57-81af-b8bbe8903d18 |  | note | QUALITY CONTROL - I
text | ed3a5ea9-79f1-5055-a6fd-e02c73fdc8cd |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | bc0ec284-845b-51bd-b0ab-e5791eaeb6f5 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - MANUAL CALL POINTS INSTALLED
label | 4f13b685-ecb7-50f3-a1a9-6302ccd2de9d |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: An MCP shall be mounted between 750 mm and 1100 mm above floor level and a clear space of 600 mm shall be provided in a semi-circle in front of the MCP.
label | d0e6a243-0eeb-5269-82f6-fb152d6fc2c8 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 13f903ba-5120-54f5-a8fa-04dc0299fce4 |  | radio | C5.10.0 Manual Call Points | Pass
text | 4bf394f6-063f-53cb-9f13-449c88091e42 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 280a076b-2ddd-5f59-9e02-15378b2e808f |  | note | QUALITY CONTROL - I
text | bcda8c10-b038-5ad0-8bd5-fa11f5efc563 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 1c902bc3-7c81-518e-840b-19b4537124ef |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - STROBES FITTED OFF
label | 4e5a0097-cf38-51fa-be53-dda8a7016db7 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Check with Design Drawing and/or RCP
label | 5755ff7e-5532-57d8-b0dc-bc52009bbf4f |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | fc83272b-0008-5df2-ba2e-9651ba32c71b |  | radio | C5.2.2 Set Points | Pass
text | c1aac25b-863f-573f-b143-237b1bf15193 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | f1585f6c-d8b7-52db-9b4c-774244b1a10c |  | note | QUALITY CONTROL - I
text | 9cc917d3-f0f7-5262-898c-083f642685a7 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 10a116f0-4f81-5789-a759-aff34d2fd9aa |  | date | DATE:
checkpoint-status |  |  | checkpoint | 8 - SPEAKERS INSTALLED
label | 6c82906b-94c6-59e1-9575-51d4af3ec855 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670: Check with Design Drawing and/or RCP
text | 463c0674-93bc-5c37-94d2-0c5ea2f3a106 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 0bf48339-ef41-5dcd-9ba7-b82252d60b1a |  | note | QUALITY CONTROL - I
text | 6b85662a-3ddd-5a21-b45f-18467db78e76 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 707570db-a2c9-5def-90c4-6865bf367df2 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 9 - WARDEN INTERCOM PHONES
label | dd32d5cc-0920-5cb8-ae4b-40fea56c1182 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018: The WIP handset shall be mounted at a height of not less than 1200 mm and not more than 1800 mm above finished floor level.
label | af49d41a-e9dc-5963-9691-9a4b6c1ca905 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | ea915006-c7ae-5c22-8b7a-060a7354cb13 |  | radio | C6.2.8 Warden Intercom Phones | Pass
label | c2d8f4e6-9db0-57ce-a105-087b72efaa29 |  | note | QUALITY CONTROL - I
text | f40ae91e-c1b2-59b4-9b9f-01caf65a2ac7 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 72706a85-c6a4-5109-bcd7-5e28fde29f62 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 10 - SPRINKLER INTERFACES FITTED OFF
label | ed3d0ab4-fc6f-5524-9c43-3ec4f73de60f |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
label | 4cb6a86f-e8d3-56ae-8074-f25cadff44e2 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 6ac0db7a-3970-5d40-a730-6a9611e7f7a2 |  | radio | C5.2.2 Set Points | Pass
radio | 54aae543-3290-566e-ac16-156ec12a4a60 |  | radio | C5.8.0 Modules Input/Output | Pass
text | 6be1ffe6-f62b-5c8d-8205-c745f650e6f8 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 354e8838-d46f-579e-8a3f-33935025e063 |  | note | QUALITY CONTROL - I
text | fd44afeb-b35b-5a19-81a7-271919b4c41f |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | a11d1279-f471-5414-9309-ba836ceb7cbf |  | date | DATE:
checkpoint-status |  |  | checkpoint | 11 - FIRE RATING TO PENETRATIONS CORRECT
label | 895532f9-bede-51e1-b0e4-99c2b16a6038 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: Ensure correct Test Report is used – refer to FRL requirements on wall selection
label | 192a1a4b-c22c-54f3-8eb3-9be62b887063 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 48eb6881-7716-560e-9690-ee597992ef59 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 69800c1d-aead-5ff3-8cd0-922deec70218 |  | note | QUALITY CONTROL - I
text | 74f8b7f7-8280-5a31-b506-5e548bce54ae |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | b5f74187-9b95-590c-8635-51c7e40542f1 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 12 - LABELS AFFIXED
label | 6bdffb09-2bf8-5e8d-91f7-72ab60bf16ec |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: The label should be positioned close to the service penetration
label | 379427d2-26ec-558f-ae77-f3a1f069359c |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 0e9ccd41-7920-55d5-ab0d-b046ff463637 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 45cfbc81-93de-5aef-9826-fd78670ce5ac |  | note | QUALITY CONTROL - I
text | 69975f77-b866-53ec-931f-dfc891e9bef3 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 9a8723d3-cd73-5c79-9962-a0b23908fedc |  | date | DATE:
checkpoint-status |  |  | checkpoint | 13 - ACOUSTIC PENETRATION SEALING
label | 195a101f-30de-5680-ac53-cd69ffbe0bd4 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: Sound proofing sealant may be used depending on dB Level requirements
label | 4757be05-a185-5444-8a85-cb18b6997e04 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 52c419cf-45da-5601-a2fb-e94ac97c7a16 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 738f9fe0-9eae-5b0c-975a-ebbdf77eecb0 |  | note | QUALITY CONTROL - I
text | bea98d6b-b823-5809-b4d4-6fd17d444a82 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 5ccff0b7-8bba-5307-b5c0-a151b8380f9d |  | date | DATE:
checkpoint-status |  |  | checkpoint | 14 - CABLE TRAY BRACKET SPACING
label | 109e6a61-7de7-5368-8ef9-c1519eb7c4d0 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
label | c9949153-631b-5da2-ad92-c3fa0084977f |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | d846db4a-1202-556f-b961-a728eec2c478 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | bd63b58d-9233-592c-8cab-a3665c64c432 |  | note | QUALITY CONTROL - I
text | c6280678-ac3e-5a48-977b-df63e839f34f |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 72935626-1607-53da-a471-7d2cdcd7198d |  | date | DATE:
checkpoint-status |  |  | checkpoint | 15 - INSTALLED IN ACCORDANCE APPROVED WORKING DRAWING AND LATEST ARCHITECTURAL
label | 56e15e87-a18c-5df0-bde9-446f79c04651 |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House QA
label | 1d681959-82d8-5aea-a843-dd3ddc2246c1 |  | note | ○ Up to Date drawing register
label | 00b3202b-4785-58f0-a3eb-23d1a60a89a7 |  | note | ○ Drawings updated with MPX approved references
label | 23deef37-7dc7-52a1-b042-572607a55cb1 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 8b012b47-842e-51d3-8c39-5ec9edbe0f39 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 6e74e04b-a287-5cc5-854f-196509dafdc0 |  | note | QUALITY CONTROL - I
text | e8155fc3-2034-5a30-9cdb-487801a4636b |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 26ff3a14-1f45-56ed-9c1d-62ca3fbe553f |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | 82d973cb-13c9-5c75-9523-d75114cf5359 |  | button | Hold Point Required: | Yes,No,Other:
text | 49c59905-a9a7-557d-ae5c-b571349f973a |  | textbox | Other (if applicable):
text | 1367999a-d71a-5b59-b8c4-81fc451e9c01 |  | textbox | GM Sign Off - Name:
text | f940793a-0209-595b-a95c-042a832172e2 |  | textbox | PC Sign Off - Name:
text | 1f36fef9-c5af-5acc-83e7-39cd92ab4d4c |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | Site Inspection Checklist |  |  |  |  | Yes | GMFORM-007 - Workplace Inspection Checklist | 2f813446-4b4d-4034-8d01-092638082845
checkpoint-group |  |  | section | 1. Administrative, training and risk management requirements
checkpoint-status |  |  | checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
checkpoint-status |  |  | checkpoint | 1.1 - All workers carrying out construction work have received the general construction induction training.
checkpoint-status |  |  | checkpoint | 1.2 - Workers have been informed of the site-specific health and safety rules.
checkpoint-status |  |  | checkpoint | 1.3 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
checkpoint-status |  |  | checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
checkpoint-group |  |  | section | 2. Safe work method statements
checkpoint-status |  |  | checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
checkpoint-status |  |  | checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
checkpoint-status |  |  | checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
checkpoint-group |  |  | section | 3. The work environment
checkpoint-status |  |  | checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
checkpoint-status |  |  | checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
checkpoint-status |  |  | checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
label | f8272eb3-01c5-5337-a307-f72286a48c32 |  | note | ○ each worker to carry out work without risk to health and safety
label | 1be19c4f-a82e-522b-98e5-e5aa656efb60 |  | note | ○ people to move within the workplace without risk to health and safety
label | aef67d61-2c29-5ed8-9db6-bcf3ceacb0db |  | note | ○ safe evacuation in an emergency.
checkpoint-status |  |  | checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
checkpoint-status |  |  | checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
checkpoint-status |  |  | checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
checkpoint-status |  |  | checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
checkpoint-status |  |  | checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
checkpoint-status |  |  | checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
checkpoint-status |  |  | checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
checkpoint-group |  |  | section | 4. Confined spaces
checkpoint-status |  |  | checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed GMFORM 011A Confined Spaces Risk Assessment.
checkpoint-status |  |  | checkpoint | Prior to commencing the works, GMFORM 011B Confined Spaces Entry Permit has been completed and approved.
checkpoint-status |  |  | checkpoint | 4.2 - Appropriate signage has been erected for all confined spaces.
checkpoint-status |  |  | checkpoint | 4.3 - First aid procedures and rescue procedures to be followed in accordance with GMFORM 011C Confined Spaces Rescue Plan in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
checkpoint-status |  |  | checkpoint | 4.4 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
label | bed85791-cdf2-5734-99e5-42eabe40f212 |  | note | ○ nature of all hazards relating to a confined space
label | be7ccc94-3134-5b95-8b20-72fefb415b43 |  | note | ○ need for, and the appropriate use of, control measures associated with those hazards
label | b110c5ef-6275-5bf5-a856-5a63e44d03ea |  | note | ○ selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
label | 1a99ce71-7f11-5eeb-a21b-b350ded8d8c3 |  | note | ○ contents of any confined space entry permits that may be issued
label | b0c02c77-ff62-5a00-8a01-e40663b3102c |  | note | ○ emergency procedures.
checkpoint-group |  |  | section | 5. Working at heights
checkpoint-status |  |  | checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
checkpoint-status |  |  | checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
label | 15a0bb70-25a2-55ce-8391-f9705261ae79 |  | note | ○ each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
label | 098e60b1-4049-5b81-9802-dc44b50477cb |  | note | ○ the risk of death or injury that may result because of the hazard has been assessed
label | d8e17ce6-5b0d-5d71-adcb-c9012baa2fa9 |  | note | ○ any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
checkpoint-status |  |  | checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
label | df712649-e072-54fe-b908-fe63884b915b |  | note | ○ prevent a person falling any distance
label | 28993959-da47-509e-a241-bb45845a83ee |  | note | ○ if prevention is not practicable:
label | 55b684af-87ab-5194-82b6-3e644dbb1a7b |  | note | – arrest a person’s fall
label | 7575aa24-7d52-5200-8719-e639552c447b |  | note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
checkpoint-status |  |  | checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
checkpoint-status |  |  | checkpoint | 5.5 - Ladders are used where the:
label | d8458251-f7d1-554a-bcc3-372ab76e7d8a |  | note | ○ bottom of the ladder is on a stable surface
label | c8fdd838-d4e2-5652-83e9-9bc5b3b6145b |  | note | ○ rungs of the ladder are approximately level.
checkpoint-status |  |  | checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
checkpoint-status |  |  | checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
checkpoint-status |  |  | checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
checkpoint-status |  |  | checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
checkpoint-status |  |  | checkpoint | 5.10 - GMREG 004 Plant and Equipment Register is up to date and includes all mobile plant in use.
checkpoint-status |  |  | checkpoint | 5.11 - GMFORM 013 Plant and Equipment Pre-Start Checklist has been completed for all mobile plant in use on delivery to site.
checkpoint-status |  |  | checkpoint | 5.12 - GMFORM 014 Plant and Equipment Regular Checklist has been completed for all mobile plant prior to commencing operation of the plant that day.
checkpoint-status |  |  | checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
checkpoint-status |  |  | checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
checkpoint-group |  |  | section | 6. Electrical
checkpoint-status |  |  | checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
checkpoint-status |  |  | checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
checkpoint-group |  |  | section | 7. Hazardous substances and dangerous goods
checkpoint-status |  |  | checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
checkpoint-status |  |  | checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
checkpoint-status |  |  | checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
checkpoint-status |  |  | checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
checkpoint-group |  |  | section | 8. Corrective actions
checkpoint-status |  |  | checkpoint | Corrective actions
checkpoint-group |  |  | section | 9. Inspection sign off
checkpoint-status |  |  | checkpoint | This workplace inspection checklist has been completed by;
text | 4b32712d-5eb5-5f21-8318-9f10d9fee1e3 |  | textbox | Name:
date | 8f6f1e26-c9d1-5d5c-beb5-fb775c1e28a2 |  | date | Date:
holdpoint |  |  | signoff | Signature
checkpoint-status |  |  | checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
text | be7ee8f6-2fdf-5e61-aee6-adf9bbb71704 |  | textbox | Name:
date | f58dc23b-c6d5-59c2-9d2a-57694b8eff87 |  | date | Date:
holdpoint |  |  | signoff | Signature
checklist-sectioned |  |  | checklist | GM-ITPS-014 In Slab Conduit | itp |  |  |  | Yes | GM-ITPS-014 In Slab Conduit | 3f734621-7d45-403b-bf9b-98985fdd1ecc
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - CHECK CONDUITS ARE CORRECT TYPE, SIZE AND QUANTITY TO CRITERIA
label | 6780a9f8-d748-51be-9d5d-f0fc19e1b037 |  | note | ACCEPTANCE CRITERIA SPECIFIED - In-house QA
label | fe59136e-d968-5735-a78a-7e30e894d109 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 1d4d54b6-61c5-55a5-bc17-fcafd822cc07 |  | textbox | DRAWING REFERENCE NUMBER - Cut Sheet Drawing Number:
label | f26ceaae-0baa-569f-b48d-63c83a2e529a |  | note | QUALITY CONTROL - I
text | 4d8aa487-53c9-502f-a7ca-5e9d96fae908 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 3f00b1a5-c401-5cc9-96f6-b3d6fc3103d3 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - CHECK CONDUIT ROUTE IS AS SPECIFIED IN LAYOUT/ DESIGN CRITERIA
label | 17fdd024-d03e-559e-8270-225b5e16c8e5 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Shop drawings (certified by an RPEQ engineer) are to be provided for each and every item required within 1170.4 Structural design actions – Earthquake actions in Australia.
label | c035957e-0e71-5968-8883-2dedb60e5f2b |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | 4d767396-ad74-5214-a089-f107d1687b04 |  | note | DRAWING REFERENCE NUMBER - By others.
label | 2dd17b24-9724-509e-ab5f-c7f9c512f088 |  | note | QUALITY CONTROL - I
text | fbd16d5e-1a59-56db-80fd-babe64df79fd |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 63662228-becf-5361-b037-9af77fea6063 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - INSTALLATION, CONDUIT IS JOINED CORRECTLY
label | 81d77051-7052-56e7-a507-dea22124db6f |  | note | ACCEPTANCE CRITERIA SPECIFIED - Installation is in compliance with AS 1170.4 Structural design actions – Earthquake actions in Australia.
text | 324ca920-7767-5f4e-8739-aa28e114ce76 |  | textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | 7b1f61df-cd60-574e-99e4-5ee8bd642e06 |  | note | QUALITY CONTROL - I
text | 525f8621-c5b8-5a2d-b8ff-533117f9c647 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 6415e655-f646-5319-85c1-0396ac43487c |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - CONDUIT IS TIED IN
label | 1d5ce0fa-c703-58d5-af7a-1e50f6b312d5 |  | note | QUALITY CONTROL - I
text | ee218b48-8e5e-56f7-88de-b2e8e27beae6 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 87fc4d82-0207-51a4-83a4-70b4fc735966 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - CONCRETE COVER IS IN PLACE
label | 7709ecd6-30da-5808-a869-abaea38fcc09 |  | note | ACCEPTANCE CRITERIA SPECIFIED - General Technical Requirements – Services Ripley Sub-Acute Facility (RSAF) 2.2.3 - 9. All Fire services penetrations post concrete pours are to be immediately sealed with sheet metal cover plates (mastic or similar) to prevent water ingress. Plates to be fixed by use of nylon anchors or similar. Plates to remain in place and maintained until directed by Hutchinson Builders to remove.
label | f8e1478e-8dea-5143-ad8b-73e40c6aa03c |  | note | DRAWING REFERENCE NUMBER - Seismic Design Drawings as supplied by Seismic Engineer.
text | e782a2e2-c839-54c5-a510-dc5daac59887 |  | textbox | Construction Issued Drawings Number:
label | a65fd5be-0b73-5a00-9106-26f63212b294 |  | note | QUALITY CONTROL - A & I
text | ba96b991-5212-52fa-8741-6994b11398bf |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f345e4fd-195b-56e0-ba35-8f341112d09a |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | e933d674-6e4f-5ac0-8454-114932b6d60f |  | button | Hold Point Required: | Yes,No,Other:
text | 7b6245f8-135c-55bc-81d9-e85647ae9cc7 |  | textbox | Other (if applicable):
text | 44e88cf3-cf50-5199-a59a-6ff2df77334b |  | textbox | GM Sign Off - Name:
text | c310eec6-1061-5275-885f-06e3bf9bf329 |  | textbox | PC Sign Off - Name:
text | 5bb0d0c1-fcd4-5df4-839d-9c9472e4a927 |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | GM-ITPS-011 Fire Sprinkler System Commissioning | itp |  |  |  | Yes | GM-ITPS-011 Fire Sprinkler System Commissioning | 87d22ebe-ea73-4d08-b0d0-9fcc84eff4c2
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - CHECK SPRINKLER HEADS ARE INSTALLED IN AN ENVIRONMENT IN WHICH THEY ARE SUITED
label | a1bc0a3b-34c2-5dd5-a058-cba4e7d35143 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 2.2 – heads installed to correct classification and spacing
label | df427a2e-4718-5497-bb9a-a615bafea23f |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 191419f5-283c-5888-a7ce-0a0e935b0189 |  | radio | W5.2 State of the System | Pass
label | d6041c36-1419-56c7-b2b3-531307f739ce |  | note | QUALITY CONTROL - I
text | 91dede89-a3ec-5775-ba8d-89b7f8098db9 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | b276a28b-31cb-54f3-8953-3e849135be0d |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - CHECK HYDRANTS ARE INSTALLED TO CODE AND HAVE REQUIRED CLEARENCES
label | f80e2c8f-7799-5c86-8b93-b57bd18b9c1c |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2419.1-2005 – Section 3.2 – Clearances differ when related to internal or external hydrants, ensure correct standards are implemented
label | c66a009f-8888-5cd8-980a-f3de1e91a93e |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | c32092f8-0723-5d6b-b7e6-952a9353b130 |  | radio | W5.2 State of the System | Pass
label | 4c49fb3c-8949-5187-a912-fcb33da2e6b1 |  | note | QUALITY CONTROL - T
text | ff8eef12-2bc6-5fa5-a733-22b43cebe3ca |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | c01973b6-4cd7-51bb-8c08-ae996ea92fe3 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - AIR TEST INSTALLATION BEFORE WATER FILL
label | 552ab790-32e5-53a1-9db2-5dbbb5214d60 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 7.9.4 – hold 300 kPa for 30 minutes without a 10% loss.
label | e6974635-a695-5728-810e-241cea261ea5 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | cd742355-5c43-5b04-84d6-62bc221585d8 |  | radio | Hold Point Required: | Yes
radio | 28a04ff0-1a4a-51d7-bcb7-0c06e922dc7b |  | radio | W5.4 System Filling and Venting | Pass
label | b65d9064-8be6-544a-a8ff-5694dc7980ec |  | note | QUALITY CONTROL - T
text | 410be762-8414-57f0-a613-d025ff0e2c79 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | e895f7c2-c81b-59c2-9ca6-add6ad3f0648 |  | date | DATE:
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 4 - STATIC TEST INSTALLATION WITH WATER TO 1600KPA
label | c67c9738-a6d4-551a-9d96-599916a9da62 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 7 (7.9.3) – system tested to 1.6MPa and holds pressure for 2 hours
label | 644adf6e-bff1-5c07-aaa1-f73929372033 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 049b9bcc-6983-5978-a622-29054852e3b0 |  | radio | Hold Point Required: | Yes
radio | 71107acd-ef7b-5ed3-aa20-56efcf4cf7f3 |  | radio | W5.4 System Filling and Venting | Pass
radio | d701db62-cbae-5b8e-bfde-932e9674498d |  | radio | W5.4.1 Pressure Testing | Pass
radio | a66fcb0b-3e0a-5c3d-b190-bb040555f0e9 |  | radio | W5.5.2 Flushing Procedure | Pass
radio | d1d6a48d-233a-529e-b6a1-853a7880161b |  | radio | W5.7 Static Completion Records | Pass
label | 53d0030b-271e-5918-859a-fdaef12119c7 |  | note | QUALITY CONTROL - T
text | 47ba1fee-398d-5eda-a72a-a23889a90ed2 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f10c8b69-1298-59f5-b656-5263ca999409 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - CHECK & TEST WATER SUPPLY CAPACITY TO MEET SYSTEM DEMAND
label | 55c48131-57e6-5bb3-b43f-9f49c4b793e3 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - section 4.2.2.1 – capable of supplying the flow and pressure requirements of the sprinkler system.
label | bf23fbf0-8160-5bbf-9ab0-6882cdebc782 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | a5416993-59ad-5ffa-a0ea-7040620095b1 |  | radio | W7.2 Flow Rate Measurement Tolerances | Pass
radio | c94240d1-ae77-591e-acfd-1c22d23c6818 |  | radio | W7.5 Preliminary Flow Rate Check | Pass
label | 45a6cca4-5e1d-5cb1-bbf6-beb6586e0676 |  | note | QUALITY CONTROL - T
text | 3b5391a3-6871-5cfe-9d76-ca5898cc9624 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 2b973774-7318-5fbc-a2a0-97132be5bd98 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - CHECK OPERATION OF PRESSURE SWITCHES TO DBS
label | 91ec9be0-6d6c-53ff-af4e-f83f80aed0b4 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Appendix H4 – Test via 15mm test valve and record time taken to operate. Confirm with ASE monitoring service that alarm was received.
label | 2c32260a-e0fc-58b4-8f21-ad645707f5ea |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 0cd149ee-fdf2-56f6-b568-6e909ccbdbdd |  | radio | W5.6 System Checks | Pass
radio | 375383a4-9404-56b3-936e-fadb9c9d370c |  | radio | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
label | d8715d05-d8db-571c-9625-6c1586442ba8 |  | note | QUALITY CONTROL - T
text | 7852e6a5-862d-5ef5-87e8-d360d0afbbea |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 9127040c-45ac-52e1-a65a-adddc758652c |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - CHECK OPERATION OF PRESSURE SWITCHES FOR PUMP START
label | a94921ad-e0f5-5d9d-b5d2-c560e19f6760 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Appendix H5.4 – P/Sw to be tested via dropping system pressure via test valve or remote test point.
label | feae7986-5236-5e35-9fba-1f788f424576 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | c6a7534e-e4b9-5a01-8d76-40a269665798 |  | radio | W5.6 System Checks | Pass
radio | bb82baf2-8718-5312-862e-6cc3e37d43b2 |  | radio | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
label | 090f0a3b-d3d7-558b-ae20-61819890f053 |  | note | QUALITY CONTROL - T
text | 12733177-6996-5ac5-80a4-32fc5aba4f22 |  | textbox | PERFORMED AND/OR WITNESSED BY:
date | 71193325-c816-52cd-b483-d41b91d225ef |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - CONDUCT 100% TESTING OF PRESSURE SWITCH, FLOW SWITCH & VALVE MONITOR
label | 5e7e77fa-2b60-51b0-96d1-018a9afb5c42 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 Appendix H6 – equipment to be tested to procedure set out in standard and in conjunction with Fire alarm workers.
label | 20bc593d-5337-5a7e-8a64-7a92781697b1 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 05f8ff2c-adc0-537e-a912-11c42fdd1328 |  | radio | W5.6 System Checks | Pass
radio | fa28d8c5-c08a-5624-99cf-448d60bebf42 |  | radio | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
label | 8bfab605-ee63-532d-a59f-2847089a4cb1 |  | note | QUALITY CONTROL - T
text | c8a5676b-2670-568a-b167-5f936e4ca5b9 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | c5fac5b4-d4e0-53b8-87f3-cc95679f8a96 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 8 - CHECK PUMP PRESSURE AND FLOW REQUIREMENTS
label | 4632964c-764d-5545-b0f3-fd43504a9edd |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Section 14.9 – shall be capable of satisfying the flow and pressure requirements of the design +50kPa.
label | 018c206a-4a28-5010-a169-88ae37e67806 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 6d993509-e030-55d0-9266-9cbd66bd80aa |  | radio | W7.2 Flow Rate Measurement Tolerances | Pass
radio | c295a8b0-020e-59cd-842c-8c293ea0ecdf |  | radio | W7.5 Preliminary Flow Rate Check | Pass
label | d644c081-3aa7-560a-a220-2eff0fdeef47 |  | note | QUALITY CONTROL - T
text | 45f5b53f-686c-5e2c-9d2c-c2acff080769 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 9b03aee2-cbe2-5af5-aaed-7447ad25f7fb |  | date | DATE:
checkpoint-status |  |  | checkpoint | 9 - WITNESS TEST HOLD POINTS
label | baf300a4-9c67-5650-ac74-0b5e8f8312ec |  | note | ACCEPTANCE CRITERIA SPECIFIED - PIPE TESTING PROCEDURE
label | 95f77a54-53ad-55e5-a06b-e18407aedb37 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | f279de52-ee0f-57b2-a456-e1791adc10b5 |  | radio | Hold Point Required: | Yes
radio | 58d75261-bee2-5178-a4b1-31b2caaccc28 |  | radio | W5.7 Static Completion Records | Pass
label | 0d224cf9-e29d-5c33-be5f-de83f9aa7ad0 |  | note | QUALITY CONTROL - T & W
text | 42288b33-9af7-5672-9f01-2ee72d0032d4 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | cb8c22ac-244a-582c-862e-624e5f00d258 |  | date | DATE:
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 10 - HYDROSTATIC SPRINKLER PIPE TEST
label | 2dd1c5b6-dec5-5f07-a110-e43b777221f6 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 Appendix H & Section 7.9.3
label | ec9f034a-c519-5cc2-92d6-98f8a3b0f0f0 |  | note | ○ All new installations, trunk mains and water supply connections shall be capable of withstanding for a period of 2 h, without loss of pressure, a hydrostatic test pressure of 1600 kPa.
label | 2475467b-7e15-5b31-82b9-d8aca7ad14f5 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | f3325c52-c7f6-5f1e-9756-1ea24abaee11 |  | radio | Hold Point Required: | Yes
radio | fff7b0f5-7052-5da0-a6eb-607fc94eed32 |  | radio | W5.7 Static Completion Records | Pass
label | 0c5dfc69-a0ff-5a81-b8fa-b39e9974d870 |  | note | As per GM Fire ITPS-013 Sprinkler Pipe Testing.
label | a16d5d65-89c1-556c-8757-9cd339a0e8a4 |  | note | QUALITY CONTROL - I & T
text | 97271bdb-f70c-512c-8c70-20e8d003952f |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 28a45c1f-c743-5fdb-b595-4886933595d8 |  | date | DATE:
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 11 - COMPLETE FORM 71 SPRINKLERS
label | f98f5d7b-1370-5ed8-8651-6483d4fb0c37 |  | note | ACCEPTANCE CRITERIA SPECIFIED - NCC 2019, AS2118
label | e974ea82-7882-5d5b-9743-6884ebd0c311 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | a3a42ab2-ab28-55a8-a10a-17f135f2e47c |  | radio | W7.10 Commissioning Certification | Pass
label | 9a03af83-6531-5e8f-b556-9b6a366eb050 |  | note | QUALITY CONTROL - C
text | 529db5fe-e667-57c7-b809-5a0fb2629432 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 7361a3dc-9af6-5611-9ef4-a33daffc081a |  | date | DATE:
checkpoint-status |  |  | checkpoint | 12 - COMPLETE FORM 71 HYDRANTS
label | 27c864bd-c82a-56b5-9c95-d305c8f6adbf |  | note | ACCEPTANCE CRITERIA SPECIFIED - NCC 2019, AS2419
label | 4f1f0188-1328-5889-b108-c2dde975bdf1 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | cf940cc5-9f4b-558c-a0af-bf336e047388 |  | radio | W7.10 Commissioning Certification | Pass
label | 466f3cf3-4adf-518a-96d2-d768ff902198 |  | note | QUALITY CONTROL - C
text | 6085eca7-97d2-5e1a-9a6e-9ab787c2be4a |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 6b008284-fa83-5254-ad2e-564a406d2608 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 13 - OPERATORS MANUAL, INSTALLERS STATEMENT, AS- INSTALLED DRAWINGS, LOGBOOK AVAILABLE TO SPECIFICATION REQUIREMENTS
label | ea8cd0ac-afea-5158-816f-765bae8f6faa |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House QA
label | 9e5f4ba5-91d1-5554-91d0-7974b9b40c63 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | bf18258c-acd8-53de-af50-62183ee52ed8 |  | note | QUALITY CONTROL - C
text | 0073a765-a102-54ae-ab8e-30128cdc5210 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 02abb706-2294-5dba-b5f5-61bf3f20191c |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | 2e6654d9-30f5-5332-a522-2ddc2f3119f7 |  | button | Hold Point Required: | Yes,No,Other:
text | 34197039-a980-5728-9388-dad859c95cc7 |  | textbox | Other (if applicable):
text | 3a63e46b-2e4b-5dab-ac21-ee839909a6a5 |  | textbox | GM Sign Off - Name:
text | 58d38a38-fd4f-5608-bf3f-fd14e851570b |  | textbox | PC Sign Off - Name:
text | b2d719f5-1acc-56af-8781-46fc19d7bdd4 |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | GM-ITPS-003 Purchasing and Procurement | itp |  |  |  | Yes | GM-ITPS-003 Purchasing and Procurement | 9018ebca-5aa0-4d14-8b21-a34c7e4bffa3
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - EQUIPMENT PURCHASES TO SPECIFICATION
label | 52e317dc-acfe-53cb-b5ff-dcce0cb82ab5 |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House QA Samples approved by PC/ CL
label | ff636b60-5e1e-5bb4-8377-24cca35d1d1d |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 8d7ae4b7-35d0-51aa-a2fd-654ba00741b5 |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | 14c6698e-69ea-5571-a7ec-c659d9ec0f63 |  | note | QUALITY CONTROL - I
text | 0619487f-d616-5b4e-bdaf-9d1ac9ed28a0 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 085265d2-4adb-5f6d-a9fd-e182fcd9a745 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - CHECK SPECIFICATION SAMPLES HAVE BEEN APPROVED.
label | 98b76aa6-b960-5bcb-8863-30b4d15dd7c5 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Approval by PC/ CL
label | 0d92b17c-54bc-5b33-b82f-65fed5cd14dc |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | e3edf0ba-b5b7-5849-901e-c2f40dc73b79 |  | note | QUALITY CONTROL - I
text | b69d9ff6-4263-5300-b955-f537a0ce6ff1 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | b2e39a3a-d003-5489-a2d8-635bb5922051 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - MATERIALS APPROVED FOR INSTALLATION
label | 59623fb9-8f22-58de-8ef8-151c6101cca3 |  | note | ACCEPTANCE CRITERIA SPECIFIED - CL Specification
label | b2f7f928-e5f1-53f8-9f2c-bd0d0651b461 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | cd6aa7f0-af60-5ed3-9fd1-c6af85ff6ab5 |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | d38b6e2c-5d9a-57c3-b124-fa98b2eef83b |  | note | QUALITY CONTROL - I
text | 523e89c1-6f97-5cfd-94e5-d441657322e6 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f21bb6e6-63e7-50c5-b1d7-7b44f8d07588 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - PURCHASE ORDERS SPECIFIC AND PRICED
label | 4de3a39c-db61-5ee2-9ad2-706daf2bb7d8 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Orders from approved suppliers
label | 0cf7418d-e188-54a5-938b-53f2178021ef |  | note | ○ In House QA – Equipment ordered > Equipment Supplied
label | f63764e6-8253-5d10-9244-5b48f88c4e10 |  | note | ○ POs referenced and invoices approved
label | 300c6fdc-2a3f-58ba-a79b-04610267dc78 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 477acd74-a82b-5178-9837-1d62940b5cce |  | textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | 8909fd4e-277b-53cf-a4e7-0bf819678d01 |  | note | QUALITY CONTROL - I
text | d3faebe4-ce52-57f8-a36d-267d050a5b7f |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 4cc540a8-2d89-5c36-ab18-027eceacbb94 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - FIRE PANEL DELIVERED – AS ORDERED
label | 72ec77af-9e60-5626-b754-e5a782fba35b |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House QA Reference Design Invoice from Supplier
label | e60e96ef-2317-52fd-823c-7742bab53edb |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | a2008b50-d344-5c1f-850c-97123132f7bd |  | note | QUALITY CONTROL - I
text | 80b1c661-cf13-5029-8357-a20744774f3a |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 3adea04f-9c96-5d4d-a585-b9031da1e6a9 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - FIRE PANEL Q.A. CERTIFIED
label | 3dc36bc6-a565-5b84-9cbe-55d25d1b47ad |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House QA To system Design requirements Supplier QA referenced
label | e0c471a5-5e16-5150-86e3-14d44f195b70 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | e41e66cb-21c6-5fed-8a0d-b2af106cb38f |  | note | QUALITY CONTROL - C
text | b4b5f900-70f0-57a9-b718-20958ac7c2ef |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 1bb1bc3d-42c1-563c-96aa-91407e59282f |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - SMOKE DETECTORS DELIVERED AS ORDERED
label | 58ecf203-c676-5391-b365-6aa2229a87d5 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Samples approved by PC/ CL.
label | efef8879-2f98-514d-a69a-ed264ee98b94 |  | note | ○ Quantities as required.
label | 3676728d-3eee-5fe6-bd53-c59c939c9eab |  | note | ○ Invoices checked.
label | 9b67a54f-b6af-57e6-955b-b45cedb9b95c |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 855e725a-d1e1-546e-9d55-1910dbb15070 |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | 467d9e31-741a-536d-a78f-054cb32a804e |  | note | QUALITY CONTROL - I
text | 37c44354-b5ea-5316-af56-80aebcdc2f0c |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f260f837-8e52-5e3f-ab48-5346bc16f2a2 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 8 - FABRICATED PIPE & VALVES DELIVERED AS ORDERED
label | 89c1be84-40d4-5a08-aee2-36be781cc57b |  | note | ACCEPTANCE CRITERIA SPECIFIED - SPRINKLERS: AS2118.1-2017 – Section 7.1; All pipes, valves and fittings shall be supplied new
label | 8ca65cb8-5b60-53bd-a1ca-9298f975e2ba |  | note | ○ HYDRANTS: AS2419.2-2005 – Section 8.1.1; Pipe, valve and fittings provided shall be new and comply with fitting specification.
label | 71b64f46-d46e-5450-b19b-70a09923aab3 |  | note | ○ In House QA
label | b8cce145-7971-52c4-b452-768b40484eed |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 41236956-4633-599d-abc2-92a04a99687d |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | d1d4c99a-f565-5565-8735-3ee7e0cfefb6 |  | note | QUALITY CONTROL - I
text | 745c2d10-bbbd-5323-a4c7-a10ae5311d15 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | da3225d5-bb82-5cce-bdef-f1fce7978258 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 9 - SPRINKLER HEADS DELIVERED AS ORDERED
label | d3035241-130a-580f-b976-6399dc0eda07 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 9 & 10; Shall be new and meet the demands of the system they are installed on (Light/Ordinary Hazard)
label | 27ac99c6-3c4b-5009-b612-0d32c2a9f602 |  | note | ○ In House QA
label | 6bd23e47-2583-5bdd-b3f7-ab0f93f2a516 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 6390ecf3-ffc2-5171-bcdf-60181be23dfd |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | 4c6f81a1-7b61-5c35-8a39-f8f6e3337aef |  | note | QUALITY CONTROL - I
text | a4b6ad4b-b695-5f14-a729-e72865c488f9 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 7b72c42d-3bad-5a88-9bf7-9d7124190d41 |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | f8649dbb-9ddf-5f8e-a5a6-cb0ca09d5271 |  | button | Hold Point Required: | Yes,No,Other:
text | 21d06884-a548-58dc-8330-5dd514f30d2d |  | textbox | Other (if applicable):
text | 174f798e-9536-5851-8f59-e51069db2ba6 |  | textbox | GM Sign Off - Name:
text | 4c51b95f-6468-5185-a909-d77a5366a20b |  | textbox | PC Sign Off - Name:
text | a215ed8f-7daa-5f08-b415-5122eab50685 |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-flat |  |  | checklist | 010SAF_08 SWMS |  |  |  |  | Yes | 010SAF_08 SWMS | 9eca8bf4-9616-427d-bf93-0c156542c6f1
checkpoint-status |  |  | checkpoint | ALL STAFF - Please, read, sign and confirm. (NEW LINE IF POSSIBLE) 1. I confirm I have completed the Principle Contractor's Induction. Attach Signature.
holdpoint |  |  | signoff | By signing I confirm I have completed the Principal Contractors induction.
checkpoint-status |  |  | checkpoint | 2. SWMS - ALL STAFF
label | cbaa5304-d926-5145-abea-643403fc7075 |  | note | 003G Using Platform Ladders
label | 4c0dcfe7-d8a0-5008-bd8b-d7bc54f1ac2a |  | note | 004G Inhalation of Respirable Crystalline Silica
label | 1117a6d0-9a4c-5b98-b403-d22a7b5ad3a6 |  | note | 005G Working at Heights
label | 68979298-f5d8-548e-baec-8741d208ed87 |  | note | 006G Working at Heights Rescue Plan
holdpoint |  |  | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed below. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
checkpoint-status |  |  | checkpoint | All referenced SWMS attached by GM Fire Admin. All staff to attach Signatures.
checkpoint-status |  |  | checkpoint | 3. SWMS - WET FIRE TECHNICIANS
boolean | 5d11d398-a985-5a6c-aeb6-18ee293dc7c2 |  | tickbox | I confirm I have read, understoof and signed the Onsite SWMS
boolean | 92d6eeb4-8277-5022-83a0-fc89644f8bed |  | tickbox | I confirm I have reviewed and understood all SWMS listed below
label | 52103321-2daf-5ff5-83c8-2ade86fd2490 |  | note | 019T Pressure Testing of Pipework
label | 8205c84e-07ea-575b-bae8-d3015acb0b02 |  | note | 020T Sprinkler System and Associated Pump Test
label | 884a1c0d-249f-5a69-b8f2-2e03f9760652 |  | note | 021T Hydrostatic and Flow Testing of Pipework
label | 61c0ba51-1491-512b-936c-ac2c0f143740 |  | note | 022T Fire Rating
label | c29e79e2-249c-55ba-b869-187073053c35 |  | note | 023T Fire Alarm and Emergency Warning Systems Testing
label | 6698f16f-e52b-551a-8c01-50f33d7455e7 |  | note | 024T Commissioning and Testing of Hydrant System and Booster Area
checkpoint-status |  |  | checkpoint | All referenced SWMS attached by GM Fire Admin. All staff to attach Signatures.
checkpoint-status |  |  | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
boolean | 01119540-9e32-5363-a076-b218fe3e7cdc |  | tickbox | I confirm I have read, understoof and signed the Onsite SWMS
boolean | 906f693e-7e97-5101-a63a-1d589f6e82ce |  | tickbox | I confirm I have reviewed and understood all SWMS listed below
label | 1164fbef-f485-5ce8-9972-88d749ab96b5 |  | note | 008I Removal of Existing Fire Alarm Systems and Devices
label | dd08eba1-2c52-50e2-91e2-93442f4b25e9 |  | note | 009I Removal of Pipework Fittings
label | a5e06fbc-5171-519b-b09b-50941b72c120 |  | note | 010I Fire Alarm and Warning System Rough-in
label | 69cf7cd3-322a-5c3c-8e71-69cb9feb1b1b |  | note | 011I Fire Alarm and Warning System Fit-off and Installation
label | 31f2416b-3e29-584c-84f2-aac83d136227 |  | note | 012I Installation of Fire Alarm and Warning System Cabling
label | f59e62dc-4c79-5dd4-8f89-6a85e583c959 |  | note | 013I Installation of Pipework and Fittings
label | 97e1da5e-c97d-5245-8282-6f9e89a4a086 |  | note | 014I Installation of Fire Control Panel & Emergency Warning Systems
checklist-sectioned |  |  | checklist | GM-ITPS-005 Fire Alarm and EWIS Commissioning | itp |  |  |  | Yes | GM-ITPS-005 Fire Alarm and EWIS Commissioning | a009c352-01ad-434a-aeba-5b6ec7e0ed6c
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - CONDUCT 100% TESTING OF ZONING
label | f4ce93ca-3dc9-56d0-96cb-5b2a9e2f0c71 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCIE
label | 35055917-6e33-50bd-a2a5-43974ea80e49 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 6d9aac08-0a89-5fbc-9d7b-358bd51d63fc |  | radio | GMF-COMDRY-001 - Fire Detection Zone Commissioning | Pass
radio | c3596fe6-a573-5c62-ad2c-ac3911b0d6e7 |  | radio | C5.2.6 Sequencing | Pass
radio | 616a38f8-76bb-5beb-8c17-d94775342937 |  | radio | C5.2.9 Alarm Functions | Pass
text | 901b9857-05e6-5040-bd92-5a2001129c02 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 13ac2db3-8f3d-5e8b-a215-a59a3b952a3b |  | note | QUALITY CONTROL - T
text | 37248ba4-7693-5957-ae38-46aa3fc41c05 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 99d7d578-7989-51c2-82f5-d138d4d80f1a |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - CONDUCT 100% TESTING OF SMOKE AND THERMALS
label | 016bbf05-4fdd-5f53-9a41-15487e2aa214 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Aspirating detectors measure and record the transport time (TT) from the most disadvantaged sampling point for each sampling pipe or branch.
label | bb592676-b976-5a92-b899-94f706744791 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 76931d4f-8f9d-5928-a1ed-1bcbede78602 |  | radio | GMF-COMDRY-002 - Fire Detection and Alarms (Smokes, Thermals, Duct Probes) | Pass
radio | 6b6db891-a1e9-5014-be32-50fc890ee34a |  | radio | C5.6.0 Sensors/Detectors | Pass
text | 9ca5a91d-d205-5369-a765-fbafba6e87a7 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 62df0eab-2d97-510c-897b-12be0c5f1f47 |  | note | QUALITY CONTROL - T
text | fdc020f3-e943-5bb9-83a4-2e4df567dfbd |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 1c7e86a7-61fd-5913-a111-1c3e37699bae |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - CONDUCT 100% TESTING OF MCPS
label | 1b74aee2-d3ce-50a0-af7d-3aad9eae7960 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018:
label | e788e5b0-4f6e-5498-a263-dde49d4d911f |  | note | (i) the correct operation of each manual call point;
label | c2d12493-5eea-5882-ad71-001661962030 |  | note | (ii) that the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and
label | ed200096-e491-54aa-8b11-1e3c8626cfbb |  | note | (iii) that manual call points are not subjected to alarm dependency.
label | 94201f50-f6e9-50ac-8d8b-63add01c8cd9 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | d813cc22-f6f8-5b65-8be2-2daabcb8ee3d |  | radio | GMF-COMDRY-003 - Manual Call Points | Pass
radio | 3e59dd42-3a92-560d-95a1-f25097d3612e |  | radio | C5.10.0 Manual Call Points | Pass
text | 141ad488-27fe-5c7d-a26e-6c070295409a |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | f4f79c38-fc69-591d-9d98-68e4accd8241 |  | note | QUALITY CONTROL - T
text | 883d6285-6f2e-5e1f-aaaa-31af7c056336 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 1a5c1bd5-4bb4-583f-b53b-d215c43e7486 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - CONDUCT 100% TESTING OF DOOR DEVICES
label | c56c4937-dcfe-5159-bdef-a3849fdb9eff |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Check the operation of each device/door release once installed
label | 06ed8982-7913-50ba-83c2-791b929f2139 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | fdd126ba-8a92-5f53-990b-3dd3c3d0225b |  | radio | GMF-COMDRY-004 - M.D.H / Auto Door Commissioning | Pass
radio | d7e8aa1e-af2b-51d9-ac64-57d9e96c572e |  | radio | C5.8.0 Modules Input/Output | Pass
text | 40ffb3d5-7288-5b7e-97e0-2de078c19742 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 2b272b60-9c31-5528-890b-2b95ab336c14 |  | note | QUALITY CONTROL - T
text | caa43783-e594-52d7-9a22-b3edee567c7a |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 72c7d176-fdb6-50fd-aef2-022d047cab4a |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - CONDUCT 100% TESTING CASCADE AND EWIS ZONING
label | f01582d2-47da-5b7d-8420-c48800b8eaf0 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018: Audible signals, visual and tactile signals to be checked – automatic operation.
label | 315af1b6-7f50-5513-85d5-3234292e2179 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 1a222f69-a717-57ee-b335-761ce4857f28 |  | radio | GMF-COMDRY-005 - Emergency Warning Cascade and Matrix | Pass
radio | 609ec260-e41d-52e3-816d-4ef8f58e0934 |  | radio | C6.2.5 Cascade Sequence | Pass
label | efa87ab9-24b6-5644-92ba-ed70ab8fa36a |  | note | QUALITY CONTROL - T
text | 27e7ff39-193c-58ec-b7e5-131242d88b7d |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | ff085a0a-de2c-5117-9707-df48904a6215 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - CONDUCT 100% TESTING SPEAKERS AND ZONES
label | 5b507ed3-9458-56bb-b562-9beb81aae434 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCIE
label | 099c7985-4b57-59f0-9060-80a70498f732 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | b040b0a0-ad6d-5af4-ba5b-53484506140f |  | radio | C5.6.0 Sensors/Detectors | Pass
radio | 9475749c-3a9f-544e-87be-d4f2e07f6b10 |  | radio | GMF-COMDRY-006 - Emergency Warning Commissioning | Pass
text | 5c5e3529-50f7-51c3-a844-e6e9cad39aa0 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 044ccafa-9ba8-5e37-a0cc-1afa7b765dae |  | note | QUALITY CONTROL - T
text | 07c93774-5c54-51b1-bd96-3584c3574cf5 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 285c96db-80b9-5f1b-9087-afcb6829811a |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - CONDUCT 100% TESTING WARDEN INTERCOM PHONES
label | 0ca07023-a682-52e4-86d1-28972d9a505a |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018: The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP. The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
label | e4c53dec-30bc-5e65-921d-b39f42d0de77 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | b857021b-a14c-523b-8d8a-30cbe6b521c6 |  | radio | C6.2.8 Warden Intercom Phones | Pass
radio | 7dcf2967-2616-5965-8ece-d1e1bf9c465b |  | radio | GMF-COMDRY-007 - Warden Intercom Point | Pass
text | e84a98a6-3916-580f-9a70-547161306137 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 350c07cc-6d5c-51a8-8e1e-8853eb502366 |  | note | QUALITY CONTROL - T
text | 67543692-3e19-5c3e-a28f-511fa5847e01 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 533b408c-919e-5456-934c-84097f340ab9 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 8 - CONDUCT FIRE MATRIX TESTING
label | 466ebb58-7993-5ad1-9c39-f5f181970bda |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix
label | 7789a253-963f-5fa5-8782-106b9b5f584b |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | d1bc0c62-206f-59a4-84b0-1cec6e39beca |  | radio | C5.2.2 Set Points | Pass
radio | de63c73b-37aa-503a-967e-f5632f5d613b |  | radio | GMF-COMDRY-005 - Emergency Warning Cascade and Matrix | Pass
text | f6b918ac-cc4d-520f-b12c-c12656946b9b |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 95e62a5b-b514-560b-9169-edf565aa26e2 |  | note | QUALITY CONTROL - T
text | 1b53498a-7e59-5836-b651-8bdfa8a00385 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 2d5eb416-a778-5277-b53a-c6967e716f12 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 9 - CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING
label | 07e786f3-1f0c-51d7-aca3-f230fb9dec8e |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: The FFCP shall be incorporated into or located adjacent to the FBP and constructed in accordance with the FDCIE requirements in Clause 2.1
label | aea9ceab-9dcc-5e3a-b04f-6ed7d1023475 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 487b0365-a5c9-50a0-97a8-7913dae8fa36 |  | radio | C6.6.0 Brigade Interface – FFCP | Pass
radio | d7213309-0a8a-57f1-ba01-f8c4a4b013f1 |  | radio | GMF-COMDRY-001 Fire Detection Zone Commissioning | Pass
text | e4ad2ce3-d6ad-54e1-9b36-4f3c3ced8aab |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | f2a205a7-627d-542a-8af7-3cf26b497f73 |  | note | QUALITY CONTROL - T
text | 9fdeb4ef-0516-5fbc-80fe-28b8464a4ff1 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | c528a041-c356-56f7-9b71-4f2893a3c8a9 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 11 - CONDUCT FULL FUCNTIONAL FIRE TESTING AND WITNESSING
label | 5b064c69-5f05-5c24-9bbe-ae18b1f6e8f7 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018 – 100% test of installed devices, Interface testing to Trades:
label | 4206ec70-eb82-5d1d-a495-48b0d6de6cdd |  | note | ○ Mech Shutdowns
label | 03a5b677-8780-5eec-9b44-e22099475c3b |  | note | ○ Security trips
label | 88306b59-f876-519d-96ed-a55defa7d2b0 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 00f0b490-ab6d-5c0b-9f71-5080a3e9c2d9 |  | radio | C7.0.0 Full Function Fire Test – Witnessing | Pass
text | f245b882-beaf-50fd-9abf-0a3851944dc9 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | e3850a54-ba67-547f-a5f1-01bdf2667c58 |  | note | QUALITY CONTROL - T/W
text | 8cb0e9f5-6644-550c-8829-46a396c57482 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 88ff3207-5cb6-555f-940b-4296d3c51e98 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 12 - SPRINKLER INTERFACES FITTED OFF
label | 2913ebfb-cdab-5fa9-81a1-24d1c96b0ca2 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2015: Systems interface testing Prior to any interface testing check that all systems listed in the system interface schedule are complete and operable. This will involve checking that all systems interfaces to the FDAS
label | 95cacfd2-9d30-5f00-9ac6-0bbc96e37e60 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 79e85036-6528-5b47-b483-40c9644b4977 |  | radio | C5.2.2 Set Points | Pass
radio | dae8a991-24b6-59d9-be9f-0b4397f1cdc4 |  | radio | C5.8.0 Modules Input/Output | Pass
radio | 9dc6a2cb-d057-56d6-b810-787c6c6edfa6 |  | radio | GMF-COMWET-001 - Sprinkler Zone Commissioning | Pass
radio | f29f9da3-8a9f-54b4-a9e6-f3e952df24d2 |  | radio | GMF-COMWET-002 - Flow Switch, Valve, Pump and Tank Indication | Pass
text | 52c2280b-0baa-566d-b83a-0f2a62c47a3a |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | b0b7e113-3a0a-5109-b2a9-9f66b7bf6c94 |  | note | QUALITY CONTROL - T
text | 763cbfdb-ebe2-558c-baa5-687c3324d78a |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | c36644b3-2366-5f8f-8062-21b72697e06e |  | date | DATE:
checkpoint-status |  |  | checkpoint | 13 - OPERATORS MANUAL, INSTALLERS STATEMENTS, AS- INSTALLED DRAWINGS, LOGBOOK AVAILABLE TO SPECIFICATION REQUIREMENTS
label | 0228834c-b138-5492-8744-58ecebff19d7 |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House QA
label | 43a841b0-80ae-5df2-a4d7-21080e5fd657 |  | note | ○ Correct documentation
label | 827fc417-1d9c-583c-becd-448931359ca3 |  | note | ○ Referenced and submitted to PC
text | 1cd15bc7-8fd8-53df-86a8-a3163abf4b4e |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 24bd0a50-6dc8-54b8-820b-067cddf414b7 |  | note | QUALITY CONTROL - T
text | d87212f0-9b28-5e9a-bc81-1738fd6b99d4 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 216295f1-b796-5186-b42b-f05814f71310 |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | 38066b36-4fe2-5bca-b0bd-1b2495a2def2 |  | button | Hold Point Required: | Yes,No,Other:
text | 4ebdae1d-a8a9-56c6-8559-c4618a0d6de1 |  | textbox | Other (if applicable):
text | 52923515-66a0-5e13-9e0c-2d910801dc28 |  | textbox | GM Sign Off - Name:
text | ae8c5576-e5cb-5897-8514-f05e36d723bb |  | textbox | PC Sign Off - Name:
text | 5c84b622-a162-5236-8ebc-bd769a037a79 |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | GM-ITPS-010 Fire Sprinkler Installation | itp |  |  |  | Yes | GM-ITPS-010 Fire Sprinkler Installation | b8965e64-4bc2-4a17-a206-75a9f7f319ab
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - PIPING, DRAWING & CUTTING SHEETS CROSS CHECKED
label | 71465694-263a-53f5-b834-16a515a0bef8 |  | note | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE
label | 15a2b43f-6f11-595e-801c-02d07bc34b83 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | a7f8ba8e-97d6-5e01-ab72-4311823961bd |  | textbox | DRAWING REFERENCE NUMBER - Cut Sheet Drawing Number:
label | 3ac70356-8c7d-55cf-abbd-362e49a9ed35 |  | note | QUALITY CONTROL - I
text | 8b729f7a-d83d-5849-91db-997c03d50ac6 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | cf8c7c59-8733-50b9-86e5-51b6372334db |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - UNDERGROUND PIPING TO PUMP HOUSE FROM BOOSTER TO APPROVED LAYOUT & DETAIL
label | 846dcde4-6866-52e6-99bf-c4d50b225910 |  | note | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE QA
label | 2e78232a-d3c8-59be-989b-956abce9f0f1 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | f2a4300d-d6f3-5028-9446-824471928f8b |  | note | DRAWING REFERENCE NUMBER - By others.
label | e38f42e3-a8b7-5718-82cd-c8b0fa9a6c00 |  | note | QUALITY CONTROL - I
text | 04057f80-05c0-5c6b-948a-028ba1f5bb51 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f88cce42-3aae-58af-9582-fd7a2abd7594 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - PIPING & SIZE TO DESIGN CRITERIA
label | f691ead5-947e-5ffe-b7e1-a15f93e6e1ba |  | note | ACCEPTANCE CRITERIA SPECIFIED - SPRINKLERS: AS2118.1-2017 – Section 7.1; All pipes shall be supplied new and conform to the standards and relevant requirements.
label | 19eb9836-b57e-5260-a063-02e6adbd4423 |  | note | ○ Latest Design Drawings
label | ff429e7e-b406-54be-b897-4926a913e025 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 024bb0c3-e88b-5446-a8f9-ee82647aa8d2 |  | radio | W5.5 Pre – Commissioning | Pass
text | 630fe848-d76f-5a46-a12a-952c13509ec5 |  | textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | d3a7aedd-8ddb-50bc-beb1-5c4c1ab3542d |  | note | QUALITY CONTROL - I
text | 07b8bddc-5133-521d-a095-b4904746ebea |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | e3bb2836-2103-507b-a9ee-7b041be1fc9c |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - MANUFACTURED FITTINGS TO DESIGN DETAILS
label | 8c8db65b-190a-5c4c-b9c7-8950ead03036 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118-2017 – Section 7.1; All fittings shall be supplied new and conform to the standards and relevant requirements.
label | 1ee1916a-b6ad-5e25-baaa-79692a44face |  | note | QUALITY CONTROL - I
text | 7bbd934a-122a-5a9d-a221-cf08c17e5e2a |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | e69eb898-9d05-5979-afc2-f03d9d15be89 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - PIPEWORK SUPPORTED BY SEISMIC BRACING
label | a64dee6e-31a6-5528-b22b-aef6f948b50a |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
text | 39c64afe-8f62-59a7-b60f-e225aa9aa0b9 |  | textbox | DRAWING REFERENCE NUMBER - Seismic Design Drawings as supplied by Seismic Engineer.
label | 49f2f49d-66f5-560e-9a64-c539370f6527 |  | note | ○ Construction Issued Drawings Number:
label | ef8a65ed-9fd7-5105-9db2-a21571e6a253 |  | note | QUALITY CONTROL - A & I
text | c83b5de2-8ad0-5ae8-a045-bd0332a014c9 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | b81b8158-7371-5d18-8666-bfd061258ece |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - PIPING FIXED TO SPECIFIED REQUIREMENTS
label | 7c7d1b7f-5523-54e8-a89f-d7b910da0984 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Section 7.8; Sprinkler supports shall be of the correct type installed in the correct locations and meet required load ratings for the pipe they are supporting.
label | fa9ef15e-2539-5eab-b7b7-02b9e9a6ee2d |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 1c98cd36-1c3b-5b5a-84da-d89f8ad58f2b |  | radio | W5.5 Pre – Commissioning | Pass
radio | c3e2dd59-938b-541b-8802-81c7bea0312a |  | radio | W5.6 System Checks | Pass
text | 916bf14b-205c-56e0-b7e3-efdcf809f21d |  | textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | 85fd5f6a-3ec9-5b50-aaf7-2ce0b1fb0bbd |  | note | QUALITY CONTROL - I
text | 802a935f-05e9-54b1-b41c-3f67d4f0e5e2 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 942cc24c-f8fc-5011-a694-93cc026a77b6 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - VALVES TO DESIGN DETAILS
label | dc14d65f-e37a-572b-99b7-b60363af4036 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 8.2 – each installation shall have a main stop valve fitted, have clear identification and be shown on the Block plan.
label | 1b6c2e36-8b2b-542a-90d1-b5874dd02f45 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 440a8da0-85a6-5329-8c81-12d83b1f1f4d |  | radio | W5.5 Pre – Commissioning | Pass
radio | 5ec7e58e-4619-51b0-94e0-3e50b985e2b5 |  | radio | W5.6 System Checks | Pass
label | dccf2598-5d18-55e6-b2d0-973409af96a8 |  | note | DRAWING REFERENCE NUMBER - Construction Issued Drawings
label | 03f4ade1-850f-5b27-8cbf-57bbe97a1802 |  | note | QUALITY CONTROL - I
text | edb26e39-d030-5d2e-8366-d184245ae7f2 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 8e09596b-828e-548e-aa63-1f96a3b87c20 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 8 - SPRINKLER INTERFACES FITTED OFF
label | 712be1cd-daa5-5501-abc7-1dfd0b0da4a7 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Appendix H – check to ensure alarm interfaces are fit off and tested prior to sign off
label | 4020952f-119d-5061-8f19-b7a33feb5c0c |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 0c315dc4-bff4-5c3b-87f8-5b4d932ef763 |  | radio | W5.5 Pre – Commissioning | Pass
radio | d29e6e3d-6302-5702-8f89-aa5a2aa7bf3a |  | radio | W5.6 System Checks | Pass
label | 155f19db-accd-5cbf-8ecf-6a919583e171 |  | note | QUALITY CONTROL - I
text | 56f870ec-f896-5c69-b85c-5facb9a2aabd |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 69ec0a44-d43b-5fcb-b5a0-a20f4eb1f01d |  | date | DATE:
checkpoint-status |  |  | checkpoint | 9 - WITNESS DRY FIRE TESTING OF VALVE SETS AND MONITORING EQUIPMENT
label | 7e2b0ac0-735d-5c60-a8eb-8eec9cbb1f18 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018, AS2118.1-2017 – Appendix H6 – system tested in accordance to the standard prior to witness testing with client or QFES.
label | 5d621c6a-916a-52ff-afb8-22b408dc9e92 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | d014c727-9d75-56b3-88ad-a199c2a1413f |  | radio | W8.2.2 Witness Requirements | Pass
label | 4b72712e-c460-5489-9c30-7295ad60cea8 |  | note | QUALITY CONTROL - W & I
text | 80936da8-6f84-5534-9323-b38adab52aa0 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | b8507125-651c-5cc7-9c4f-b4d93da373ff |  | date | DATE:
checkpoint-status |  |  | checkpoint | 10 - SPRINKLER HEADS FITTED OFF
label | b2f8396c-6f13-5e55-9f17-8ba74c90fa44 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 5 Approved and up to date Reflected Ceiling Plan (RCP)
label | f872b209-ed5d-5d6c-b8aa-5f6e74b726a6 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | e3ec8212-29d5-5147-ba5d-8021c2c63db1 |  | radio | W5.6 System Checks | Pass
text | c595c89d-f834-5b85-9954-827176fdc0cb |  | textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings
label | 59fc581b-aafc-50c5-bcef-56f836f02e91 |  | note | QUALITY CONTROL - I
text | 71d6c1cc-d465-5a78-ac41-9218ec89c0e3 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 8a7ba3b0-9f3c-557f-a29a-7bafbac0e028 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 11 - OMISSION OF SPRINKLERS
label | f5851cca-dfb3-5f5a-9019-67042183ea53 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Fire Engineers Report (FER)
label | 4faab791-1ee4-5f67-b3f7-8f8c44110d40 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | b2ea29cd-a02e-5297-bfa5-ef142a94cfe1 |  | radio | W5.6 System Checks | Pass
text | 9e1c5466-6413-5d54-8086-24960a35109d |  | textbox | DRAWING REFERENCE NUMBER - Fire Engineering Report.
label | e9d479a2-e823-5683-b372-3be86e2edcb5 |  | note | QUALITY CONTROL - I
text | e1671474-6b3a-5782-8743-8b4f6080aa35 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | a5adb717-b03c-5d87-a112-b4198f6a33cb |  | date | DATE:
checkpoint-status |  |  | checkpoint | 12 - SPARE SPRINKLERS & KEY INSTALLED & TYPE CHECKED
label | 6a0728c0-61a5-50f7-89d1-c77969116aaf |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 6.7 – spare sprinklers of each type used in the installation shall be provided and located in a spares box.
label | b8030181-7605-5c34-aebd-75a85c28934c |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | f97bd35f-141b-5ab4-9e78-756f7162488e |  | radio | W5.6 System Checks | Pass
label | f57698e1-4fed-5c50-94b3-49b65bd77956 |  | note | QUALITY CONTROL - I
text | dc7cd86c-e789-51a2-a9ed-e68096489ead |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | c8d07ac2-3f48-55e1-8a51-dcf9051d2969 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 13a - LABELS & BLOCK PLAN INSTALLED
label | 0964ae79-e3ac-595b-bc0c-2360adb6f9b9 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 8.3 – Block plans shall be provided, be of permanent design, water and fade resistant
label | f0037aaf-85d2-515b-99dd-e9d6542aaca3 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | c82a9985-72e2-5793-8c22-a4787fb181e9 |  | note | QUALITY CONTROL - I
text | 4c260486-6aa7-58f6-a9c7-5c753618686b |  | textbox | PERFORMED AND/OR WITNESSED BY:
date | 063121a5-05bc-5e40-afc2-739cdaaca44d |  | date | DATE:
checkpoint-status |  |  | checkpoint | 13a - CONTROL ASSEMBLIES
label | d34adb1c-ed1e-55ee-9b27-95eed82296f7 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Section 8.1 – shall be located in a secure location and readily accessible to the fire brigade.
label | c48c86f0-73b0-5ca5-b683-b03f77e65c39 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 09553069-d1dc-5f59-b99d-6a9346fcf2b9 |  | radio | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
text | b90f5619-01cf-5035-a908-fbf92c9bee98 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | faa9f391-65b2-5b33-a1b9-5b37423312b5 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 13b - LABELING OF CONTROL EQUIPMENT
label | a7be95fe-82c3-52e0-a7a7-3208e6bd628b |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Section 3 (3.3.4) – shall be permanently affixed fade- resistant and water resistant
label | ed955e32-4111-54b5-9b46-233ad71d6046 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | 628c3601-201d-5e96-a503-6d096bb52ee4 |  | note | QUALITY CONTROL - I
text | c52dc809-01d7-5dd4-afe1-4124d04b6261 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | d1ac72e7-5810-5855-bc5d-74b0e9e5fdb8 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 14 - FIRE RATING TO PENETRATIONS CORRECT AND LABELS AFFIXED
label | acd0740e-ab8f-590f-aabd-a163f0ae3dfb |  | note | ACCEPTANCE CRITERIA SPECIFIED - BCA
label | ab8b1108-f9ce-53a7-be2e-b90f4d7c2012 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | 067f6bdb-4b68-54da-a590-34a53861e94a |  | note | QUALITY CONTROL - I
text | 3e6e42d7-7167-56d0-bbaa-974ec251c266 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f8246cf7-57c5-54fc-aa0d-0b3a29de7491 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 15 - ACOUSTIC PENETRATION SEALED
label | c2fc3432-9e89-5848-a831-02bdf528abd2 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS4072
label | d280eab5-0461-5fe8-8839-0ffe20afc66a |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | 7ef1cf00-6dac-5ae3-bda7-b56ddbe17545 |  | note | QUALITY CONTROL - I
text | 8a569626-5af1-5f4e-896d-74d139932348 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | bd25b1dd-f7cc-5304-8799-00fb1fd383c3 |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | bbcbb141-908b-52b5-a465-71ef63bc6c4a |  | button | Hold Point Required: | Yes,No,Other:
text | a06b36b1-009e-5f7e-8bf2-092de7546592 |  | textbox | Other (if applicable):
text | 5f92a269-706a-5215-a61e-9674e53093e3 |  | textbox | GM Sign Off - Name:
text | 90f602e7-7176-5940-b7f7-0203ff6eeba6 |  | textbox | PC Sign Off - Name:
text | a8122c50-ba6c-56be-9324-1509d45c876d |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-flat |  |  | checklist | GMF-020 - Daily Prestart |  |  |  |  | Yes | GMF-020 - Daily Prestart | beb07143-3243-4983-bf1f-2319e16d1748
checkpoint-status |  |  | checkpoint | Details:
date | c67a5ad6-470a-5e2f-997a-f5f60b5e37f6 |  | date | DATE:
text | be60c24b-9584-50b3-85e7-c97aac850d9f |  | textbox | TIME:
text | 5309490c-3518-5494-8898-6b41003721aa |  | textbox | SUPERVISOR NAME:
checkpoint-status |  |  | checkpoint | ISSUES ARISING FROM PREVIOUS DAY?
text | 29d3d625-f08c-54b1-bf3c-b22dfa3fbd75 |  | textbox | If YES, please state:
label | 88bc1641-daee-577f-b7e3-efc84c9a3236 |  | note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
checkpoint-status |  |  | checkpoint | PLANNED WORK ACTIVITIES / TASKS
text | 89e3b170-750e-51d8-a682-a426806358d3 |  | textbox | ACTIVITY / TASK |  | Write below specific daily work task
label | 63009163-b71f-5d74-88ab-182d0339fbec |  | note | SWMS NAME & NUMBER
boolean | 3217cd42-d7b4-5c06-8925-f508bd3b2eb4 |  | tickbox | 001 – Working with elevated work platforms
boolean | 4e6ff252-595a-527a-99b7-8b0d317de7fb |  | tickbox | 002 – Wiring Rough In Minor
boolean | cd7e73e3-d703-52b7-9d32-c59cb15791e0 |  | tickbox | 003 – Fit off fire alarm system
boolean | b8ad95df-8b35-52b0-9faa-5efb930c096d |  | tickbox | 006 – Installation of pipe and fittings
boolean | 2fc333ec-8649-5094-9bac-e7db22722260 |  | tickbox | 007 – Manual handling
boolean | 793477a1-ebab-528d-ac0f-4cf5e41a28fa |  | tickbox | 009 – Pressure testing of pipework
boolean | abf682f7-668c-584c-add3-69603f01ffe9 |  | tickbox | 051 – Using platform ladders
boolean | aab532fe-44ab-58ce-84b2-320c641c1eca |  | tickbox | 060 – Inhalation of Respirable Crystalline Silica
boolean | 55efd7fe-fc29-5217-af4c-3858f7a3124e |  | tickbox | 061 – Working in Major Area of Concern
boolean | 774a66c3-3fea-5200-a769-32e4e0d72e01 |  | tickbox | Task-specific Safe Work Procedure
checkpoint-status |  |  | checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
label | 018251a3-fdc4-5187-821b-085ee9060fc3 |  | note | IF NO, STOP AND DEVELOP!
checkpoint-status |  |  | checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
text | 95fe8c17-73e5-5a12-84ab-0e88db6ce7aa |  | textbox | If YES, please list
checkpoint-status |  |  | checkpoint | Permits in place for today’s Activities - Stating Permit No. and Description
button | ccbee4d0-b0fc-50f9-aba7-187627b00d3a |  | button | Isolation Permit | Yes, No
button | e9e5dd68-707a-5644-8f38-af984c59f3e6 |  | button | Have conditions changed since permit approval? | Yes, No
label | 498988e2-fa90-543d-abe2-62bbc0b59d3d |  | note | If YES, please state in section 11 notes.
button | 49f83c80-5eec-5445-acf1-c5c9e01af072 |  | button | Hot Works | Yes,No
button | 26129dde-acee-57f3-b54c-c083077e591c |  | button | Permit to cut or drill | Yes,No
button | 1d20b088-7c9c-5436-8f27-c1ecd33f79fd |  | button | MAC Permit | Yes,No
checkpoint-status |  |  | checkpoint | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust? List.
boolean | d043a4ae-8752-53fc-bcd7-920e72521388 |  | tickbox | Clean up the general area
boolean | be468b16-df19-537b-854e-46bbd3df7b89 |  | tickbox | M-Class vacuum
boolean | 03b3f67c-e939-50e1-8cb2-87e19dbe9fd7 |  | tickbox | Fit test and appropriate fit mask
boolean | 054df62a-5657-559a-8159-5ed36c7947b6 |  | tickbox | Spill kit onsite
checkpoint-status |  |  | checkpoint | Checklist for Activities (Select YES or NO)
label | f1e2b79e-aefd-53e7-bcd3-7868bdf06e49 |  | note | Complete activities or issues must be detailed in section 10 notes
button | 57c8c5eb-69d5-5928-bcc8-b3fe0690aa3a |  | button | Daily Risk Assessment Completed | Yes,No
button | d198e689-340f-595d-aa6c-5796b9e55eea |  | button | Qualifications/training of staff adequate for work activities | Yes,No
button | a89c730d-f0a5-5583-9141-f6861600debc |  | button | Plant and Equipment on/off site | Yes,No
button | c2abc099-5048-5862-be7e-69276e515d47 |  | button | Equipment safe to use | Yes,No
button | c35b1cc8-2353-5462-9376-b66fbffbe2eb |  | button | Work area inspected and safe for staff to enter and work in today | Yes,No
button | 446e2139-b3e3-5032-b3b7-4b2ecf6682f2 |  | button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
button | 1297b9fc-83fc-5f03-8c96-a7ef0df8cad5 |  | button | Weather conditions for work to be conducted assessed | Yes,No
button | 50775e4c-331c-5bcf-9d61-90de79b49eb6 |  | button | Indicate Number of workers allocated for today’s clean up? | Yes,No
button | 31b028e3-39b4-5b10-96c0-301d4210e7d4 |  | button | Pre-start communicated to all work teams including all trades & subcontractors listed in section 4 | Yes,No
text | 0ee11d88-49b3-5ce0-a39a-8acea8053a9f |  | textbox | Number of people in your Work Group
checkpoint-status |  |  | checkpoint | Builders Briefing Notes
label | 96ad1a92-eed7-5574-b446-3263c628aa29 |  | note | Attach a photo of the builders brief
checkpoint-status |  |  | checkpoint | General Notes
checkpoint-status |  |  | checkpoint | Signoff
label | ad0d0126-8a7e-5cc0-84b3-32f1ee14e2ef |  | note | Remember to clock in and out using the Connectteam Kiosk app
label | da9a5ff0-e485-5595-af87-441d7391c382 |  | note | ATTENDEES
text | dd3f218b-eb60-5b49-b3b1-bc928b3eafa8 |  | textbox | Print Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | GM-ITPS-008 Sprinkler and Hydrant Design | itp |  |  |  | Yes | GM-ITPS-008 Sprinkler and Hydrant Design | bf0589fc-713f-48fc-97f4-a8e6b036d376
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - REVIEW CLIENTS DRAWING REGISTER
label | 63d8da30-8599-5f07-8490-fbfb94b693d3 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 5435e5ac-041c-5277-b918-9081ba9e3c28 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 68d15c42-c7a9-57e1-8e34-2476e012ee93 |  | note | QUALITY CONTROL - I
text | c612f198-f0a1-5aa8-adeb-95b9cd1fe0ed |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 1e5f7dd3-fc92-5d7d-b62e-578634e0d2fb |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - REVIEW TENDER/CONSTRUCTION DRAWINGS
label | fe3f7d6b-5227-5d88-97ec-dc3d5a6818fb |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | 8ea3e282-6113-5cac-af8e-e2af9e19ee63 |  | note | QUALITY CONTROL - I
text | 9f373b84-d9c7-5244-907a-bb959e146bb5 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | ad0149c5-111d-5728-a4ae-9f9a7d894499 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - REVIEW SPECIFICATION
label | 2541ff51-bd39-585d-88de-15ade542e3ca |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | da3cc992-3260-5708-b4e4-06a34a09bdce |  | textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | e7522c72-f8c3-5b85-ba80-e27c7994a81b |  | note | QUALITY CONTROL - I
text | e5491d43-8ef1-578e-92b4-8eaf3e60b4d2 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 515c2cc2-ac45-5796-949e-721b791ad967 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - PREPARE SHOP DRAWINGS/LAYOUTS TO LATEST ARCHITECTURAL DRAWINGS
label | 7152f046-06b0-51e0-b7c8-3d02b2e996d1 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | fcc9de67-6e90-5136-b28b-8349bbb64d87 |  | note | QUALITY CONTROL - I
text | 1c6407e7-3d26-507a-ad33-08ae7964d1d3 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | d060f218-b814-5cac-875d-d367a105206a |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - DESIGNING PIPING LAYOUT
label | 39739c6e-d30e-554e-bead-442d136f4c5a |  | note | ACCEPTANCE CRITERIA SPECIFIED - SPRINKLERS: AS2118.1-2017 – Section 2; All new sprinkler systems shall be hydraulically designed in accordance with the requirements of Section 14 (hydraulic calculation of Sprinkler Systems)
label | 0ec156e9-2d4b-501b-b3ce-3c07fd436d1b |  | note | ○ HYDRANTS: AS2419.1-2005 – Section 2; Fire Hydrant systems shall be compatible with the equipment and procedures employed by the attending Fire Brigade
label | 60d93fbf-eefb-58a4-b740-9ff4078b4bc3 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | e6096a61-de28-58dc-9d41-0f789e342935 |  | note | QUALITY CONTROL - I
text | a870b07f-bbb1-5359-9934-ec9c2afcb5de |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 14fe8e1d-fe41-5310-ba3a-bca94d2ebb22 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - PREPARE SPRINKLER VALVE DRAWINGS
label | d1f418c2-4553-5d33-8215-e99cc454b043 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 8.2.3(b); All sprinkler stop valves shall be clearly labelled on this Sprinkler Block Plan
label | 1165b646-615d-5f54-8d54-0545fd1bf92b |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | d8528eeb-581a-5a98-8c18-dd820cf270d7 |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | 766858fd-ff1a-5d62-8101-68600efa49ab |  | note | QUALITY CONTROL - I
text | aac8df5d-76e1-5b71-ad4f-f90b14358921 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 61ac235e-9c78-5703-809c-e6a41c71560d |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - SUBMIT SHOP DRAWINGS FOR APPROVAL
label | 11ac9c5f-97db-56a6-94dd-1172273f2327 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Clients Specifications In House QA
label | e92087d3-865f-5ddd-992a-fdf3fdce499a |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 66229b8b-3679-5f0b-a3a1-926793b34c0f |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | 21eeb33e-ac89-56f9-99d1-594570bb1d5b |  | note | QUALITY CONTROL - I
text | b33f01c7-343b-5078-bbb1-2165bd57a3eb |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 8ae43f2f-0dfb-5b23-bdec-415518512949 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 8 - REVIEW RETURNED SHOP DRAWINGS
label | 990f8ee5-4679-586c-b4fe-10203e678823 |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House QA
label | ab24e20d-47e3-5854-81e4-8a2d46989ef0 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 3702eca1-97a4-5077-9a76-94c9f9e10830 |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | 1dafe5ad-4c90-56a8-8ba4-889730e7f051 |  | note | QUALITY CONTROL - I
text | 26ac68d6-788d-5648-9643-da59331b4fc6 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 4621bd8f-3e05-5a3c-8ee2-22a28c9e6cae |  | date | DATE:
checkpoint-status |  |  | checkpoint | 9 - DISTRIBUTE "FOR CONSTRUCTION" DRAWINGS
label | e421997a-7234-5b45-9d35-18b9cc8563c5 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Per clients Specification
label | 2751cc37-1e56-5776-903e-81f91f72aa4c |  | note | QUALITY CONTROL - G
text | 23aecc4d-e9a7-5206-9818-aef2b4055c10 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 317d56c8-82a5-5614-ae14-626e843dc08c |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | 85af548c-38b3-5a56-824e-49dc1001455c |  | button | Hold Point Required: | Yes,No,Other:
text | e8488e25-9f10-5b76-84bc-93dec28ffe5c |  | textbox | Other (if applicable):
text | 6b4af6b1-a531-5869-8855-c00e9b7977c2 |  | textbox | GM Sign Off - Name:
text | d4847cb3-ecbd-57be-a5df-6eba86449af2 |  | textbox | PC Sign Off - Name:
text | 2f5dcaff-7a0a-5789-8537-98c7f96abf76 |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | Site Establishment Checklist |  |  |  |  | Yes | Site Establishment Checklist | d08c98f1-cd66-42cd-8498-ee96b3e837f3
checkpoint-group |  |  | section | Details
checkpoint-no-status |  |  | checkpoint | Details:
text | a9f0eb07-3912-523a-be5f-a802d6ff641b |  | textbox | Project Number:
text | be704f51-8345-5d07-82ad-4691b8d46bd7 |  | textbox | Project Name:
text | 55438198-cfca-5417-84b8-414b08417475 |  | textbox | Project Manager (PM):
text | cecfc96f-5250-5907-bbf1-e0562cea155d |  | textbox | Project Address:
text | 71a86034-b956-5203-b873-8d6f798b33ad |  | textbox | QA Platforms used:
checkpoint-status |  |  | checkpoint | 1 - Specification review
label | 5a7e625c-1819-565b-b8ed-287d8663d3b4 |  | note | ACCEPTANCE CRITERIA: In house, FER & Specification Numbers
date | 62d9c92d-c1ab-5446-89b1-bf80cbc0d1a4 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - Site visit & survey
date | 9d598589-23f2-5739-abd1-38084d2be5a8 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - Project review (1)
label | dad37bbf-5281-5085-83f6-8f84a96552eb |  | note | ACCEPTANCE CRITERIA: Review Drawings & print for site
date | 767f52ec-aec3-5775-a064-7229f459323b |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - Project review (2)
label | c209cde7-35f5-53dc-ab3f-1bc167638729 |  | note | ACCEPTANCE CRITERIA: Review Fire Engineering Report
date | 0d7909f1-54e9-5c90-92e6-074eee42c7aa |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - Project review (3)
label | c9c59e99-5545-5c04-ba3e-7c3b676785f3 |  | note | ACCEPTANCE CRITERIA: Allocate labour
date | 0a895642-a262-5e46-a17d-2bd265707331 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - Site program review (1)
label | 50cb14e5-f6fc-5fee-9212-3c0afc632663 |  | note | ACCEPTANCE CRITERIA: Review Principle Contractors (PC) proposed baseline program
date | 1692f978-f249-5f30-958a-396ff70c258b |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - Site program review (2)
label | c92ff856-383c-57de-a824-9a4bb8b1aa63 |  | note | ACCEPTANCE CRITERIA: Create Fire Services Proposed Programme
date | 07f60850-c8ec-5c07-8cb3-4760f7a199c5 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - Site program review (3)
label | 163e7bc0-42b2-5210-a5e9-fffb25e55c5c |  | note | ACCEPTANCE CRITERIA: Upload to ALL necessary QA platforms
date | b5b18c80-8662-5430-9ca2-81c6feb62800 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - Site program review (4)
label | a2f23d1b-6df3-5c78-bf3e-5facaf41db06 |  | note | ACCEPTANCE CRITERIA: Save softcopy in GM Dropbox
date | c65d94ba-f3ef-5124-bde6-1efbcc2ca74a |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - Site safety plan/induction (1)
date | 2c4053b0-b92a-5f9f-9c5e-5d41d1181b30 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - Site safety plan/induction (2)
label | 0324e805-e610-5102-9c70-6e290f700260 |  | note | ACCEPTANCE CRITERIA: All employees have attended Induction
date | f2578d06-522d-52c8-91f5-609e406fe43b |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - Site safety plan/induction (3)
label | df349619-885b-5544-ae23-f2f3bfb90085 |  | note | ACCEPTANCE CRITERIA: GMFORM007 - Workplace Inspection Checklist has been updated/ completed and uploaded to ALL necessary QA platforms
date | 69485439-6b90-5c33-a8e0-8651bdee03cd |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - SWMS signed
label | 0f743682-f338-5f0a-90b3-ebcaa19ca99c |  | note | ACCEPTANCE CRITERIA: All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
date | ccf4434e-fcc7-5408-8a54-c9b9b3f5816e |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - Preparation of Daily Documents (1)
label | de69f797-72d6-5870-8c58-137707e732cf |  | note | ACCEPTANCE CRITERIA: GMFORM 019 - Tool Box Talks
date | f757b8a3-54cf-5981-b3f3-31dc4b82e49d |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - Preparation of Daily Documents (2)
label | 1d797b82-e92a-5311-a599-54f025af2983 |  | note | ACCEPTANCE CRITERIA: GMF020 - Daily Pre-Starts
date | 33147827-df18-5288-ad7e-bc9699a7d177 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 9 - Electrical tools Tagged & Tested
label | fd9ce00c-d05e-5fb4-ab7c-0274cc392135 |  | note | ACCEPTANCE CRITERIA: Completed Onsite
date | 09062a64-5747-5087-aa33-3054ec59cdf0 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 10 - Tools checked for wear & tear
label | 669d38cb-7536-5534-a124-c09cbb1306bb |  | note | ACCEPTANCE CRITERIA: Completed Onsite
date | bb31431c-68ab-56dc-aef6-7c753705ef21 |  | date | DATE:
checkpoint-status |  |  | checkpoint | PM Signature:
date | 1ec883e5-6967-525b-ae22-80125604b1fd |  | date | DATE:
holdpoint |  |  | signoff | PM Signature
checklist-sectioned |  |  | checklist | GM-ITPS-012 Fire Brigade Inspection Sprinklers and Hydrants | itp |  |  |  | Yes | GM-ITPS-012 Fire Brigade Inspection Sprinklers and Hydrants | d9cef835-6d8b-4c53-8038-d799bf7a1132
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - CHECK SPRINKLER HEADS ARE INSTALLED IN AN ENVIRONMENT IN WHICH THEY ARE SUITED
label | 2f017b45-68bb-5182-a6b1-bf7d1bc48992 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 2.2 – heads installed to correct classification and spacing
label | c99bdc92-526a-5d3c-998b-92639bf9e306 |  | note | QUALITY CONTROL - I
text | a969ff56-5663-5391-b0b7-a5f77bec8833 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 2356c08e-7faa-5b72-98a9-cb459ed5f91b |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - CHECK HYDRANTS ARE INSTALLED TO CODE AND HAVE REQUIRED CLEARENCES
label | 5897017f-f53e-5039-885b-86ec2059c7b7 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2419.1-2005 – Section 3.2 – Clearances differ when related to internal or external hydrants, ensure correct standards are implemented
label | 4317a96d-950a-51e1-98e9-bc5c50a2c8b0 |  | note | QUALITY CONTROL - I
text | af67527d-5250-5a8f-ac10-67a270346b5b |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 1aaf4b76-64d3-5594-9725-6f681006c217 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - CHECK & TEST WATER SUPPLY CAPACITY TO MEET SYSTEM DEMAND
label | bb101329-c681-5714-b7a3-01b6891f24b2 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - section 4.2.2.1 – capable of supplying the flow and pressure requirements of the sprinkler system.
label | 89fc61b4-ee8e-5580-9f46-5f30f7db7dea |  | note | QUALITY CONTROL - I
text | ddc2b9a6-ef2b-5442-a870-5cfde0dc82d9 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | e1975c8a-6d32-5c85-a392-d62f56b28ebc |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - CHECK OPERATION OF PRESSURE SWITCHES TO DBS
label | 99bf5489-730c-52c7-af65-7ad83d793c80 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Appendix H4 – Test via 15mm test valve and record time taken to operate. Confirm with ASE monitoring service that alarm was received.
label | 51c0501c-d96c-505c-bac7-1cd8249dea42 |  | note | QUALITY CONTROL - I
text | 0362f8ed-af00-520e-9dc6-3a8f134bbe3d |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 6bd22fa7-3cfe-527c-a87a-770cdbb1cc00 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - CHECK OPERATION OF PRESSURE SWITCHES FOR PUMP START
label | 5c9dd13a-ce9d-5561-8331-9c89408b7da7 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Appendix H5.4 – P/Sw to be tested via dropping system pressure via test valve or remote test point.
label | a76b0ea3-d359-5cdb-8285-a9cc9e01a217 |  | note | QUALITY CONTROL - I
text | 55ae55ce-44c1-5c77-bd2d-edd2363b1f6e |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f41431e7-0c36-5a53-add6-d271200e529a |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | e1f67be9-e3bc-5c6a-8053-c640a06cd2ca |  | button | Hold Point Required: | Yes,No,Other:
text | 0653fdf2-50b0-5c1c-a840-ab58dd8cf7cb |  | textbox | Other (if applicable):
text | 5e0ef3ed-2931-5bfa-9df2-7431afd8d7bb |  | textbox | GM Sign Off - Name:
text | 70f51f8b-6d87-5c24-a877-331f9981195e |  | textbox | PC Sign Off - Name:
text | d38b432e-8f72-5a74-afb4-338c69e3ceb0 |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | GM-ITPS-013 Pressure Testing of Pipework |  |  |  |  | Yes | GM-ITPS-013 Pressure Testing of Pipework | e0303800-66ff-4e5d-a795-0d5656e545e2
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Test Information
text | d71ba73f-3ef4-5490-8f80-0e1c2940cc5a |  | textbox | Maximum System design pressure:
text | 3edc4f22-2542-5073-81fc-bca83f90c947 |  | textbox | Required test pressure:
label | aee9b2ae-f030-54f8-925c-28902f8b9c0a |  | note | STOP TEST IMMEDIATELY IF PRESSURE GAUGE REACHES 1650 kPa
radio | a848a8c0-db2f-51f7-8985-d4e207c5ca14 |  | radio | Hold Point Required: | Yes
text | a69494c2-c869-5635-8479-4e0511afdc91 |  | textbox | Holding time:
text | 30891645-af68-55ba-aa50-1cf9d93ad7a7 |  | textbox | Description of test configuration (attach sketch or piping and instrument diagram):
text | 10d849e9-532e-5f8b-9710-9966c441151c |  | textbox | Test fluid:
text | 064206d7-c128-503c-8a93-3fdff618c33d |  | textbox | Test Fluid Volume:
checkpoint-status |  |  | checkpoint | Test Equipment
text | fc7bedbe-7cd0-5857-bc00-6014f24a82bb |  | textbox | Pressure Gauge:
text | 0c9b2a52-2a47-52ef-b5f1-512d7e9792c0 |  | textbox | Pressure Relief Valve:
text | 1feaec21-e745-5767-9633-71db56bb09f2 |  | textbox | Bleed valve:
checkpoint-status |  |  | checkpoint | Safety/Environmental Controls
text | e6967557-0e79-5b07-a656-9e19aeb2cf9e |  | textbox | SWMS Name:
radio | 3036397a-547e-5ad2-a7ce-4cd47ff19ec5 |  | radio | Have all workers reviewed and signed off on SWMS prior to commencing work? | Yes,No (do not commence works)
text | c91f4c63-7d5f-5646-9786-26e60c9ce96e |  | textbox | Safe disposal of test fluid:
text | 292f874a-b16a-5747-b390-4b499094872c |  | textbox | Test area controls (barricades, signage, etc.):
text | 4b3043b0-f72b-5c05-8c59-f47bbe3d61cb |  | textbox | Inspection requirements (before, during, and after the test):
radio | 933bf8f2-70f4-50a5-aca1-e0f0fb5d638c |  | radio | Is test equipment rated for test pressure: | Yes,No (do not commence works)
radio | b9003231-56ea-575e-a6b5-ab3bf53545fa |  | radio | Are end caps sufficiently tightened: | Yes,No (do not commence works)
text | fa50cb29-514c-5df5-8f73-08f66566e6df |  | textbox | Pressure Gauge reading at completion of test:
text | ecbe351f-b857-5fbc-8dfb-49a02905dcb0 |  | textbox | Any visible water leaks?:
text | 697f50c7-9292-59cd-886e-a2e9b4bc464e |  | textbox | Test Date and Time Commenced:
text | 27f27fb1-78f7-5755-8227-04adfeb45758 |  | textbox | Test Date and Time Completed:
checkpoint-status |  |  | checkpoint | Approvals
text | 0d7b1e49-d1ca-5e35-af0c-9bbc254cdc90 |  | textbox | Supervisor in charge of test:
text | 6c2a2921-b001-5575-bec1-ec603a4c98ad |  | textbox | Person conducting test:
date | a641222e-81ba-5b9a-ba11-e4616f40c8e1 |  | date | Date:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | db9d36a3-2fec-50bc-8538-d8b7f281c812 |  | button | Hold Point Required: | Yes,No,Other:
text | 7e2ad56c-35ae-55fc-822d-3b4c4091a16f |  | textbox | Other (if applicable):
text | 8fb0ea7c-2b4f-5705-ae0f-fa1f69ed15e9 |  | textbox | GM Sign Off - Name:
text | 3930912f-465f-537b-8f9b-1369b82e235e |  | textbox | PC Sign Off - Name:
text | cef567d7-33b1-54f1-8bdd-06cecc6e53e3 |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | GM-ITPS-006 Fire Brigade Inspection | itp |  |  |  | Yes | GM-ITPS-006 Fire Brigade Inspection | e2c7bf9e-b3fd-4b3f-9bce-088efa152317
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - FIRE INDICATOR PANEL LOCATION ACCEPTABLE
label | 8afb1027-9c1e-5f27-bdf6-56d703d1de51 |  | note | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018 Section 3.9 – FDCIE to be installed with .5m clearance either side of panel and 1.0m clearance in front of Panel.
label | 837fc45b-bc52-5d9f-b45b-afbb7dfe0adb |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 425f413d-b2a2-5648-ac41-cbffcca5ccef |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | bcefb302-fc6f-5ebd-b940-2ac0d2449f45 |  | note | QUALITY CONTROL - I
text | 3d7241e0-ade8-52b2-bf4e-11c725ea3e5e |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 2e48ca8a-5043-559f-a524-68f70ef255b1 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - HEAT DETECTORS TESTED
label | 219f3d42-4622-54b4-a2f1-700af6db03b2 |  | note | ACCEPTANCE CRITERIA SPECIFIED - 100% Test of installed devices.
label | 76df5905-5f15-5e08-ab33-a6b6b9ad4144 |  | note | ○ Correct location and spacings
label | 7f51ad25-c2af-525c-a5f0-9dbc1a57f1ea |  | note | ○ Correct zoning and description at FDCIE
label | 819abd50-7aec-524d-9dd8-2695eeaaa2af |  | note | ○ Correct interfaces triggered
label | dd9a51c2-a8f9-5177-9617-7980f784a865 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 66c40977-2b64-502f-a367-8d54ca870620 |  | radio | GMF-ITP-005 | Pass,Reviewed
text | da0c1e37-95b6-5a81-b7fa-3ad05fe38617 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 574cca27-3bc8-5fcc-8e16-e25ac7e741dc |  | note | QUALITY CONTROL - I
text | 01121ae5-de11-58d2-b34c-905cfb8bff98 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f6fae19f-d0f3-5086-883d-454fac2087ec |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - SMOKE DETECTORS TESTED
label | 283ac684-cd51-5ee0-9f6f-d4e7ed16e724 |  | note | ACCEPTANCE CRITERIA SPECIFIED - 100% Test of installed devices.
label | 685d5218-86f6-5edf-a07a-25396e6e7cb3 |  | note | ○ Correct location and spacings
label | 5076e485-4ac4-5ab4-9813-556050a5cb1a |  | note | ○ Correct zoning and description at FDCIE
label | 83ec7c2d-52a3-5349-8907-0e32a03d0003 |  | note | ○ Correct interfaces triggered
label | 6c1abde3-de90-5263-82fa-c3616c0c026b |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | c9ccd312-05e8-5c40-8acf-2bf239f57a6c |  | radio | GMF-ITP-005 | Pass,Reviewed
text | be412fb7-a82d-564d-bdfd-ffbacc6911f7 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 87133b4c-1835-5345-85a2-6700eaac9548 |  | note | QUALITY CONTROL - I
text | 8e56dbcc-7622-56cc-807f-374f840ee60c |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 9cedb935-a9d0-57d6-b1ca-8ab4696dfbef |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - A / C INTERFACE TESTED
label | 643db737-a0fa-5991-8872-e1839546ccf2 |  | note | ACCEPTANCE CRITERIA SPECIFIED - GFAs triggered from correct zones/devices
label | d123b0a6-a9c2-5d27-bd49-9225b047b430 |  | note | ○ Interface Matrix referenced
label | d964bb6c-49c6-5072-bd69-cf99638594e0 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | a1bca428-3e9c-58ba-b11d-4188f6968ac7 |  | radio | GMF-ITP-005 | Pass,Reviewed
text | 9aa37dd0-df53-509f-a372-7a3460046362 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | c5a37b72-1ca1-5c93-9436-9d3a968fdea8 |  | note | QUALITY CONTROL - I
text | 88980bf0-c347-5e36-9f41-a5da11255c24 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | df46d8c5-d74f-5b99-9d41-27b849bcac2e |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - MANUAL CALL POINTS TESTED
label | 73380529-c80e-57d5-8092-f88f4464e27d |  | note | ACCEPTANCE CRITERIA SPECIFIED - 100% Test of installed devices.
label | 199ef1d9-f78f-562f-9476-3876e76d3d9d |  | note | ○ Correct location and spacings
label | 37b57032-93be-5926-9dc4-756aaccfdd25 |  | note | ○ Correct zoning and description at FDCIE
label | 9b68d1c2-1e46-5919-ac2a-82d69f517313 |  | note | ○ Correct interfaces triggered
label | b684e693-ecfd-5401-adeb-d37870166f7c |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | 32cca62c-18a0-50c1-8e63-8afd796316f4 |  | radio | GMF-ITP-005 | Pass,Reviewed
label | 51a88a58-e17d-5297-b6c7-3b49b14d4662 |  | note | QUALITY CONTROL - I
text | 8421ceaa-0c34-5432-8da8-9cdc90201f8a |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | c5e72f7f-5e7d-5980-8514-afabb7473948 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - DOOR INTERFACES. BMS INDICATION
label | fbf8d188-d68a-5d18-8f9c-4bc7c947481f |  | note | ACCEPTANCE CRITERIA SPECIFIED - GFAs triggered from correct zones/devices
label | 4072338b-d91d-5a11-8c1f-6d6bd92ed912 |  | note | ○ BMS correct to descriptions provided from trades
label | b5a6d09b-3f0d-515e-9125-05a6ff5c88b8 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | a9b13fd5-31c8-53a6-91eb-e52acc82800d |  | radio | GMF-ITP-005 | Pass,Reviewed
text | 88394a7d-bd13-5954-8c7d-398f6919df8d |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 6daccc7e-e083-5d80-b0ab-2dc3b44c41f6 |  | note | QUALITY CONTROL - I
text | 19329dd1-2e60-5d7a-a8d7-bab2d0a4cf16 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | b3c27d2c-e6a9-530a-b40b-4f296e603f57 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - CERTIFICATES PROVIDED
label | 5f18ba3b-99ae-54d8-a989-9dce96d731d3 |  | note | ACCEPTANCE CRITERIA SPECIFIED - GMF-COMDOC-001, GMF-COMDOC-002, GMF-COMDOC-003, GMF-COMDOC-004
label | bbcc4d00-bc21-541d-8905-e1d63422574d |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - n/a
text | 62b6a1dc-a28e-5e9d-afed-5b3ccf35f390 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 8fa5a4c2-37e9-5102-b746-e23be873bd78 |  | note | QUALITY CONTROL - C
text | d461aca1-a9c7-5ee2-8670-20819bc8d3c3 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 5579da96-0f93-5cb9-a59d-dc7f25f7fbc8 |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | deaf9a1c-8173-5695-a1d6-70c75c83bd3d |  | button | Hold Point Required: | Yes,No,Other:
text | 5bc6bc00-2286-54ae-ae7b-340b19028554 |  | textbox | Other (if applicable):
text | afb723fb-d55f-5096-a2fc-73699145d1d5 |  | textbox | GM Sign Off - Name:
text | 8921a4ad-37c2-55a2-9dd7-2a4c91dfd196 |  | textbox | PC Sign Off - Name:
text | 5424299a-2db6-581d-9959-c074232890e1 |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | GM-ITPS-007 Warranty Period | itp |  |  |  | Yes | GM-ITPS-007 Warranty Period | ea5c79c2-91c1-49e0-a3fa-4968ca6bd539
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - PROVIDE CLIENT OPERATOR INSTRUCTIONS
label | 354db54b-c378-560d-9d16-06da73a92c21 |  | note | ACCEPTANCE CRITERIA SPECIFIED - As and when required
label | 93e95ec5-9749-53d2-a87a-40efdd0ee540 |  | note | QUALITY CONTROL - G/W
text | 448099fa-3cc0-5d9e-b53a-e5b26e00d18d |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | e34ff725-756c-5329-b19b-0e9ffe4d8a82 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - TRAINING
label | 071b5532-bc3b-576c-b44c-30bc38264968 |  | note | ACCEPTANCE CRITERIA SPECIFIED - As and when required
label | 86928ad5-8e9f-5765-9eae-9f1854cae7e0 |  | note | QUALITY CONTROL - G/W/H
text | d0af0170-2cfd-5da2-85e0-cf0d97c90bdf |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 7e181b80-c746-5381-a6f4-15ff436345cc |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - MAINTENANCE PLAN
label | 81b1ec02-5dc1-5df0-b5cb-ca47b40f419b |  | note | ACCEPTANCE CRITERIA SPECIFIED - As per spec. and quoted offer.
label | a6cd1839-de6d-56c5-bba4-0bbbf2212c74 |  | note | QUALITY CONTROL - G
text | eecb9723-8ff1-5f1b-96c2-4c7568b6f3ca |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | b32d20ab-47b5-5a0d-91bf-c6e2e03de3b7 |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | e321ac3f-9cd3-52f0-a2ae-5f40c4c03fe0 |  | button | Hold Point Required: | Yes,No,Other:
text | 9c44acae-608c-5381-b00e-27003c52e231 |  | textbox | Other (if applicable):
text | 9bfe2111-c07e-5ff6-85ea-59f69e82b7f9 |  | textbox | GM Sign Off - Name:
text | 7f730866-7219-55bf-98ba-1af3f128453b |  | textbox | PC Sign Off - Name:
text | b8f375f7-dd72-586f-ae17-23655e652cce |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-flat |  |  | checklist | Lendlease Contractor Schedule H Checklist |  |  |  |  | Yes | Lendlease Contractor Schedule H Checklist | eccb5f1a-42f7-439b-b784-23328f04a690
checkpoint-status |  |  | checkpoint | 1 - Report any incidents to Leandlease.
boolean | 113bade5-99ae-50a1-bd5b-05933d370746 |  | tickbox | Any incidents were immediately verbally communicated to Lendlease
boolean | 60c0b019-3f87-5a6f-b836-c260c3906058 |  | tickbox | A copy of Incident Notification Form was submitted within 4 hours
text | c9d5e1d0-06ac-59d5-8b43-b95a98407374 |  | textbox | Detail any incidents from the past month below and attach relevant forms.
checkpoint-status |  |  | checkpoint | 2 - Workers compensation first, progress and final medical certificates and Return to Work Plans
text | 8f269c97-5a2f-59ff-8c4a-d18ed4df06b3 |  | textbox | The following have been provided;
button | 267066da-45e9-5fff-b0b3-6f1ea6d02ac5 |  | button | First Medical | Yes, No
button | 23121e1b-e304-5110-8f3f-3844e6675b0f |  | button | Progress Medical | Yes, No
button | 2c9b487f-a848-565a-8437-322fd70f1790 |  | button | Final Medical Certificate | Yes, No
button | 3a928175-cace-568d-9092-be6b6e879ce0 |  | button | Return to Work Plans | Yes, No
button | 4d45aa0a-5717-5bec-a83b-0244c66ac443 |  | button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes, No
checkpoint-status |  |  | checkpoint | 3 - Notices from Regulator
button | 6fcabe6e-5929-5633-9f10-f7c886af3b3a |  | button | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator. | Yes, No
checkpoint-status |  |  | checkpoint | 4 - Daily Pre-Starts
button | 1353b0d5-d3cf-5b7a-a345-4243c807911b |  | button | I have delivered Pre-Start meeting minutes to the office by 9am each morning. | Yes, No
checkpoint-status |  |  | checkpoint | 5 - Conduct Toolbox Meetings
button | bb533f97-93ac-5221-bd01-463587b72622 |  | button | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance. | Yes, No
checkpoint-status |  |  | checkpoint | 6 - Conduct Workplace EHS inspections
button | 929e534b-5355-5894-a63c-8031591e25d6 |  | button | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted. | Yes, No
checkpoint-status |  |  | checkpoint | 7 - Labour Statistics and Man Hours
text | 9d2ea0b0-6ba2-5683-87ce-20307f196ba6 |  | textbox | Contractor Labour Statistics
button | 1313893d-9203-5d04-abe2-3ebca3837076 |  | button | ○ has been completed weekly | Yes, No
button | 13d9230f-cf2c-5616-8c55-47e4122b8ee6 |  | button | ○ submitted before the 26th day of each month | Yes, No
button | 36e38928-007a-52a3-89a1-c5d8298a12c3 |  | button | ○ is attached below | Yes, No
checkpoint-status |  |  | checkpoint | 8 - SWMS
text | b936c03c-7c77-5e40-b886-dbce6692f98d |  | textbox | Copies of updated SWMS have been submitted to Lendlease and
label | e9e3c8d5-f25c-50b5-a079-52ace15a3a3e |  | note | ○ Contractor SWMS review register has been submitted to Lendlease
button | 3927737a-6312-57fd-b467-060fa29f8a8e |  | button | ○ Updated copies of signed SWMS have been submitted after onboarding each worker | Yes, No
checkpoint-status |  |  | checkpoint | 9 - Workers are trained and competent
text | d6c438a8-99da-5111-8f44-d5fbc9cd174e |  | textbox | Copy of current training register has been submitted and
label | 9e121ee9-7ede-5d2c-a719-fc50f068f9b3 |  | note | ○ Copies of licences, qualifications, training records for any courses attended during the month.
button | 39a64f59-1e3b-5f6d-b174-35cd4ad4ad58 |  | button | ○ VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes, No
checkpoint-status |  |  | checkpoint | 10 - Plant Pre-Starts
button | 6b07f0b0-eaf0-5036-b29e-05426997dc45 |  | button | Copies of daily pre-start inspection records for the month to be submitted. | Yes, No
checkpoint-status |  |  | checkpoint | 11 - Maintain Plant & Equipment Register
text | 461185be-819c-5692-871c-42878dd7058b |  | textbox | Attach copies of up to date Plant Register
checkpoint-status |  |  | checkpoint | 12 - Plant and Equipment Maintainence
text | 70a494a0-194f-57ba-a7a1-7016cd492a7c |  | textbox | Copy of current and up to date Electrical Register to be submitted ( 3 monthly unless new tools added)
checkpoint-status |  |  | checkpoint | 13 - Maintain Electrical Register
text | 96196c2d-618e-53de-a973-dc85028316a0 |  | textbox | Copy of current and up to date Electrical Register to be submitted ( 3 monthly unless new tools added)
checkpoint-status |  |  | checkpoint | 14 - Maintain Fall Prevention Equipment Register.
text | bc9bc954-4e24-51c3-b190-8ef47b10e5ae |  | textbox | Attach a copy of the Fall Prevention Register
checkpoint-status |  |  | checkpoint | 15 - Lifting gear to be inspected, tested and tagged
text | 25af4a23-96b5-522d-b9c1-0034653ff7fa |  | textbox | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register and
label | a92a16ca-dcce-5c73-9be2-6acdceb4c4c8 |  | note | ○ I have submitted annual inspection certificates to Lendlease
button | 9422c0fa-1d97-5ed8-ac06-086b1e4786f0 |  | button | ○ monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes, No
checkpoint-status |  |  | checkpoint | 16 - Maintain Hazardous Substances Register
text | ad02dcd6-c0c3-501f-a7af-e3476c485d7e |  | textbox | A copy of Hazardous Substances Register highlighting anychemicals brought ont site this reporting period.
text | 07603931-cf96-5f53-b4c9-106352846bcc |  | textbox | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
checkpoint-status |  |  | checkpoint | 17 - Maintain Ladder Register
button | 538cd13b-7c5b-5b45-be68-2403e69b6a8a |  | button | A copy of the Ladder register has been submitted this month | Yes, No
checkpoint-status |  |  | checkpoint | 18 - Safety Data Sheets and Risk Assessment documentation
boolean | 57755786-186f-5a96-9dbe-e50039be2f6e |  | tickbox | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
checkpoint-status |  |  | checkpoint | 19 - Temporary Works Design Register
text | 99994a40-c1fb-5887-b768-d6efccd5139c |  | textbox | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
button | 48f95bb9-74dc-5e4a-9170-a822a246b2c6 |  | button | I have attached the updated Temporary Works Design Register | Yes, No
button | 87ffe83e-b719-54cf-a8f0-6e2ce88d184a |  | button | I have attached Evidence of Engineering Certification | Yes, No
button | 54bb9071-d58a-5e1f-83d2-a988c09c3006 |  | button | I have attached Evidence of 3rd Party review of engineering | Yes, No
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | GM-ITPS-002 Fire Alarm and EWIS Design | itp |  |  |  | Yes | GM-ITPS-002 Fire Alarm and EWIS Design | f28484bb-5ba1-4dcc-ae59-abf1c5adbb12
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | 1 - REVIEW CLIENTS DRAWING REGISTER
label | a064fcea-3ffd-5d82-b24b-38991b6429ba |  | note | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE
label | 7f9588e7-0c50-5090-aa3f-8ee02933f370 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
text | 92e68273-1a07-5da3-b052-9cf8cbfae874 |  | textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | 541802ea-08b3-5a8a-aeb3-2c6b7aa2891f |  | note | QUALITY CONTROL - I
text | 6b4ae65c-17b8-54ed-900b-53ddbfea7562 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 66c9d8ef-8b5a-50cb-8589-98c04cf352ee |  | date | DATE:
checkpoint-status |  |  | checkpoint | 2 - NOTATE INTERNAL DRAWING REGISTER
label | b4773135-bcec-52f6-a2dc-21f429d42a7a |  | note | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE
label | 61a57915-aa52-5f36-b490-66d7bf98aec1 |  | note | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | 9dc0c5ac-9328-547b-a224-a547aa52566d |  | note | QUALITY CONTROL - I
text | 36ac551e-de37-5524-b163-9b19f8851a68 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 34949e7b-8ec2-5c73-b8d1-3989033a4feb |  | date | DATE:
checkpoint-status |  |  | checkpoint | 3 - REVIEW TENDER/CONSTRUCTION DRAWINGS
label | b47443b9-8ccd-5f3d-a7f2-b2f62cd31e5b |  | note | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE
text | 7693e38b-788b-5a7b-86c1-3efa973fcef6 |  | textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | dc8fff02-5d0b-5be5-aab2-da595f0ca61f |  | note | QUALITY CONTROL - I
text | 9f26fde9-2076-5fe0-9931-c8b9126c4e2f |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | e618dccc-2177-57d3-8779-3cc7a18e0810 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 4 - REVIEW SPECIFICATION
label | 1734aa88-4741-5e30-af1d-8479754dc958 |  | note | ACCEPTANCE CRITERIA SPECIFIED - NCC2019 FIRE SPECIFICATION
label | 9de4e92a-b431-5cdd-ac2b-c73d9a5e2301 |  | note | QUALITY CONTROL - I
text | 00d5633f-16ad-5fb1-a24a-c9d96f348b0a |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 77748099-7a47-5a67-9b13-9d615a91f89b |  | date | DATE:
checkpoint-status |  |  | checkpoint | 5 - PREPARE SHOP DRAWINGS/ LAYOUTS
label | 41662d22-9166-5a47-bed5-ac4a57d95758 |  | note | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE NCC2019 FIRE SPECIFICATION
label | fa0dbdbc-d0a3-5a0b-8a68-e757c8982277 |  | note | QUALITY CONTROL - A & I
text | 5a9508ac-cc7b-542a-a155-3fad64cc7ff7 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 4eadd2a2-2e8a-5aea-a196-ce15c5fca140 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 6 - REVIEW SUPPLIERS SHOP DRAWINGS
label | 4e6df98e-43b8-5574-9773-c6d366452da2 |  | note | ACCEPTANCE CRITERIA SPECIFIED - NCC2019
text | ed90f828-c390-51eb-a126-fd3f2bf2426d |  | textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | 32d3d843-b04d-5f39-90ae-cbe966372c20 |  | note | QUALITY CONTROL - I
text | a51fcbda-3839-599f-9230-1fb70592cadb |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 5aee3a47-a276-5ef8-a96b-a95309ae0cb8 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - DESIGNING FIRE ALARM SCHEMATIC
label | 2c6622d5-264b-55f9-b9a4-73961d1b10fa |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House Design 1670.1-2018 – Must specify size/type of cable to be installed, transmission paths, type of devices to be installed and End of Line Devices
label | 3b0f0a6c-66cf-5178-881d-50b19bdc5bec |  | note | QUALITY CONTROL - I
text | 1b7d91d6-8438-5101-a8a2-ebe6e4cfefce |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | f3261dc3-b3df-51d4-9a18-f222ab3013ea |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - PREPARE SCHEMATIC DRAWINGS
label | 43c47f22-f751-5ce7-b0bd-58bc582551a7 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Prepared to as installed drawings.
label | d840e19f-4ef4-561c-b488-34ad5ad35454 |  | note | QUALITY CONTROL - I
text | c19364b6-0404-52af-acab-6790dd41e57b |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 36caae91-9557-57e0-b3c7-df1e72102fa8 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 7 - SUBMIT SHOP DRAWINGS FOR APPROVAL
label | 89fa32f9-cab7-51de-bc77-f55d2b9ecb3f |  | note | ACCEPTANCE CRITERIA SPECIFIED - In house design Referenced to PC specifications
text | 391ec2d4-eeaa-5485-9eca-df591f01ac80 |  | textbox | DRAWING REFERENCE NUMBER - For Approval Issued Drawing No:
label | e5caa871-88f4-513f-bce7-e1a569d32fbc |  | note | QUALITY CONTROL - I
text | 7e12f842-2fa0-5275-a0eb-b5e7647d1d41 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 663d4073-caa9-584a-bd60-88db3cd6b5f4 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 10 - REVIEW RETURNED SHOP DRAWINGS
label | 633a1ffb-378f-5cd4-93ef-6c519fc45931 |  | note | ACCEPTANCE CRITERIA SPECIFIED - In House QA
text | 359501c1-1dc0-5c51-b223-7855b471eec5 |  | textbox | DRAWING REFERENCE NUMBER - For Approval Issued Drawing No:
label | f28ef354-c2cc-5f76-8052-74a335d6ac26 |  | note | QUALITY CONTROL - W & I
text | a8b961ce-39af-5ddf-a31f-9ca93a7cee69 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | 93dbe3d3-7615-5334-a053-c10056568963 |  | date | DATE:
checkpoint-status |  |  | checkpoint | 11 - DISTRIBUTE "FOR CONSTRUCTION" DRAWINGS
label | 9b899d3a-0dd8-5d8a-b81f-8e2846908510 |  | note | ACCEPTANCE CRITERIA SPECIFIED - Referenced to PC specifications. Updated and superseded as needed
text | 5c64924d-ba11-5f3e-bdc0-b42bb6eae1b6 |  | textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawing No:
label | 6ec447f0-4cff-570c-8526-41725cc97018 |  | note | QUALITY CONTROL - I
text | e5dc3978-ebd6-55f0-b378-309a1e128e20 |  | textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | da1366fb-3e26-53c8-a16f-73ac90154af1 |  | date | DATE:
checkpoint-status |  |  | checkpoint | Hold Point Details
button | 4a58546a-393e-5121-a38b-36fa356e3229 |  | button | Hold Point Required: | Yes,No,Other:
text | 0c5437bd-196b-5672-8981-2e6ea3b88d9f |  | textbox | Other (if applicable):
text | 6ff01513-285c-53b2-b930-18cfe65cc4a6 |  | textbox | GM Sign Off - Name:
text | 1466eabd-55e9-520d-ac8a-631d944d8425 |  | textbox | PC Sign Off - Name:
text | c31c0a8b-4e9e-5fe9-8569-f8e86236e42f |  | textbox | CS Sign Off - Name:
holdpoint |  |  | signoff | Signatures
checklist-flat |  |  | checklist | Tool Box Talk - Platform Ladders |  |  |  |  | Yes | Tool Box Talk - Platform Ladders | fb3230ac-a3f8-47d3-9a01-1b12f4769b76
checkpoint-status |  |  | checkpoint | Tool Box Talk - Platform Ladders
label | 887bab57-3216-58e7-9dd5-6974b3a623f9 |  | note | ○ DO NOT use platform ladder unless you are familiar in its safe use and operation.
label | ac68153f-7547-5f9f-b14c-f8801309e330 |  | note | ○ Always complete as much work as possible at ground level before using the ladder.
label | 3271903a-2c15-5d14-ac31-800aa151f93c |  | note | ○ Make sure the platform ladder is stable before climbing.
text | 5c4a49ee-d931-5509-bdad-bc64c1ca1617 |  | textbox | Project:
text | 00a320e9-986f-593f-bfe8-d25f2931da45 |  | textbox | Tool Box delivered by:
date | d0208122-f03a-5610-bde4-6bcb1a760f97 |  | date | Date:
text | da9865ac-d3b6-579f-bb6b-472d8b97b3d7 |  | textbox | Attendees:
checkpoint-status |  |  | checkpoint | Potential Hazards
label | 3674f2b7-e39a-58bf-b062-1209a407d5a0 |  | note | The folllowing potential safety hazards and risks have been explained to attendees:
boolean | 5ea57c24-c9ef-5ac2-aae7-14b6543b15e5 |  | tickbox | Falls from height
boolean | e35ecb4b-a22f-5bcd-833f-fe852d10554a |  | tickbox | Falling objects
boolean | a3d70cbf-4729-5583-aee4-bcf73f29102e |  | tickbox | Awkward posture
boolean | 016ab889-7fd8-5c55-95e3-1cf5f8ca44c5 |  | tickbox | Duration of task
boolean | 674a0483-b78e-5388-ad6a-db7ac2554b1c |  | tickbox | Repetition of movement
boolean | 3f4946f8-8fdd-526a-bb60-7b0d27db4098 |  | tickbox | Sprains/strains
boolean | a6af3874-9657-5afa-ac7b-5c30211f6885 |  | tickbox | Over-balancing
boolean | 75d35ab2-1c77-568c-80f3-d9d45ae93ef3 |  | tickbox | Slip/trip/fall
boolean | 4a7ce000-11b4-5942-9d59-57beec09de90 |  | tickbox | Electrical hazards
boolean | 70790ef5-6074-57a2-b56e-987747b11967 |  | tickbox | Climbing with loads
checkpoint-status |  |  | checkpoint | Pre-Operational Safety Checks
label | 6ffbd377-bf17-5fba-98aa-8caef52856d1 |  | note | 1. Familiarise yourself with the safety instructions on the ladder. 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing 3. Do not use if affected by a medical condition or medication. 4. Keep ladder clear of live wires, electrical hazards and ceiling fans. 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards. 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing: • joints between steps and side rails tight, all fittings secure, moving parts operate freely • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and • all components of ladder intact including side rails, rungs, platform, feet, hand grip. If any component is found to be worn or damaged, rectify any faults before use.
checkpoint-status |  |  | checkpoint | Operational Safety Checks
label | df307b10-6066-5dfe-b2be-ccdabe4b711c |  | note | 1. Complete as much of the task at ground level as possible. 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder. 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed. 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing. 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free. 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder. 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform. 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform. 9. Do not ‘walk’ the ladder while on it. Always get off to shift position. 10. Before moving a ladder, take care to ensure that all tools and other items have been removed. 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
checkpoint-status |  |  | checkpoint | Housekeeping
label | b7b52c7c-7b6c-5b22-8666-70b57f43c8ee |  | note | All attendeeshave been made aware they should:
boolean | 5c711e95-86eb-5f70-9f58-45404bea1e34 |  | tickbox | Return ladders to secure storage in a clean and in safe working order
boolean | 0d24abf6-09a7-54db-913a-af58fcfdb176 |  | tickbox | Regularly check ladder feet for excessive wear.
boolean | fdb2ffa5-48c5-5b86-a475-b5e212b244b3 |  | tickbox | Enter any maintenance in an equipment maintenance record
text | ac8f4780-7d87-5234-98fe-0fee60585788 |  | textbox | Items for Discussion
text | 61838543-8502-5082-8baf-f0fa703ab465 |  | textbox | Items for Review and discuss at next meeting:
holdpoint |  |  | signoff | Signatures