## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITPS-013 Electric Fire Pumpset Installation and Commissioning | itp |  |  |  |  | ITPS-013 Electric Fire Pumpset Installation and Commissioning
section | Details
checkpoint | 1 - Check location of pumpset - in a position that is protected from falling debris, and vehicular and mechanical damage
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - Check clearence of pumpset - For ongoing inspection and testing, a clearance of not less than 1.0 m shall be provided around the perimeter of a complete pump assembly;
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - Check clearence of pumpset - for multiple pumpset installations, a clearance of not less than 600 mm between each of the installed pumps shall be provided
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - Check elevations - Multiple pumpsets shall be installed with the centre-line of all suction pipes at the same elevation. If the pumps are to be installed at different elevations, the elevated pump shall be installed on a properly constructed mezzanine floor with head clearance of minimum 2.1 m to the underside on both levels
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - Check Plinth - Pumpset baseplates shall be mounted on concrete plinths with a height not less than 150 mm above the floor. For fixing purposes, the concrete plinth shall extend 150 mm past the edge of the baseplate on all four sides.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
section | Electric Pumpsets
checkpoint | 6a - Check the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 and 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6b - Check the direction of rotation
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 and 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6c - Ensure that the delivery from the pump under test is the only supply to the measuring device and that all flow from the pump passes through the device.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 and 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6d - Ensure that the pump is primed and that lines are clear, valves correctly set (open, closed or adjusted to required pressure), and that water is available.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 and 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | Hold Point Required: | Yes
radio | W5.4 System Filling and Venting | Pass
radio | W5.4.1 Pressure Testing | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
holdpoint | HOLD POINT
checkpoint | 6e - Isolate all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and compression-ignition engine driven pumps
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
radio | W5.4 System Filling and Venting | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7a - The following shall be reported – Pump plate details / photo
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7b - Record - the pressure in the system at which the pump starts automatically.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7c - Record - Pump shut-off pressure on delivery gauge
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7d - Record - Motor current at shut-off pressure.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7e - Record - Delivery pressure at maximum flow
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7f - Record - Pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7g - Check –
label | (i) periodically check the temperature of the bearings and stuffing box leakage and note any abnormality;
label | (ii) check that all alarms and indicators, both visual and aural, have been activated; and
label | (iii) check that alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - Whether the electric pumpset, together with its associated control gear and ancillary equipment, functioned correctly.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 9 - Whether the pumpset satisfies the intended performance conditions (e.g. flow rate and head).
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 10 - Whether there is operational abnormality.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | ITPS-014 Diesel Fire Pumpset Installation and Commissioning | itp |  |  |  |  | ITPS-014 Diesel Fire Pumpset Installation and Commissioning
section | Details
checkpoint | 1 - Check location of pumpset - in a position that is protected from falling debris, and vehicular and mechanical damage
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - Check clearance of pumpsets - For ongoing inspection and testing, a clearance of not less than 1.0 m shall be provided around the perimeter of a complete pump assembly;
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - Check clearence of pumpset - for multiple pumpset installations, a clearance of not less than 600 mm between each of the installed pumps shall be provided
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - Check elevations - Multiple pumpsets shall be installed with the centre-line of all suction pipes at the same elevation. If the pumps are to be installed at different elevations, the elevated pump shall be installed on a properly constructed mezzanine floor with head clearance of minimum 2.1 m to the underside on both levels
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - Check Plinth - Pumpset baseplates shall be mounted on concrete plinths with a height not less than 150 mm above the floor. For fixing purposes, the concrete plinth shall extend 150 mm past the edge of the baseplate on all four sides.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 11 Installation
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
section | PRE COMMISSIONING CHECK LIST
checkpoint | 6a - Check the – Check the cooling supply system
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6b - Check the – Check engine fuel supply
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6c - Check the – coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6d - Check the - direction of rotation.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6e - Check – Engine lubricating oil is at the correct level. Check – the battery electrolyte level and the battery leads and connections. Check – exhaust system is intact
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6f - Ensure – pump is primed and that lines are clear, valves correctly set (open, closed, or adjusted to required pressure), and that water is available.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6g - Isolate – all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
section | PUMP COMMISSIONING CHECKLIST
checkpoint | 7a - Record – For automatic starting pumpsets, record the pressure in the system at which the pump starts automatically.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7b - Record – Engine Oil Pressure
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7c - Check – Coolant Flow is correct
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7d - Check – That the fan is rotating and all fan belts are intact
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7e - Record – pump shut-off pressure.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7f - Isolate – the flow meter, partially open the test valve, and flush to remove any debris or foreign matter; open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - Run the pump for 30 min at maximum flow and record the following:
label | (i) Suction and delivery pressures.
label | (ii) Engine running temperature, which shall be within the engine manufacturer’s recommended limits.
label | (iii) Engine oil pressure, which shall be within the engine manufacturer’s limits.
label | (iv) Air temperature at pumpset.
label | (v) Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate.
label | (vi) Check that the requirements of Clause 9.3.6.2 are complied with by holding the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles. On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position and check if the engine starts immediately.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8a - During the operations in Item (h)—
label | (A) periodically check temperature of the bearings and stuffing box leakage and note any abnormality;
label | (B) check that all alarms and indicators, both visual and aural, have been activated; and
label | (C) check that alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped. If the pump failed to start alarms that are fitted on the pump fire pump controller and at the remote station, check that these alarms operate both aurally and visually.
label | (j) Shut down and restore starting mechanism to stand-by status.
label | (k) Restore power supply to the electric pumps and check correct status of indicators.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2941.1-2013 – Section 12
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | ITPS-015 GM Tank Installation | itp |  |  |  |  | ITPS-015 GM Tank Installation
section | Details
checkpoint | 1 - Confirm – Structural Elements as per AS2304 – Section 3
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - Confirm - Correct Installation drawing, onsite.
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - Confirm – Ladder selection and orientation to submitted design drawings, Confirm – Nozzle selection as per submitted design drawings
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - Confirm – Position of tanks with principle contractor onsite
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - Confirm – Competencies and Authority to work of subcontractor
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6a - Commissioning – Structural inspection prior to filling
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6b - Commissioning – Inspect all ladders for conformance and clearances and position of tank accessories
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6c - Commissioning – Hydrostatic inspection after tank is filled to maximum capacity
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6d - Commissioning – Record any defects
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6e - Commissioning – Submit certificates and warranty periods
label | ACCEPTANCE CRITERIA SPECIFIED - AS2304 – Water storage tanks
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | ITPS-016 Fire and EWIS Panel Installation | itp |  |  |  |  | ITPS-016 Fire and EWIS Panel Installation
section | FIRE INDICATOR PANEL
checkpoint | Check – Location
label | (i) Installed in a location protected by the FDAS (expect where external to building)
label | (ii) Operation of FIP shall not affect evacuation of building
label | (iii) Located in an area which presents low risk of damage to equipment and persons
label | (iv) Not mounted in any rooms containing sprinkler, pumps or motors
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Check – Particulars
label | (i) Have controls and indicators not less than 750mm and not more than 1850mm above floor level.
label | (ii) Have unobstructed access to controls and indicators
label | (iii) Be mounted above ground level to protect batteries/on a plinth
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Check – Where the FIP is obscured by a door ensure the words “FIRE PANEL” in letters not less than 50mm high. There SHALL be no other lettering on the door.
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Check – Clearance. 1000mm in front of FIP and 500mm to each side shall be maintained.
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Zone Block Plan – Installation shall be securely mounted and easily accessible.
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Manual Call point – Manual call point must be installed at the entry point to site if the FIP is not located close to that point.
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Check – Power cabling is installed at FIP location
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Check – Location strobe on front of building is installed and operational.
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
section | EWIS PANEL
checkpoint | 1 - CABLE TYPE & SIZE TO DESIGN CRITERIA
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018 Have a cross sectional area of no less than 0.75mm2 AS3000
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.4.0 Wiring | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - CABLE HEIGHTS & LOCATION ADEQUATE FOR FIT OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: internal domestic and office situations where cabling is mounted on walls at heights above 1.5m AS3000
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.5 Control Loops | Pass
radio | C5.4.0 Wiring | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - CABLE FIXED TO SPECIFIED REQUIREMENTS
label | ACCEPTANCE CRITERIA SPECIFIED - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.5 Control Loops | Pass
radio | C5.4.0 Wiring | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - DETECTOR BASES FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670, AS1668: Detectors that can be contaminated by construction works should not be fitted unless suitably protected until the construction works are completed.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - DETECTOR HEADS INSTALLED & TYPE CHECKED
label | ACCEPTANCE CRITERIA SPECIFIED - Detector type to appropriate location. Installed to Latest RCP
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.6.0 Sensors/Detectors | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - MANUAL CALL POINTS INSTALLED
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: An MCP shall be mounted between 750 mm and 1100 mm above floor level and a clear space of 600 mm shall be provided in a semi-circle in front of the MCP.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.10.0 Manual Call Points | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - STROBES FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Check with Design Drawing and/or RCP
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.2 Set Points | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - SPEAKERS INSTALLED
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670: Check with Design Drawing and/or RCP
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 9 - WARDEN INTERCOM PHONES
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018: The WIP handset shall be mounted at a height of not less than 1200 mm and not more than 1800 mm above finished floor level.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C6.2.8 Warden Intercom Phones | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 10 - SPRINKLER INTERFACES FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.2 Set Points | Pass
radio | C5.8.0 Modules Input/Output | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 11 - FIRE RATING TO PENETRATIONS CORRECT
label | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: Ensure correct Test Report is used – refer to FRL requirements on wall selection
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 12 - LABELS AFFIXED
label | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: The label should be positioned close to the service penetration
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 13 - ACOUSTIC PENETRATION SEALING
label | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: Sound proofing sealant may be used depending on dB Level requirements
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 14 - CABLE TRAY BRACKET SPACING
label | ACCEPTANCE CRITERIA SPECIFIED - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 15 - INSTALLED IN ACCORDANCE APPROVED WORKING DRAWING AND LATEST ARCHITECTURAL
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA. Up to Date drawing register. Drawings updated with MPX approved references.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures