## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Drawing Upload - Checklist (V.101221) |  |  |  |  | Yes | Drawing Upload - Checklist (V.101221) | 07b62baf-73f5-43a5-a9e9-12fefe37e254
checkpoint-status |  |  | checkpoint | Drawings/comments/signatures - attached below
checklist-flat |  |  | checklist | Commissioning (V.061221) |  |  |  |  | Yes | Commissioning (V.061221) | 19ae57fc-9ee4-4545-8de9-20b731d838dd
checkpoint-status |  |  | checkpoint | Check products for imperfections
checkpoint-status |  |  | checkpoint | Fixtures location & ixings all correct (as per drawings & samples)
checkpoint-status |  |  | checkpoint | Clean out all strainers / aerators
checkpoint-status |  |  | checkpoint | Check for no cross connections / leaks / access to isolation valves
checkpoint-status |  |  | checkpoint | Floor wastes (clear of debris & draining correctly)
checkpoint-status |  |  | checkpoint | Quality of silicone seals to fixtures acceptable
checkpoint-status |  |  | checkpoint | Hot water tempering valve set to 50c (+/- 5c) & DDA thermostatic mixing valve set to 42 degrees.
checkpoint-status |  |  | checkpoint | Water pressure acceptable 350Kpa to 500 Kpa
checkpoint-status |  |  | checkpoint | Hydraulic Work(s) completed to specification/drawings & Area left clean/tidy
label | f742363a-ebc0-57a8-a848-3ad2a31e205b |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 39cbcaa3-6d12-5b3a-a7fe-8841f76ddf64 |  | note | Click to Attach Signature(s) below
button | b9191a12-48d2-5b30-91f7-8dc651fde593 |  | button | Signature by Builders Site Coordinator | Yes, No
button | 353f317a-3fb9-58ea-9874-f01620d9b4b6 |  | button | CDC Plumbing Signature Sign-Off added below | Yes, No
checklist-flat |  |  | checklist | ITP 001 - Drainage In Ground |  |  |  |  | Yes | ITP 001 - Drainage In Ground | 2181e0a8-aadf-4a42-8761-e4e01c3193d6
checkpoint-no-status |  |  | checkpoint | Spec. Ref: CRPP-UML-SPE-HY-SI-001-1
text | 1d1ef807-8978-4cb2-ae4e-3d7a35fc4106 |  | textbox | Drawing Ref:
label | b198462b-4057-4360-88cc-940dd09fb065 |  | note | Service Type:
boolean | e556bd3c-e297-4860-af55-b59e49dd6037 |  | tickbox | Stormwater
boolean | baad32c2-2b76-425f-974e-e3dc73975746 |  | tickbox | Sanitary Drainage
boolean | fe987511-4125-4772-a811-5e75b1274aad |  | tickbox | Trade Waste
text | a5df39ec-02f9-42d2-98a8-503a17abdad3 |  | textbox | Other:
checkpoint-status |  |  | checkpoint | Set out and alignment
label | a8813d32-1611-4276-b633-07a164a5fc0f |  | note | Acceptance Criteria / Reference: Approved installation drawings
label | c9558065-7226-425c-aa13-206e5d2930d1 |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Inverts and grades
label | 4b4e1c33-8d85-45e9-ba74-85bc98f068ff |  | note | Acceptance Criteria / Reference: Approved installation drawings
label | ab6b4466-c42a-4346-ad7a-c4c4212e6d50 |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Pipe bedding material
label | a9954946-7e36-404c-b072-09a84ea48412 |  | note | Acceptance Criteria / Reference: As per specification
text | 5fb7ad5c-1729-4279-9f09-8973ef00ec99 |  | textbox | Specification:
label | 33b84550-828f-4f83-adf1-5fb3f2071e0b |  | note | Inspection Type: N
label | de55d271-f149-4ebc-b615-76e93ecba722 |  | note | Comment: CST By Others
checkpoint-status |  |  | checkpoint | Pipe material correct
label | 1136505f-8ef3-4fa4-8354-bee4bfce7d87 |  | note | Acceptance Criteria / Reference: As per approved installation drawings
label | cb89ad1f-2602-4556-b150-7e441da461de |  | note | As per approved installation drawings
boolean | 7cf9bb0a-e126-471f-8145-ea24c64a95f3 |  | tickbox | PVC
boolean | 00496936-01e7-4f83-98d3-555447559ae2 |  | tickbox | HDPE
boolean | 2e4d6bf4-303a-4dc6-a298-e4a0eee7979e |  | tickbox | STORMPRO
boolean | 03148373-bb78-4795-bf57-b08aadc9759a |  | tickbox | RCP
text | 025c35d1-de74-4237-8ed6-8d370bde83bf |  | textbox | Other:
label | b7b930d3-45e8-473a-8e1a-082929865ec8 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Inspection & testing prior to Concealing
label | 6f1ca685-b40f-4199-a0eb-bc41ad9c8fad |  | note | Acceptance Criteria / Reference:
boolean | 7500cb95-1b91-4dcc-b47e-9e943e14f510 |  | tickbox | Hydrostatic
boolean | 9a561934-af43-41ad-852b-27ab50b1e27c |  | tickbox | Air test completed
label | 72cc7c0a-3f2a-4393-a67b-0e4407fab80e |  | note | Inspection Type: H, T, W
label | bb17406d-335a-4e47-ab74-ee51cc3530fb |  | note | Comment: REF TEST CRITERIA; Air test to 30kPa, minimum of 3 min.
checkpoint-status |  |  | checkpoint | Seal open drainage points
label | 5fc0273b-78a2-42f1-bc63-d2754337c72b |  | note | Acceptance Criteria / Reference: Sealed
label | 5bcf1ca4-c602-450b-86b8-e77639959487 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Heat Trace Installed to trade waste
label | 6cf8c50f-5c96-40e1-97a8-171ed6b919f9 |  | note | Acceptance Criteria / Reference: As per installation drawings if required.
label | 4c795919-9bb6-4d8c-a8b4-2349adce3365 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Backfill trenches & ID Tape
label | 29490c24-1aed-47a5-8a1d-7a8c8951bf16 |  | note | Acceptance Criteria / Reference: Existing material used for backfill or approved alternative (details in comments) . ID Tape laid 300mm OVER SERVICE
label | 9435dece-6413-481e-8b92-f05e3bc8afa7 |  | note | Inspection Type: N
label | 5fe4f44f-0c34-4111-8d03-7e29598da7ab |  | note | Comment: Detail as per CDC shop drawing, CST By Others
checkpoint-status |  |  | checkpoint | As Built Records
label | f5539b4f-23fc-4e4e-ad0b-11a25500613b |  | note | Survey as installed works and update AS Built
checkpoint-status |  |  | checkpoint | Compaction and compaction testing
label | 5dad6594-4cb5-49cd-a7a5-a5ebbcf18ed7 |  | note | Acceptance Criteria / Reference: Stabilised sand back fill, N/A, Landscaped areas N/A
label | a14771d9-57bd-4063-a34c-a1dc2986c239 |  | note | Inspection Type: N
label | a73a8d6d-74a8-4122-90d3-5be024e26991 |  | note | CST By Others
checkpoint-status |  |  | checkpoint | CCTV & Photo records
label | a5a7fc3e-0e7b-43e3-888c-96957b3c2cd8 |  | note | Acceptance Criteria / Reference: Photo records during installation works and CCTV after backfilling. Attach reference drawing
label | def7d1d8-b9a8-4e5e-a8c1-d1824ef802c2 |  | note | Refer Independent CCTV records prior to Practical Completion
checkpoint-status |  |  | checkpoint | Inspections carried out by
text | 402a829b-cdd1-424c-a972-ce3a44233a9c |  | textbox | Name:
text | 77d80e10-34ec-44dc-a1ca-2f87507cd0c9 |  | textbox | Organisation:
checklist-flat |  |  | checklist | ITP 004 - Reticulated Above Ground |  |  |  |  | Yes | ITP 004 - Reticulated Above Ground | 417d43bf-c2a6-4c11-a44e-f34619b070b7
checkpoint-no-status |  |  | checkpoint | Spec. Ref: CRPP-UML-SPE-HY-SI-001-1
text | fce13593-69a4-4b15-ae4d-2051f0db3ea9 |  | textbox | Drawing Ref:
label | b909c059-ab96-4db4-8bc8-632824115b08 |  | note | Service Type:
boolean | 7a15f067-6e81-4ef2-936d-9aa23861d9b9 |  | tickbox | Cold Water
boolean | df29216f-21c4-45df-b3c9-1fcd72c00886 |  | tickbox | Hot Water
boolean | 203de37d-af5e-4b8e-9d79-cc439f716c9d |  | tickbox | Recycled Water
boolean | 5fdeba95-edb2-46c8-9724-da6344380f9c |  | tickbox | Fire / Hose Reel
boolean | 78635c6a-fafe-456e-ab7f-3a0f18ed24ae |  | tickbox | Gas
text | c9fb5264-6afa-48dc-ab4a-652f790eb916 |  | textbox | Other:
checkpoint-status |  |  | checkpoint | Set out and alignment
label | d5fb47be-ff52-41aa-9157-8c7665482fcc |  | note | Acceptance Criteria / Reference: Approved installation drawings
label | 875c6d86-1a9d-49cd-ae31-e026003ca003 |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Inverts and grades
label | 8208538c-610a-4293-a670-5144285e246e |  | note | Acceptance Criteria / Reference: Approved installation drawings
label | 08d86591-f37c-44e1-bd8d-848f36099db1 |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Brackets installed correctly
label | 36e21b03-6f19-4edc-982f-757921f9bee1 |  | note | Acceptance Criteria / Reference: Bracket spacing as per AS 3500
text | 3106c032-4f20-4698-9ea6-1d01ab2b0589 |  | textbox | Bracket Types -
text | 6c391c41-440d-4e22-a892-25f803ba743e |  | textbox | as per -
label | c7ed76c8-16b8-41c8-aa2e-0c70a850bae5 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Pipe material correct
label | 2cbe45ce-1168-4bad-bc07-0ef54182f59e |  | note | Acceptance Criteria / Reference: As per approved installation drawings
label | 2168d2b8-7a12-4752-9789-5da926afd9fc |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Inspection & testing prior to Concealing
label | 4af51c35-43ca-440a-b565-9d6fef03d42b |  | note | Acceptance Criteria / Reference: Pressure test completed per:
boolean | 3678361e-7816-40a2-a7ee-4975a6adfa69 |  | tickbox | AS3500
boolean | 23653f5b-bbdb-4102-9ae0-2abe598cc01c |  | tickbox | AS5601
label | aa5e4972-bccb-41bb-92f7-ff4874bbfcee |  | note | Test Type:
boolean | a4fb5f66-f8e7-462f-9b63-099cd093cb32 |  | tickbox | Water
boolean | 6ec02fb9-e421-46a2-93ea-e1c155dd8de9 |  | tickbox | Air
boolean | 62a0e212-f531-4eb2-9950-0117653534e6 |  | tickbox | Nitrogen
text | 8ce121c6-f7dd-45ae-b15b-f03e8def9a39 |  | textbox | Pressure: |  |  | kPa
text | 0d2a5507-6699-4685-8751-219079143937 |  | textbox | Duration:
text | 392e6317-2888-4edb-92ca-65ef0c2f434d |  | textbox | Gauge Number:
label | e7565b05-8420-4bf3-8aa7-bd9feece00f8 |  | note | Inspection Type: H, T, W
label | bf4a918d-7b65-4150-b37a-b72458e5090d |  | note | Comment: Nominate test criteria
label | bd2ccebe-8fdf-4b85-8945-ecdf581ecf38 |  | note | Water:1 ½ times the working pressure or 1500kPa.
label | bd943a70-9e4a-4b42-9c85-e013d265f4a8 |  | note | Fire: 1 ½ times operating pressure or 1700kPa whichever is greater
label | 339e1f75-c685-4df9-94c9-7cfb969fd8e1 |  | note | Refer commissioning plan for disinfection and flushing of mains
checkpoint-status |  |  | checkpoint | Pipework labelled
label | 66444f60-c43d-410c-bfb6-b1def32ca7da |  | note | Acceptance Criteria / Reference: As per AS 1345
label | 94efdfbe-7a4a-4e11-9976-c3a0135d5d00 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Heat Trace Installed to Hot Water
label | bc895095-810d-49b4-b5c6-8c464487899a |  | note | Acceptance Criteria / Reference: As per installation drawings, if required
label | a9983ed6-3d1b-420d-bb66-279ebd3f2e8e |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Thermal lagging
label | 0ccec1a3-b184-46c9-a759-7002bd444629 |  | note | Acceptance Criteria / Reference: Secure and full coverage
label | 4f6cf906-65f0-4c1b-bbce-0a3eafdfe68b |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | As-built information recorded
label | 542aef55-4635-4dc9-b4b9-a196b60d83cd |  | note | Acceptance Criteria / Reference: Recorded on shop drawings as required prior to concealment
label | 3fec1ddf-803d-443b-917d-505787661092 |  | note | Inspection Type: S
checkpoint-status |  |  | checkpoint | Inspections carried out by
text | 59a1f1ff-c542-45c4-bb8c-aabd6088922d |  | textbox | Name:
text | 46b147df-afd6-4b99-ae1b-10beb4fa79bd |  | textbox | Organisation:
checklist-flat |  |  | checklist | ITP - Water Disinfection |  |  |  |  | Yes | ITP - Water Disinfection | 5802c609-be84-46fa-8d14-4bc828e547f2
checkpoint-status |  |  | checkpoint | Drawing #/Revision checked and referenced
text | 390ea2c2-715b-539e-897c-26af99c81222 |  | textbox | Drawing & Revision # (or Attach photo below)
checkpoint-status |  |  | checkpoint | Service type referenced
text | 3d2be6e2-77cf-5ff0-a4bc-01b59e6adc72 |  | textbox | Service Type
checkpoint-status |  |  | checkpoint | Photo Records completed and attached below
checkpoint-status |  |  | checkpoint | Pipe Material Correct
checkpoint-status |  |  | checkpoint | Testing completed and referenced/attached below
text | 71b59db6-508e-5e59-94de-a2e71a56b293 |  | textbox | Testing Results
checkpoint-status |  |  | checkpoint | Water Disinfection Inspection complete
text | 09f26c40-30dd-5ca5-9d52-70b46b1e8471 |  | textbox | Inspection carried out by
checklist-flat |  |  | checklist | Penetrations |  |  |  |  | Yes | Penetrations Checklist | 6b579c9f-c007-4330-b060-bb7a3787a036
checkpoint-status |  |  | checkpoint | Set out and alignment
checkpoint-status |  |  | checkpoint | Materials types
checkpoint-status |  |  | checkpoint | Inspection Prior to concrete pour
checklist-flat |  |  | checklist | ITP 005 – Fixtures & Fittings |  |  |  |  | Yes | ITP 005 – Fixtures & Fittings | 91ea5607-5695-46d6-96ba-2f4022778ecc
checkpoint-no-status |  |  | checkpoint | Spec. Ref: CRPP-UML-SPE-HY-SI-001-1
text | fab6593e-b614-4229-88b3-b34797ed1d07 |  | textbox | Drawing Ref:
text | b159356d-2097-4bdf-be17-54784a599a03 |  | textbox | Service & fitting types:
checkpoint-status |  |  | checkpoint | Correct items installed
label | 543b2b4d-4b8e-49ff-af18-a1a9ec2c73c6 |  | note | Acceptance Criteria / Reference: As per approved shop drawings
label | 012b21cf-aebc-49f9-ba64-e3af9db5daf1 |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Items are of high quality
label | 985fc945-2f42-4897-afd9-ba2c8fdc6d1e |  | note | Acceptance Criteria / Reference: No apparent damage - free of cracks, chips, crazing or other defects.
label | 8947989c-4ec2-496d-bcad-801d06890da9 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Sealant
label | 2223b187-c1d3-414b-af8a-8301601ae775 |  | note | Acceptance Criteria / Reference: Sealant is neat. Correct type, colour and volume.
label | 9995a072-05cb-4b53-838d-cfe3eadffb8a |  | note | Inspection Type: N
label | b4b12dd5-d231-4fb8-ac71-80d8196897bd |  | note | Comment: Cell fixture sealant by others
checkpoint-status |  |  | checkpoint | Fittings installed straight
label | 74becc56-88b6-4fd2-8db1-092693494355 |  | note | Acceptance Criteria / Reference: Visual inspection
label | f8ccb385-f8e2-4c01-b4ff-1412880f5fe7 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Access panels are installed
label | ff2d3de1-52e8-4d01-8512-ce08ae46cfa5 |  | note | Acceptance Criteria / Reference: As per approved installation drawings
label | 247b9b40-59de-4e63-b8d1-a775d17ee120 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | WCs
label | ad6d5b27-20a3-4c5f-bfb6-07d02ae7f867 |  | note | Acceptance Criteria / Reference: Fixed with levelling brackets after floor installation, seat lid secure
label | 6db62e02-8dd7-4c96-95c1-c6520607bc1d |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Items all operate correctly
label | af8c41ab-ac64-41f7-b5a9-f94c556d1b8c |  | note | Acceptance Criteria / Reference: Check each item for operation – hot and cold if applicable. No leaks.
label | f7408618-cd54-4f00-894b-bbf8479d20ad |  | note | Inspection Type: T
label | ab0f94e6-0f52-42ab-aa6d-d6544ff13263 |  | note | Comment: Refer commissioning plan for disinfection and flushing of mains, TMV commissioning and Cross connections Potable & Recycled water
checkpoint-status |  |  | checkpoint | Inspections carried out by
text | aac7f753-b37e-4481-8f73-e77b26fca50d |  | textbox | Name:
text | ef0f0b24-9edd-471f-9a23-a78e72704e0b |  | textbox | Organisation:
checklist-flat |  |  | checklist | Metal Detection On Site |  |  |  |  | Yes | Metal Detection On Site | cead93a4-bafa-40ab-b266-92c41419fc9a
checkpoint-no-status |  |  | checkpoint | Details
text | 239c6785-2c76-4e12-9348-45a3a220a536 |  | textbox | Drawing Ref:
text | 26b6284a-e73b-415f-9233-ae3458728abf |  | textbox | Service & fitting types:
checkpoint-status |  |  | checkpoint | Metal detection on site
label | f88bfc2a-c393-4a37-a1b6-7a633671c44f |  | note | Acceptance Criteria: No Metal Collected or All Metal Collected
checkpoint-status |  |  | checkpoint | Final Sign-Off
text | 5e9656b9-4a06-4787-ae14-934eaea64ff7 |  | textbox | Name:
text | 1c5b01a6-8ad8-4207-91e4-e1a3099ba79a |  | textbox | Organisation:
checklist-flat |  |  | checklist | ITP 002 – Reticulated Systems In Ground |  |  |  |  | Yes | ITP 002 – Reticulated Systems In Ground | e78d5284-8f99-435b-94a6-2bb4afa6f074
checkpoint-no-status |  |  | checkpoint | Spec. Ref: CRPP-UML-SPE-HY-SI-001-1
text | 9a2adfdd-608d-4a05-9913-57a1d5a2bc53 |  | textbox | Drawing Ref:
label | 4a6b6f4b-5cd6-4306-92a0-08f870bb6d29 |  | note | Service Type:
boolean | 809a80eb-929f-42fc-8697-6a597751ab0e |  | tickbox | Cold Water
boolean | 1c7b8cc9-341b-4564-a541-e95eac77169f |  | tickbox | Recycled Water
boolean | 262b1dcb-fe7b-43d5-820d-3eb93cf9d81a |  | tickbox | Gas
boolean | c7d6af5b-aa0b-4880-9be9-b42f207dd257 |  | tickbox | Fire
text | 825dae78-d0f5-4981-aedb-f23a202bc3d8 |  | textbox | Other:
checkpoint-status |  |  | checkpoint | Set out and alignment
label | 32dce072-5e80-419d-a59e-a3c0a865c704 |  | note | Acceptance Criteria / Reference: Approved Shop drawings
label | 1fa8aae3-1e37-4d68-a082-df53d49cde12 |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Inverts and grades
label | 6889aed4-44a1-40c3-aa0b-0c884c3fd641 |  | note | Acceptance Criteria / Reference: Approved Shop drawings
label | 1c8598ec-5acb-4252-8218-ee137624d2ef |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Pipe bedding material
label | 263fc843-a490-4fcd-8b13-0a340418fc10 |  | note | Acceptance Criteria / Reference: As per specification
text | 8dc9d75c-540c-4818-bcc6-6151c659e4de |  | textbox | Specification:
label | db1095a4-a611-4f69-ae17-13b031f9f45b |  | note | Inspection Type: N
label | 33c0c824-76c2-4005-a592-cedd32b7f724 |  | note | Comment: CST By Others
checkpoint-status |  |  | checkpoint | Pipe material correct
label | 0cf6bfe8-f6cb-406c-96fd-8a121c84ae59 |  | note | Acceptance Criteria / Reference: As per approved installation drawings. PN 16 MDPE Butt Welded Joints / Copper Tube Type B under Buildings
label | 2d0820a0-9c75-4229-bfad-d3bb0dd132e5 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Electro fusion/Flange Joints
label | 9cf06809-a25a-419d-98eb-6da08e22e6b0 |  | note | Acceptance Criteria / Reference: Visual check on joints
label | 7c6f0fd6-7fae-4e24-baab-a183e439e476 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Inspection & testing prior to Concealing
label | 8b2cc3a3-3a70-4d11-9b0f-5ffe63c35dfa |  | note | Acceptance Criteria / Reference: Pressure test completed per AS3500
label | eecd616b-36b9-4180-a055-41431f49a39c |  | note | Test Type:
boolean | 1724161a-a328-4185-af94-4a99442bfefa |  | tickbox | Water
boolean | 125b4fbd-81d5-4bed-b7dc-33605efa3657 |  | tickbox | Air
boolean | 847f351b-82c2-47aa-89d1-99bbb7e75aac |  | tickbox | Nitrogen
text | cbb41993-a2ca-4d82-a14d-6545f7a7c729 | Hidden property width:100 | textbox | Pressure: |  |  | kPa
text | 58a6507f-3e8d-484a-b7eb-2abac0337f6e | Hidden property width:100 | textbox | Duration:
text | 8f3793b7-2716-46c8-8e40-bc4863a9fc4c | Hidden property width:100 | textbox | Gauge Number:
label | 17020dda-81a6-450f-ac9a-add3011f789c |  | note | Inspection Type: H, T, W
label | efa6f19b-eea5-4255-87aa-fca145d67868 |  | note | Comment: REF TEST CRITERIA
label | d60ee962-786a-4b6d-b1fc-9afb8a118cac |  | note | Water:1 ½ times the working pressure or 1500kPa.
label | a57bddfc-21fd-4d07-a6cf-0b7b7937149e |  | note | Fire: 1 ½ times operating pressure or 1700kPa whichever is greater
label | e0942642-12d8-4fa4-8187-da7c37182f8e |  | note | Refer commissioning plan for disinfection and flushing of mains
checkpoint-status |  |  | checkpoint | As Built
label | 9965fbe3-35c9-4208-a4ec-c095c736d9f5 |  | note | Acceptance Criteria / Reference: Survey as installed works and update AS Built
checkpoint-status |  |  | checkpoint | Backfill trenches
label | 454b863e-e37f-4956-b3f1-5182a06a25a6 |  | note | Acceptance Criteria / Reference: Existing material used for backfill or approved alternative (details in comments)
label | f0847940-5288-49a5-a81c-322babe4e515 |  | note | Inspection Type: N
label | ceee070d-9ab3-4b60-9d09-684455f51072 |  | note | Comment: CST By Others
checkpoint-status |  |  | checkpoint | Compaction and compaction testing
label | b63860ae-29c3-465f-9361-dc0a522b97fe |  | note | Acceptance Criteria / Reference: Stabilised sand N/A, Landscape areas N/A
label | 68c0eb81-ad6d-46b7-8d38-f6c750774469 |  | note | Inspection Type: T
label | ebe7ab9f-9419-4003-a7dd-2c4caf0df7de |  | note | Comment: CST By Others
checkpoint-status |  |  | checkpoint | Photo records
label | 040b304b-74c6-4b34-9879-bc59c94fe244 |  | note | Acceptance Criteria / Reference: Photo records during installation works. Attach reference drawing
label | c1882a32-dc74-47cd-8ad7-d4856871141f |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Inspections carried out by
text | d2766a06-263b-4b05-bba9-79f1d47dab93 |  | textbox | Name:
text | cad5bf5e-df54-485f-b105-dfb1c6564e21 |  | textbox | Organisation:
checklist-flat |  |  | checklist | ITP 003 - Drainage Above Ground |  |  |  |  | Yes | ITP 003 - Drainage Above Ground | ecd8c23a-0b4f-4d45-ab8e-6c4daf5d5fd9
checkpoint-no-status |  |  | checkpoint | Spec. Ref: CRPP-UML-SPE-HY-SI-001-1
text | 6252a774-06fe-475c-876c-b9c49e1cc47d |  | textbox | Drawing Ref:
label | e87c2106-57dc-4c18-bdf1-749f3d40e6c6 |  | note | Service Type:
boolean | de1b2878-b8d4-48b1-be10-3916d6f9ccd8 |  | tickbox | Stormwater
boolean | 2830d7af-cdc5-4f52-98e0-82a19084728e |  | tickbox | Sanitary Drainage
boolean | d1807a76-191a-4f18-8a25-ad50f142750b |  | tickbox | Trade Waste
text | 6f2177c9-a728-490d-8a40-37fdb397b6a6 |  | textbox | Other:
checkpoint-status |  |  | checkpoint | Set out and alignment
label | fc81026d-cc6a-46d2-aa8c-855b7b8f814c |  | note | Acceptance Criteria / Reference: Approved Shop drawings
label | 189ec6f3-61e1-4e73-b5fa-d17e66427c87 |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Inverts and grades
label | 2385991b-8ac0-4d7a-8016-8bb945c98ecf |  | note | Acceptance Criteria / Reference: Approved Shop drawings
label | 23b1e4fc-755d-42db-96a0-7a209bfda144 |  | note | Inspection Type: H
checkpoint-status |  |  | checkpoint | Brackets installed correctly
label | 0074d503-32af-43a0-b629-4af43ea59ee3 |  | note | Acceptance Criteria / Reference: Bracket spacing as per AS 3500
label | 86ee7532-ecc3-43e2-9818-fe50641295a6 |  | note | Inspection Type: N
label | 3c757fea-7158-481b-ad06-8e57d2d9d0d8 |  | note | Comment: CST By Others
checkpoint-status |  |  | checkpoint | Pipe material correct
label | 0286dc65-fefd-4332-9f12-5c0db991019e |  | note | Acceptance Criteria / Reference: As per approved installation drawings.
boolean | a9a569bd-5603-4be7-9fe2-7b04a8846268 |  | tickbox | PVC
boolean | dae97151-a8cf-45bb-b5aa-ffb113f82570 |  | tickbox | HDPE
text | 00306b01-5958-4d58-8202-34dd394998fb |  | textbox | Other:
label | 02afed45-64fb-4ae7-bb7b-e5e563085252 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Inspection & testing prior to Concealing
label | 937a3288-b197-400a-b442-dc8c8db3ba59 |  | note | Acceptance Criteria / Reference: Hydrostatic test completed
label | 0683772b-bd56-44d6-9e78-d1e6cce74483 |  | note | Air test completed
label | ff3b5081-490b-4b6f-be86-59e28ef8881f |  | note | Test date recorded on stack/system
label | 0c045baf-f57c-44e4-b0cb-24251ffaf595 |  | note | Inspection Type: H, T, W
label | 6bdfadb8-45a6-4ffb-b0c0-93c198a9c30d |  | note | Comment: Nominate test criteria; Air test to 30kPa, minimum of 3 min
checkpoint-status |  |  | checkpoint | Pipework labelled
label | 0771deea-da72-48f3-8ceb-32907104afb7 |  | note | Acceptance Criteria / Reference: As per AS 1345
label | 53eb2835-1a48-49dc-8d8a-beb523259563 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Floor waste riser length
label | a8a8ec9b-d69f-463c-a88a-dd24a88ff87d |  | note | Acceptance Criteria / Reference: Check not to be greater than 600mm from water level to FFL
label | 37c5a023-13ca-48bf-9a7c-9f4e3f52261d |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Heat Trace Installed to trade waste
label | 06a1880e-4e83-49f1-ae36-6fe394fac9d4 |  | note | Acceptance Criteria / Reference: As per installation drawings, if required
label | 06094fe3-6332-4834-91be-44cbfbd8434c |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | Acoustic lagging
label | e4d51635-0a7d-4305-a595-04fd70fc7f76 |  | note | Acceptance Criteria / Reference: Secure and full coverage
label | 01ea4840-78fd-4550-8d47-fef67c46b2e7 |  | note | Inspection Type: N
checkpoint-status |  |  | checkpoint | As-built information recorded
label | 6318c399-0ce2-41ac-a172-76a3b705f5db |  | note | Acceptance Criteria / Reference: Recorded on shop drawings as required prior to concealment
label | d1184df5-7a36-4908-85ae-3802f83c9fcf |  | note | Inspection Type: S
checkpoint-status |  |  | checkpoint | Inspections carried out by
text | 78ccc910-f6b3-43bf-908b-0beb094d213d |  | textbox | Name:
text | 16e2652b-bb51-4173-8e2d-d00f7118dd72 |  | textbox | Organisation:
checklist-flat |  |  | checklist | Document Attachment Checklist (V.081021) |  |  |  |  | Yes | Document Attachment Checklist (V.081021) | f4f611b2-57ac-4cc1-8931-cad02b8bbd63
checkpoint-status |  |  | checkpoint | Documents attached for reference - Pass once attached