## ITP Cover Page
Northern Access Road and Carpark Utilities Inspection and Test Plan
Project: Tauriko Enabling Project
Number and Revision: DN1210-SP2 - 011-004 - Rev 0
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Tauriko Enabling Project |  |  |  |  | ITP Number: |  |  | 011-004
Project Number: |  |  | DN1210-SP2 |  |  |  |  | ITP Status: |  |  | Approved- IFC
ITP Description: |  |  | Northern Access Road & Car park utilities |  |  |  |  | Revision: | 1000 |  | 0
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 232735.02-WSP-DR-UTI
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | SH29 Tauriko West Enabling Works Contract No.NZTA8287 Section 25
Quality Specified: |  |  | ISO9001:2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft | 2025-03-02 |  | Cordelia Girdler-Brown & Nick Adams | [5 empty] | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) |  | QM | QA Manager / Rep
[10 empty] | I | Inspection |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | NICK ADAMS |  |  | #VALUE! |  | 19/02/2025 | Downer PM |  | NICK ADAMS
Downer QM |  | CORDELIA GIRDLER-BROWN |  |  |  |  | 31/01/2025 | Downer QM |  | CORDELIA GIRDLER-BROWN
Client (If Applicable) | [7 empty] | Client (If Applicable)

## ITP Master Body
Northern Access Road and Carpark Utilities Inspection and Test Plan
Project: Tauriko Enabling Project
Number and Revision: DN1210-SP2 - 011-004 - Rev 0
Item No. | Inspection and Test Point | Detail | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Testing Quantity Required (based from schedule qtys) | Verification Activity |  | Downer Conformance of Compliance Signoff
[7 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 3 – PRE-CONSTRUCTION HOLD POINT - MATERIAL, PERSONNEL AND THIRD PARTY APPROVALS (P&G / ESTABLISHMENT)
3.1 | GENERAL
3.1.1 | Trench Profile | Tolerance of +/- 100 mm of the planned horizontal alignment and the maximum deviation shall be 1 in 20 in both the horizontal and vertical planes. | Survey Set out | PS 25.13.2 a (1) | Survey Data | Prior to Construction Review existing service location drawing supplied by WSP. | H | ENG
3.1.2 | Underground Services | Pothole all services within traffic management prior to commencement of trenching. Accurately record the location and reduced level of each service and forward Engineer. | Surevy Data/Existing utilities Drawings | Appendix V | Survey Data | Prior to Construction Review existing service location drawing supplied by WSP. | H | SE
3.2 | MATERIAL TESTING
3.2.1 | Bedding and Overlay Material: sand | Material grading:PSD | Free of larger sharp particles conforming to GAP 7 | PS 25.13.2 g) & h) | Delivery Dockets/Material Certification | NA | HP | ENG
3.2.2 | Material grading: Materials (GAP20/AP20) | Material grading:PSD | Sieve Size % Passing 19.0mm 100% passing 13.2mm 80-95% passing 9.5mm 64-76% passing 4.75mm 37-58% passing 2.36mm 30-40% passing 1.18mm 18-28% passing 0.600mm 12-22% passing 0.300mm 6-14% passing 0.150mm 2-7% passing 0.075mm 0-3% passing | PS-21.5.7 PS-21.7.2 Table 21.2 | Lab Test Report NZS 4407.2015 Test3.8.1 | 0-400m3 2 Test 400-1500m3 3 Test 1500-4000m3 4 Test >4000 1 Test Additional 1000m3 | HP | ENG
3.2.3 | Weathering index: Materials (AP20) | Weathering index: | AA to CA | PS-21.5.7 PS-21.7.2 Table 21.3 | Lab Test Report NZS 4407.3.11 | Prior to construction - 2 test per source | HP | ENG
3.2.4 | Crushing Resistance: Materials (AP20) | Crushing Resistance | >100kN | PS-21.5.7 PS-21.7.2 Table 21.4 | Lab Test Report NZS 4407:1991 Test.3.10 | Prior to construction - 2 test per source | HP | ENG
3.2.5 | Material grading: Materials (Gap65/AP65) | NZS4407:2015, Test 3.8.1 - Particle Size Distribution | No Particles >200mm Maximum fines 10% passing 75micron sieve | Appendix XVIII PS 16.5.5 Appendix V | IANZ Accredited Report | Stockpile Size (m3): 0-400 - 2 tests 400-1,500 - 3 tests 1,500-4,000 - 4 tests >4,000 - 1 test for each additional 1,000m3 Results to Engineer 2 wks before importing | HP | ENG
3.2.6 | Weathering index: Materials (Gap65/AP65) | NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate | AA, AB, AC, BA, BB, or CA | Appendix XVIII PS 16.5.5 Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP | ENG
3.2.7 | Crushing Resistance: Materials (Gap65/AP65) | NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load | >100KN | Appendix XVIII Appendix V | IANZ Accredited Report | 2 Tests Per Material, Per Source Results to Engineer 2 wks before importing | HP | ENG
3.2.8 | Materials Approvals | All works and materials are to comply with the National Code of Practice for Utilities Operators' Access to Transport Corridors, and Individual Utility Providers Requirements | Prior to Commencement and throughout construction | Project Specifications | Utilities Providers Approval/Material Certification /Delivery Dockets | Each Delivery to site | H | SE
3.3 | MATERIAL DELIVERY
3.3.1 | Pipe and fittings. Ducts | Duct Pipes shall be of the size, material and class nominated in Drawings. Ducts shall be high impact uPVC Duct colours shall be to local authorities requirements. Duct colours for the different Utility Structures must be in accordance with the guidelines. | Duct Pipes shall be of the size, material and class nominated in Drawings. Ducts shall be high impact uPVC Duct colours shall be to local authorities requirements. Duct colours for the different Utility Structures must be in accordance with the guidelines. | PS 25.13.6 b) | Delivery Dockets/Material Certification | Each Delivery to site | H | SE |  |  | Duct details will be instructed by service providers.
3.3.2 | Bedding material | Free of larger sharp particles conforming sand | Free of larger sharp particles conforming to sand | PS 25.13.2 g) & h) | Delivery Dockets/Material Certification | Each Delivery to site | H | SE
3.3.3 | Backfill Material | Under roads, driveways and footpath - refer to pavement section for appropriate materials and layer thickness. Under berm or grass areas - site Won materials to be approved by Engineer or GAP65 to be used if site material does not meet Specs | Comply with Project Specifications | PS 25.13.4 a) | Delivery Dockets/Lab Test reports | Each Delivery to site | H | SE
3.3.4 | Pits Covers | Jointing and pulling pits shall have slip resistant surfaces complying with AS/NSZ 3661-1-1993. the cover set load rating shall be in compliance with AS3996. | Class A-10kN loading - footways and areas only accessible to pedestrian and cyslists. Class B- 80kN loading - footways that may be mounted by vehicle or livestock and light tractor paths. (Light duty) Class C- 150kN loading - grass verges or other areas open to slow moving commercial vehicles such as tractor mowers etc (medium duty) Class D-120kN loading - Carriageway of roads and areas open to commercial vehicles (heavy duty) | PS 25.13.6 c) AS/NZS 3661-1- 1993. | Material Certifications. Delivery Dockets | Each Delivery to site | H | SE
SECTION 4 – CONSTRUCTION ACTIVITY
4.1
4.1.1 | Trench Excavation | To be excavated to within a tolerance. Not more than 100 metres of trench associated with each site shall remain open at one time. | +/- 100 mm of the planned horizontal. The maximum deviation shall be 1 in 20 in both the horizontal and vertical planes. Less than 100m | PS 25.13.2 a) i | Survey | Each Cable | M | SE
4.1.2 | Unsuitable Materials | All confirmed unsuitable material shall be excavated down to suitable materials. | Dig Down to Get Suitable Materials or get Engineers Approval. | PS 25.13.2 b) ii | Checklist | Each Cable | M | SE
4.1.3 | Foundation Compliance | It shall be de-watered prior to installation of bedding material. If the bottom of the trench is naturally occurring rock, or has stones, gravel or other sharp material in occurrence | 50mm granular layer shall be laid and compacted before the bedding layer is laid. | PS 25.13.2 c) and g) | Checklist | Each Cable | M | SE
4.1.4 | Bedding | The floor of the trench shall be clear of any obstacles and shall be as flat as possible. | Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench. | PS 25.13.2 g) | Checklist | Each Cable | M | SE
4.1.5 | Installation of Ducts | If more than 2 ducts are being placed. | Must have 50 mm bedding material between the two ducts. | PS 25.13.7 b) iii | Checklist | Each Cable | M | SE
4.1.6 | Draw Wires | A draw wire shall be intalled in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting. | Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load. ≥20 years design life. The ends of draw wires shall be made fast within the pits and be secured to the duct plugs. Blue colour wire | PS 25.13.7 e) ii to iv | Checklist | Each Cable | M | SE
4.1.7 | Caps | All duct ends shall be capped | Capped ducts | PS 25.13.7 e) v | Checklist | Each Cable | M | SE
4.1.8 | Warning Tape | Warning tape to be placed above services. | Warning Tape to be placed no more than 300mm above the topmost duct | PS 25.13.7 b) iii & f) | Checklist | Each Cable | M | SE
4.1.9 | Overlay | 99 mm minimum sand placed on top of duct. No mechanical compaction will caarry out till 300mm drom top of duct. | 100 mm minimum sand placed on top of duct. | PS 25.13.7 b) ii | Checklist | Each Cable | M | SE
4.1.10 | Backfill | GAP65 to be used if site material is not approved. | Clegg Test every 200mm compacted layer of GAP65 clegg >28CIV | PS 25.13.10 a) modified | Lab report | Every 10m | H | SE
4.1.11 | Pit Installation Location | Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid . | Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas. When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side. When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side. | PS 25.13.8 a) i and ii | Checklist | Each Pit Location | H | SE |  |  | If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
4.1.12 | Pit Installation Bedding | Bedding with 150mm compacted GAP20 hard-fill coverd with 20mm compacted sand. Pits shall be carefully lifted into place and lined up with the ducts to penetrate the chamber. | 150mm compacted GAP20 hard-fill covered with 20mm of compacted sand | PS 25.13.8 d) | Checklist | Each Pit Location | H | SE |  |  | If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
4.1.13 | Pit Installation Sidefill concrete | Plactic pits shall be cast into the ground with 150mm concrete surround | Plactic pits shall be cast into the ground with 150mm concrete surround | PS 25.13.8 d) | Checklist | Each Pit Location | H | SE |  |  | If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
4.1.14 | Pit Installation Backfilling | Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts in 200mm layers of GAP 65. | Min 92% compaction rate and Average of 95%. | PS 25.13.10 a) modified | Checklist | Each Pit Location | H | SE |  |  | If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
4.1.15 | Pit Installation Concrete | Top 300mm of pit shall be concreted around with a with of 150mm with a 20MpA concrete. | 20 mPa | PS 25.13.8 d) iv. | Concrete Dockets | Each Pit Location | H | SE |  |  | If pits are installed by utility service providers, service owners/operator’s requirements and standards will prevail.
4.1.16 | Pit Installation Clean up | Clean out all pit after completion of the work | Pit are free of dirty, mud,water and foreign materials | PS 25.13.8 e) | Checklist | Each Pit Location | M | SE |  |  | If pits are installed by utility service providers, service owners/operator will clean the pit.
4.1.17 | Survey As Built | As Built every ducts joint before backfill | Completed as per drawings | Standard Practise | Survey | On going | H | PE
SECTION 5 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
5.1 | AS-BUILTS
5.1.1 | Survey As-Builts | Quality Check on New Works based on the tolerances in RITS | Meets spec and thickness requirements as per drawings | PS-21.7.7 | Red pen markup only | Post works completion of a lot | H | SE