## Master List Templates
Id | Type | Name | Values | Prompting Name
c5dc7d7c-df99-5ec2-a589-b436df406a75 | checklist | 010SAF_08 SWMS |  | 010SAF_08 SWMS
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
cbaa5304-d926-5145-abea-643403fc7075 | note | 003G Using Platform Ladders
4c0dcfe7-d8a0-5008-bd8b-d7bc54f1ac2a | note | 004G Inhalation of Respirable Crystalline Silica
1117a6d0-9a4c-5b98-b403-d22a7b5ad3a6 | note | 005G Working at Heights
68979298-f5d8-548e-baec-8741d208ed87 | note | 006G Working at Heights Rescue Plan
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
b4e0d11c-383a-5193-a4d8-06886c652d7b | note | 019T Pressure Testing of Pipework
543f3f86-57b8-5b16-b786-9b1a07dba3bc | note | 020T Sprinkler System and Associated Pump Test
e8307916-4807-52bf-87e5-102669e43c3f | note | 021T Hydrostatic and Flow Testing of Pipework
b9ed5514-0cad-5767-9bc2-787d09c4b91b | note | 022T Fire Rating
3eda0a35-e17c-5ffa-8f13-550cbe45fa28 | note | 023T Fire Alarm and Emergency Warning Systems Testing
6a966737-d7b0-592b-adaf-4fd6c5c1ce28 | note | 024T Commissioning and Testing of Hydrant System and Booster Area
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
5d11d398-a985-5a6c-aeb6-18ee293dc7c2 | note | 008I Removal of Existing Fire Alarm Systems and Devices
92d6eeb4-8277-5022-83a0-fc89644f8bed | note | 009I Removal of Pipework Fittings
52103321-2daf-5ff5-83c8-2ade86fd2490 | note | 010I Fire Alarm and Warning System Rough-in
8205c84e-07ea-575b-bae8-d3015acb0b02 | note | 011I Fire Alarm and Warning System Fit-off and Installation
884a1c0d-249f-5a69-b8f2-2e03f9760652 | note | 012I Installation of Fire Alarm and Warning System Cabling
61c0ba51-1491-512b-936c-ac2c0f143740 | note | 013I Installation of Pipework and Fittings
c29e79e2-249c-55ba-b869-187073053c35 | note | 014I Installation of Fire Control Panel & Emergency Warning Systems
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
c16f635a-3bca-5dac-a689-9e680d369d3b | checklist | ASSESS-001 Risk |  | ASSESS-001 Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
72f2e306-5d72-5abb-8da1-c93ffe754371 | note | Use this form to document the risk management process for a single generic hazard.
c973ae1a-adbf-593a-9b40-b65190b6dcfe | textbox | Work Area:
c0fe0e0a-a9b7-57c5-a8c8-a0ab295604a6 | date | Date of Assessment:
0e56de85-9875-5cd2-9244-81e1e1deb32d | textbox | Name of Assessor(s):
a23cb753-93b5-5114-860e-93a0592e96f4 | textbox | Position(s):
ccdf75f8-024b-54d9-8a66-2aa0bb78f88c | textbox | Incident Ref. No:
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
0108eee0-212f-54ad-a619-d6f1332feec2 | textbox | Describe the Hazard:
bfd5195d-87aa-5c40-ac91-f0b3a6ea86bc | checkpoint | Risk Assessment
79f36614-2009-5aa8-8970-3b5fed35e949 | textbox | What harm could the hazard cause?
eb59b0a2-5709-5763-9f45-742f4d0ace4c | textbox | What is the likelihood of this happening?
93b1cffd-dc53-5d67-a367-a44bc2195093 | textbox | Persons at risk:
b934ad05-1324-5895-90da-2d07f5fac002 | textbox | Existing control measure:
4bfa7635-78a2-5657-8fb4-ce164b694a02 | textbox | Consequence:
16d731a9-e8b8-558f-85cb-dfbad7fe50b5 | textbox | Likelihood:
f2092f95-afce-5d99-9a72-a29c8b4faa3a | textbox | Outcome:
32563b01-0feb-5e94-999f-2bc4f92e2c20 | checkpoint | Control Measures
b775ca3c-f515-5603-a2bf-41f6a3c0832a | textbox | Elimination:
dedc9731-78cc-577a-bd23-40e4c771b74f | textbox | Substitution:
12bc024a-c90e-5886-ac2d-d2d7b5a324b6 | textbox | Isolation:
bfd397df-9038-5f92-918d-7f965ab842e5 | textbox | Engineering:
300d31ac-b056-547f-9d49-8e31ab4ebe3f | textbox | Administrative or PPE:
3a752e96-005c-540c-9fa4-0fcd922583a7 | textbox | Preferred control option:
71245745-e635-5d28-b0f1-51a28405fcc8 | checkpoint | Implementation
6bfba640-dbc9-5e89-8bcc-20f6e176a15b | textbox | Associated activities:
a5d13add-fb1f-53b8-a898-a80a4ea908fc | textbox | Resources Required:
14d671f3-f25f-55de-8015-a25ca77191b4 | textbox | Person(s) Responsible:
154b17d1-0967-5ad4-bcda-0d5f566e0b97 | date | Scheduled Review Date:
7717528b-ba68-53aa-a357-393c48e0a282 | signoff | Signature
bda1b2aa-a2eb-5eeb-86c9-93b0d73f9c32 | checklist | ASSESS-002 Manual Tasks Risk |  | ASSESS-002 Manual Tasks Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
88191c58-e7fd-5040-8c4f-a61353b1fa9b | note | This assessment identifies how to manage the risks associated with hazardous manual tasks and control the risks of workers being affected by musculoskeletal disorders as per the code of practice under section 274 of the Work Health and Safety Act 2011 (the WHS Act). Use this form to help identify and manage risks of hazardous manual tasks.
5de6db16-8419-5d70-982f-4f01e00b83e6 | date | Date of Assessment:
03726dfa-63a9-5264-ae5c-f1e5ed73786e | textbox | Name of Assessor(s):
0e73d8d5-8bd4-5da5-9be3-cd09dee4079f | textbox | Position(s):
2420a771-d981-5582-ab3e-1606f889d4a8 | textbox | Incident Ref. No:
58267725-2c6f-55fe-83b6-0579eb36ea4e | checkpoint | STEP 1 What is the Manual Task?
b4e39399-6aaf-5064-aa51-edba0c4bb3b7 | textbox | Relevant worker(s) to consult:
ec550514-2041-56cb-a872-dde5a04b2a9b | textbox | Name of task or activity:
d552f0c7-9f1c-544c-803d-0e354d2cbe32 | textbox | Location where task occurs:
1c593298-ebf6-58a6-912f-235d066a30f0 | textbox | Who performs the task:
c7407722-5f98-5535-8300-e44bb8050b50 | textbox | General Description:
bf2b5766-0a58-58a5-9304-cb818f3230f5 | checkpoint | STEP 2 Is the Manual Task hazardous?
6bb09e7b-27a6-5223-bed6-25d0a7d4fea7 | note | Hazardous manual tasks can result in musculoskeletal disorders (MSDs) such as sprains or strains. Work through the following to determine which postures, movements and forces of the task pose a risk.
bd58ce33-5df7-5218-8cbf-74ddd6fec3a6 | note | 1. Does the task involve any of the following risk factors?
6c428ef3-a139-5948-b918-b2cd5c79aab2 | button | Repetitive movement | Yes, No
c643118f-537d-5397-8dbc-0945effc47a5 | button | Sustained or awkward postures | Yes, No
99a8e050-9618-5a9e-b03a-54889f2c1a73 | button | Repetitive or sustained forces | Yes, No
52d48251-f2aa-5bc4-b5d7-81e34c90b21b | note | 2. Does the task occur over a long time?
3c2e0c88-3344-5f4d-b1b7-7ae982a3239c | button | More than a total of two hours over a whole shift? | Yes, No
99957572-003c-515e-858c-ada07486271f | button | Continuously for more than 30 mins? | Yes, No
470df989-f349-5aed-a3e6-cd8dad4b2b28 | button | 3. Does the task occur over a long time? | Yes, No
be018380-5737-53b0-ab65-86fd870c1b69 | button | 4. Does the task involve vibration? | Yes, No
c05f7811-9b10-50f0-a9cd-0e4f533307ba | note | 5. Is there a Risk? The task involves a risk of MSDs (e.g. sprain and strain) if you answered ‘yes’ to either:
48530b6b-e927-5de8-aba8-80b78e0a6cdc | tickbox | Question 1 and 2 (above)
f8843d5c-4097-527a-a5c6-307dfcaac8e1 | tickbox | Question 3 (above)
bc1162b7-b9ae-53ed-9038-72f314872e32 | tickbox | Question 4 (above)
ff0e3e57-1c0d-5ac9-8a29-86c71ad76106 | note | If you ticked anything in question in Question 5, continue to Step 3.
83ac9d16-4add-5de6-93fe-a6dd01595278 | note | Additionally, if you answered ‘Yes’ to Question 4 the task may be a risk and will require further investigation.
43bb97fe-9131-5be9-be82-2660ffb39a19 | checkpoint | STEP 3 - What is the source of the risk?
e1b8541b-b6a9-5e9d-b75c-6a64df4d8934 | note | These are the things that are causing the risk and may be changed to eliminate or minimise the risk.
835a163f-5e3b-5e47-8dd1-69e6362c9177 | tickbox | Work area design and layout: workspace available; design of workstation, furniture and equipment.
f5a4cad3-dae5-5c98-825e-d6c70fc9db51 | tickbox | The nature, size, weight or number of things handled in performing the manual task.
26463d22-6924-55a4-aa93-34431f4a9359 | tickbox | Systems of work (e.g. pace and flow of work; resources available; maintenance).
52408b07-baf7-56c1-bd10-fef07e00ace4 | tickbox | The environment in which the manual task is performed (e.g. flooring; obstructions; lighting; hot/cold/humid environments).
75306ffa-8cad-5fb5-8c60-4770efcfbc4e | checkpoint | STEP 4 - How do I control the risk?
eec83f82-aaa0-5a99-91e7-3399ae977068 | button | Can the task be eliminated? | Yes, No
0237db45-bc55-5611-b6e0-5fdfec114238 | button | Can you change what is causing the risk (the source)? (e.g. change the work area; alter the size of loads; use mechanical aids; manage environmental conditions; use adjustable equipment; implement preventative maintenance program). | Yes, No
052f0405-4586-5b50-ab81-928223e9fd40 | textbox | If 'Yes', provide detail:
b09fc82b-320f-5a0c-bf5b-e975eebdf51c | button | Is training needed to support the control measures? (Training needs to be task specific, noting that training in lifting techniques is not effective as a sole or primary means to control the risk of MSDs.) | Yes, No
82589687-d73e-5d91-a652-af546e0b8679 | textbox | If 'Yes', provide detail:
249717bf-db57-5fb4-b61b-9f7678983512 | checkpoint | Implementing Controls
4f3739d1-5413-58b3-bcac-3b8cfc769edb | textbox | Name of Responsible Person:
da874497-48bd-59ee-a40d-6fcd080d941e | button | Responsible for: | Approving, Implementing
f88c52db-91b3-5ae6-b2c0-bc3636126ccc | textbox | Name of Responsible Person:
eb6f4298-535b-5037-86fc-03f3282535fa | button | Responsible for: | Approving, Implementing
e771d6c3-7367-5c5d-a865-65e74337162e | textbox | Name of Responsible Person:
7e378c68-adcf-5545-a5d1-767f5aa43ae9 | button | Responsible for: | Approving, Implementing
e7b121d1-48a6-556a-8c0f-2e2afe0eb37c | textbox | Name of Responsible Person:
cd1ab814-71c7-5e5d-a2ce-8adae90c201a | button | Responsible for: | Approving, Implementing
89334ebf-57ec-5f05-8b4e-750b91a0dc81 | signoff | BY SIGNING I CONFIRM I AM AWARE OF MY RESPONSIBILITIES AS OUTLINED IN THIS RISK ASSESSMENT
1ac85fbd-c1e0-52f8-a16f-a7d8e29a8854 | checkpoint | STEP 5 - Review the Controls
124171fc-31fc-554d-ad9a-15f11fffdd73 | date | Evaluated on(date):
f99ca706-8a57-5441-97c0-265c36556675 | textbox | Name of Assessor(s):
a3c2db9f-aa0c-54fd-9746-64106a5607ee | button | Consultation undertaken with relevant workers and others? | Yes, No
3446072a-2a55-5392-b68e-b41c823605d6 | button | Have any other risks been created by the controls? | Yes, No
8857121a-aeb5-5aff-ae17-8db3cbf48613 | button | Have the controls implemented reduced the risks? | Yes, No
ce8820cf-b033-577e-938f-d3abae3dca03 | button | Can further controls be implemented to minimise the risk? | Yes, No
783332ff-f381-5872-a1d9-f0abd0db72ef | checklist | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment |  | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
daf7c8c0-f265-53b6-b089-18b4f9c9ed8d | textbox | Hazardous Chemical (product name):
5e40300f-d00b-54b4-a412-99b7d8d87e9e | textbox | Hazardous Chemical Reg Item No:
7167959e-0e37-52be-95ff-e77a351f2d9f | textbox | Use:
eec44df0-883b-5db0-a668-e111f5465eb4 | checkpoint | Nature of Hazard:
515ccb2f-5574-5f1b-af25-f0e017aec55b | tickbox | Toxic (Poisonous)
69117132-d710-50b0-87a2-fd6561a5cc6e | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
4fbbc003-7f0b-545d-82d7-85b1776097e4 | tickbox | Carcinogenic (Cancerous)
cf543727-8bf1-56d2-9505-f6d576dda93a | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
649e5f59-4e67-564e-831e-5816594e372a | tickbox | Teratogen (Harmful substance that could affect abnormal prenatal development)
78797bd9-40bf-5c2e-a9ea-5d4e13b691b4 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
32f85441-3499-51a3-96ec-4ce9d5c22585 | tickbox | Sensitiser (Reaction to an antigen, such as pollen)
76be498b-ffed-5b6c-964f-490a7ed77b12 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
84f10eda-8d41-5a98-9a47-07dcfd238f3d | tickbox | Mutagenic (Capable of mutating DNA, such as radiation)
e660e6d3-d724-5d0d-9b4c-3395061ef371 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
cefd1dd4-beda-5048-b933-ce6ee624521f | tickbox | Irritant (Inflammation of the skin, eye or respiratory system)
3c251afa-d2e4-5d96-9754-f71b101a14b0 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
5f371315-fde4-5a60-9d8d-bb5607875476 | tickbox | Flammability (The ease of which a substance will ignite, causing fire or combustion)
fb610737-61f7-59e5-8ffb-40e9869618be | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
c5299fc2-0138-5c3e-9df0-fdb6f6a23c55 | checkpoint | Risk of Injury
8d021389-9a67-50bd-8ec8-d4ab23272c6c | button | Risk of Acute (Short term) Injury: | High, Medium, Low
067e974c-26ab-5b2b-a523-3e6f322db22a | button | Risk of Chronic (long term) Injury: | High, Medium, Low
6adca422-e108-5631-9168-8f36735799d3 | checkpoint | Controls and Requirements
6024ac9c-b7fb-5c3b-ad6c-8c2a711574ad | textbox | Control Measures to reduce exposure i.e. change to a safer product, ventilate area, (P.P.E.):
e5a3f28a-3f2e-5b9d-9ecb-2131b9172fde | textbox | First Aid Requirements and Storage Requirements:
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
f6e6ad58-755a-5ec6-ac1a-b3db6c24bfc3 | signoff | The persons listed below have been consulted in this risk assessment, understand the hazards associated and agree to use the control measures identified above to carry out the works safely and in a manner which protects themselves, others and the environment.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
d0aabc79-7a66-528f-976e-31f5a7db0456 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT
0f842a4a-0919-569b-971e-2e2c5d887732 | checklist | ASSESS-004 Plant Risk |  | ASSESS-004 Plant Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5011c755-395d-598c-bc65-ea69efabb143 | checkpoint | 1. Competent Peron(s)
0f9c8869-f0da-5106-839e-4786717533c7 | note | This familiarisation checklist should be completed by a Site Supervisor or Site Foreman to verify that the workers involved in the operation of Plant Equipment/ Mobile Elevated Work Platforms (MEWP) can demonstrate their ability to understand and operate the MEWP functions in accordance with the manufacturers operating manual. This familiarisation checklist must be verified by a competent person who holds the equivalent licence/ ticket required for the type of Plant Equipment/ MEWP to be operated (e.g. Boom lift/ Scissor lift)
f271da4c-b28b-55ba-94ec-fb2366ef3e71 | textbox | Your Name:
81c7070d-ea73-5aa1-b27d-a3c6df78d484 | note | Your Licences / Tickets:
d4fed4a1-dc6a-51cc-95e7-77453dcf8995 | tickbox | WP High Risk
9f18f57a-c1e0-5148-a0a7-ce462b1752c0 | tickbox | Boom Lift
46dcb63f-cba8-5882-9eda-41f78c80fe76 | tickbox | Scissor Lift
f1dea7a3-b36f-5df6-b20b-200c5ad8f012 | tickbox | Vertical Lift
aca5c296-d8e0-5524-9f11-a0e19c74053d | tickbox | Other
bfbb29ee-ea73-5988-aeaa-9c12bf00a38b | textbox | If 'Other" please specify:
c06fe721-a6e8-585c-ad93-6752e11d8265 | checkpoint | 2. Plant/ MEWP Details
5bb2d4bb-8c93-50b2-8404-5fc607df9200 | textbox | Make and Model:
4e664c85-b026-5352-ad98-ea82ef93fc09 | textbox | Type (e.g. BL>11m, BL<11m, SL, VL):
6b0e5610-cf37-5886-aa78-b8bc2aea3ba0 | checkpoint | 3. Employee Competency
0eadcdb0-92c2-518f-ba01-947e2d35baba | textbox | Name:
f4d58f87-5c76-5305-b26c-73f6c3a7d8f1 | note | Role:
282b31ad-bb5c-506e-9255-57ccce8371ed | tickbox | Operator
cdebc586-0f38-5d64-a9fe-2342d28bae18 | tickbox | Spotter
27c75547-7741-5074-aee6-c9df015b6796 | note | Licences/Tickets Held:
d618df27-dcf3-59ae-b4f7-a48f5b8fc678 | tickbox | WP High Risk
9bc37b09-8d29-50e1-a000-2abd2e1247c3 | tickbox | Boom Lift
4be8c6ac-6115-5194-bddf-4201b5cd42e6 | tickbox | Scissor Lift
6f8c2cd6-aecd-5f6f-8b48-7ebfeda0db4a | tickbox | Vertical Lift
06ebc66d-119e-58a4-8c6d-3668b83861ad | checkpoint | 4. Employee Competency
f0264c4a-7eb5-5db8-a750-152fcca06091 | textbox | Name:
f580e6c9-141e-550c-8ea5-c402f30cbcfe | note | Role:
b7575d34-b341-5d85-a273-45ffc5195a43 | tickbox | Operator
99dcfdbe-a571-5889-9d5e-7927bd33502d | tickbox | Spotter
3ce21582-db84-54d1-bade-8e62cdfe6662 | note | Licences/Tickets Held:
fbe4657e-5e91-5e20-aed2-a3a5e96aaffe | tickbox | WP High Risk
f21fa9b2-342c-587c-a78c-2aa96de1183b | tickbox | Boom Lift
709f1ec5-0317-5694-9c76-b407660b8097 | tickbox | Scissor Lift
bec6edab-d633-5c0c-9835-c7257d402113 | tickbox | Vertical Lift
3ef8e758-7384-5d13-8fa3-292a5f04a9d8 | checkpoint | 5. Employee Competency
dcaefec8-c403-5081-8b80-459200592818 | textbox | Name:
d8c40a12-e727-5592-8007-7a11d0087ddd | note | Role:
6055f321-e03b-5b99-871f-8d6b343290fe | tickbox | Operator
5e3cc7d7-98ba-5331-948e-6f4bc1f772df | tickbox | Spotter
ddc9024d-3a3d-53f4-a86c-e23749678bfd | note | Licences/Tickets Held:
d1f50c41-2e5e-5742-acf2-fa8ffb9ea034 | tickbox | WP High Risk
ddf7513a-784c-5287-9fa7-95921a923c34 | tickbox | Boom Lift
e679bc79-5b31-5f33-93b4-976fb16f4cae | tickbox | Scissor Lift
4916b44b-0a47-59c5-ab27-b106e07e0951 | tickbox | Vertical Lift
0db35e59-5266-54bd-bc6b-7ababdb43cef | checkpoint | 6. Declaration (to be completed by competent peron(s) noted in Section 1.
6349f156-b2fb-5681-8b0d-6a998dee30c0 | button | All 'Operators' hold the appropriate licence/ ticket for Plant/ MEWP | Yes, No
afc0cca6-ce52-5bc8-9679-5aa2c6567d1e | button | All 'Operators' understand the operational controls and emergency functions | Yes, No
a4e370b7-0985-501f-b594-2d2b8a18d367 | button | All 'Operators' are aware of the logbook and pre-start requirements | Yes, No
50e6f422-c435-5d4c-9c6f-b5e886706923 | button | All Ground Support understand the emergency functions | Yes, No
fe9486b5-7f5f-5cad-aa8a-b043393548ad | button | All GM Fire employees on site have participated in an emergency drill | Yes, No
fc61ae32-fa2d-5b88-bc9b-ea135f5605e8 | button | All GM Fire employees have signed onto applicable SWMS | Yes, No
9899d9ec-b306-5aed-bbc5-b1347ea6537c | signoff | BY SIGNING I CONFIRM I HAVE ALL PERSON(S) LISTED ARE COMPETENT TO OPERATE THE LISTED PLANT/ MEWP ON THIS SITE.
9dbe7e71-e67f-56a4-ad73-11d76128125d | checklist | ASSESS-005 Confined Spaces Risk |  | ASSESS-005 Confined Spaces Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
fa1844af-9dc5-5cc7-ae06-3efe7ab7da90 | note | Use this form to document the risk management process for a Confined Space.
047d9ce0-506c-5911-88ae-eb4489730a52 | date | Date of Assessment:
58bd51a7-40fc-53ec-bbb3-059aface69aa | textbox | Name of Assessor(s):
a39e0cf0-68e8-5f45-9dfc-4331752dab2b | textbox | Position(s):
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
5379936e-c605-52b1-9b1d-5d12f9ef1b4c | textbox | What Hazard/ Risk is associated with the task?
3f36ef24-b734-53f9-8888-8bdaa6846ce7 | textbox | Planned control measure to remove/ minimize hazards/ risks
6e23280d-aa88-5e26-bd34-4e4e2e439c40 | textbox | What Hazard/ Risk is associated with the task?
df717095-dfa1-5189-922b-1b2d80ca3657 | textbox | Planned control measure to remove/ minimize hazards/ risks
b994028a-9c6d-5d06-8d9f-fe1e1328df9b | textbox | What Hazard/ Risk is associated with the task?
91262636-3152-51d2-92cc-8e15341c97cd | textbox | Planned control measure to remove/ minimize hazards/ risks
820ecd7a-d153-5a78-a9ce-2556724c1e1a | textbox | What Hazard/ Risk is associated with the task?
40c1128f-c57f-58ab-a46a-a4c01df54ea9 | textbox | Planned control measure to remove/ minimize hazards/ risks
8dbfa3cc-a3bd-52c3-8297-932a4d3bf207 | textbox | What Hazard/ Risk is associated with the task?
1aa8bc0e-3a7d-5f7d-a1d8-411e57f4c4bd | textbox | Planned control measure to remove/ minimize hazards/ risks
520f3973-2a3e-554c-9da3-fcd0d6905a7f | checkpoint | Review
6d7eac5e-08a0-5828-9fde-e03a95d84a0a | button | Does the Risk Assessment Identify that confined space work is involved? | Yes, No
e4ab41d8-1c4c-5b7a-b4ef-9846c5dc3f19 | note | If YES the Confined Space Work Permit MUST be completed
7adcb501-bd5a-5835-9207-da6d6a29efa4 | note | NOTE: EMERGENCY & RESCUE PROCEDURE: Where an accident occurs which requires that an emergency rescue be attempted, the standby/ rescue person is to immediately contact EMERGENCY SERVICES on 000 for assistance.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
7611f657-3e12-53bf-9a28-5d86548e5c24 | date | Scheduled review date:
946f9c2d-1950-57b6-981a-43e43c738227 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT.
af42f709-0045-5d54-8b91-cc87be09a8d9 | checklist | ASSESS-006 Job Safety |  | ASSESS-006 Job Safety
5e25be48-4354-51fa-a917-1881487cb8a0 | checkpoint | Client Details
ac2eedbf-7e5c-555e-8797-1ec0c141d165 | textbox | Client: i.e. Principal Contractor
9f910329-98ae-5f0f-82c8-648ec9c275c4 | textbox | Client Contact Name: Responsible Person(s)
dfaa6fa5-9e3e-5547-8898-cfa24654593d | textbox | Client Contact Phone:
1ed3b367-0507-5ad1-a9c3-ed917275cce4 | textbox | Client Contact Email:
bad8a559-d874-55eb-a218-4243f23c1f05 | checkpoint | Job Safety Analysis Details
d0cfcfc4-ba4d-5514-af5f-0a9a287b82ba | textbox | Work Activity:
8b0be918-ba64-5526-ba0c-35f39246364c | textbox | Location:
1eeeef73-97e8-5a10-8a6e-4461c2e69c1a | textbox | Who is involved in the activity?
359d373d-64aa-57b4-bf30-d80166729ad0 | textbox | Plant and Equipment used:
a30bcf82-f134-54e0-97c4-22d24775250d | textbox | Maintenance checks required:
b988e6f4-0d85-5ee5-98e8-9105f1b85558 | textbox | Tools used:
15b3990e-82e8-552a-ad9c-380568b46ac3 | textbox | Materials used:
793efd9b-c8f9-5043-8c25-3acf51b33d35 | textbox | PPE used:
3f61bca2-330d-5d06-b588-b749e8ff038c | textbox | Certificates, permits and/approvals required:
52736c40-22b6-56f1-be8e-8fd32b2b5304 | textbox | Relevant legislation, codes, standard MSDs etc. applicable to this activity
f948400d-3b6d-5037-a27e-a1da8d06232a | signoff | This JSA has been authorized by:
df68f526-1e94-59d2-832e-1b4bc4eb113c | checkpoint | Job Safety Assessment
cf5370ec-8eca-58c6-95c1-7451c4a4ee45 | note | Refer to the attached Risk Ratings table to complete the following..
79f0ae09-d4e1-51ac-9f11-c422931627f6 | textbox | Job Step Details:
9234ac90-3e0f-555c-948c-a2d80a2889a8 | textbox | Potential Hazards:
b6d77a09-65b6-535d-9bca-fcdf2c04d858 | textbox | Name of Person(s) Responsible for work:
1c7bca5c-f42b-5cd2-a30e-f592d0defe02 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
82a1340c-4f65-5886-aeee-95f82f4fd2b7 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
7943c540-06ba-53ce-acc0-5134f396b644 | textbox | Job Step Details:
f9865afc-487f-50ff-bed7-407efbbd2580 | textbox | Potential Hazards:
ac585b4c-ff8a-5afb-b898-8b999d60b769 | textbox | Name of Person(s) Responsible for work:
03ae949c-bf08-5430-b73d-7ffdbf8be551 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
a0e12197-8e67-5396-81ad-bd36acffe33c | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
1c571f1a-b669-58af-b207-86af94d31e5d | textbox | Job Step Details:
b42e065c-5969-5332-a496-0a10f623454c | textbox | Potential Hazards:
95c6ab47-b502-5a6d-a955-fd467ed22a12 | textbox | Name of Person(s) Responsible for work:
74102006-5975-5389-b1fa-24403935dc36 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
420926c7-8660-5fd9-a1fb-a52da3f2df4c | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
9c249912-b3c0-5116-b8ec-aba0ea058e1e | signoff | This job safety analysis has been developed through consultation with our employees and has been read, understood and signed by all employees undertaking the works:
930a3e43-5647-50d1-87f2-966cce2343da | checklist | CHECK-002 Site Inspection |  | CHECK-002 Site Inspection
7604d349-3c9d-59ec-8769-a0cfe4110d87 | section | 1. Administrative, training and risk management requirements
b646b6a2-68d2-5b04-925e-0e13a9bb914a | checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
6ba63d7d-3b3f-5c31-9434-f4939b574a87 | checkpoint | 1.2 - All workers carrying out construction work have received the general construction induction training.
b9691151-2ecd-5ee2-8ec8-b533204f2fd9 | checkpoint | 1.3 - Workers have been informed of the site-specific health and safety rules.
60ac4aca-7460-564d-ba14-2d3d98bfd234 | checkpoint | 1.4 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
66bab419-a393-57f6-9c97-758d79271510 | checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
2ab82d7a-cc3c-56a0-a89c-ba9e4252acc3 | section | 2. Safe work method statements
c145e282-9bf0-58ac-8a85-4500302a4c6e | checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
fe929405-eae8-5ca8-8783-fd58e2de54ac | checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
7934e80d-dec5-5f41-be0b-42bbfcdd01e2 | checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
8f0ef03e-318f-5cf3-b827-93b54c1df497 | section | 3. The work environment
e6018bbf-c8f1-5f07-b149-1bf83ae3ef97 | checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
79bdc24c-1c00-5acf-983d-ebaa5ce5fad4 | checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
1825c9fa-24bb-50ad-8b3b-a1e424e13ba5 | checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
f8272eb3-01c5-5337-a307-f72286a48c32 | note | ○ Each worker to carry out work without risk to health and safety.
1be19c4f-a82e-522b-98e5-e5aa656efb60 | note | ○ People to move within the workplace without risk to health and safety.
aef67d61-2c29-5ed8-9db6-bcf3ceacb0db | note | ○ Safe evacuation in an emergency.
e6860137-88a0-51f5-bab0-d6de14d63cb6 | checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
4ff74d5f-cec6-5c19-bd25-e6838e8f1c56 | checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
48066b16-7c21-5768-945d-e4a5cf766b0b | checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
0b615730-4ffb-51cd-bfb3-02fcfc4435d7 | checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
8dca0770-d2f9-575c-9e8a-bc6b57a4f871 | checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
b201c421-5b2c-5c48-9704-05cf6113c44a | checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
c51929b0-8776-5f5d-9a2c-3ebcffee0dad | checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
18a4e767-8b1d-5672-a5a5-274690a036b4 | section | 4. Confined spaces
2825d9b2-da10-596a-9ce0-b40fcc56a1cc | checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed ASSES-05 Confined Spaces Risk.
0a584ab9-a5b3-52a1-b882-f4b9709cc8db | checkpoint | 4.2 - Prior to commencing the works, FORM-003 Entry Permit Confined Spaces has been completed and approved.
89309c03-7f35-5362-a583-36791c1dba8a | checkpoint | 4.3 - Appropriate signage has been erected for all confined spaces.
d0a6d31c-65a4-5bf4-bc31-672ba9175665 | checkpoint | 4.4 - First aid procedures and rescue procedures to be followed in accordance with POLICY-006 Confined Spaces Rescue in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
ded5ed0a-e444-5b8a-bb7f-fdbe7f8fb660 | checkpoint | 4.5 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
bed85791-cdf2-5734-99e5-42eabe40f212 | note | ○ Nature of all hazards relating to a confined space
be7ccc94-3134-5b95-8b20-72fefb415b43 | note | ○ Need for, and the appropriate use of, control measures associated with those hazards
b110c5ef-6275-5bf5-a856-5a63e44d03ea | note | ○ Selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
1a99ce71-7f11-5eeb-a21b-b350ded8d8c3 | note | ○ Contents of any confined space entry permits that may be issued
b0c02c77-ff62-5a00-8a01-e40663b3102c | note | ○ Emergency procedures.
e81da6f2-b7fb-5d0c-920d-ac0985916342 | section | 5. Working at heights
e2a6047c-3469-57d7-a1ee-63a6d2ce1e6a | checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
c2fb3d08-8253-53dc-a912-7762ad36b3c3 | checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
15a0bb70-25a2-55ce-8391-f9705261ae79 | note | ○ Each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
098e60b1-4049-5b81-9802-dc44b50477cb | note | ○ The risk of death or injury that may result because of the hazard has been assessed
d8e17ce6-5b0d-5d71-adcb-c9012baa2fa9 | note | ○ Any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
98b57a94-c6a8-50d7-bb1c-2783d46d3990 | checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
df712649-e072-54fe-b908-fe63884b915b | note | ○ Prevent a person falling any distance
28993959-da47-509e-a241-bb45845a83ee | note | ○ If prevention is not practicable:
55b684af-87ab-5194-82b6-3e644dbb1a7b | note | – arrest a person’s fall
7575aa24-7d52-5200-8719-e639552c447b | note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
6a7044d6-a81e-5157-bf4a-f5cbc210f31d | checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
d81daed7-0057-50a6-9fe9-8aece2cab495 | checkpoint | 5.5 - Ladders are used where the:
d8458251-f7d1-554a-bcc3-372ab76e7d8a | note | ○ Bottom of the ladder is on a stable surface
c8fdd838-d4e2-5652-83e9-9bc5b3b6145b | note | ○ Rungs of the ladder are approximately level.
3f3316e4-f01d-5a03-a2af-4637d940f52b | checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
e8760cac-e387-5620-9ab6-470830ad9fb6 | checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
faed25a7-0d74-5c49-bf12-7d35d9c1c221 | checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
06596e0e-a7d6-5ec1-ae87-b458bc352bec | checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
a1cf7634-7b7a-503b-98b6-a44b1401c2de | checkpoint | 5.10 - REGISTER-007 Plant and Equipment is up to date and includes all mobile plant in use.
92665bac-aa8b-572e-82c0-08a5392f0bfe | checkpoint | 5.11 - CHECK-004 Pre-Start Plant and Equipment has been completed for all mobile plant in use on delivery to site.
3dd77402-8a87-529b-8183-9c072abbce8a | checkpoint | 5.12 - CHECK-005 Regular Plant and Equipment has been completed for all mobile plant prior to commencing operation of the plant that day.
26a08f78-359d-5909-8059-66675eee2c23 | checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
23b709bb-1735-5ef2-90a2-edf28c5eaf62 | checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
a556791d-1316-51ef-8b5c-74f5158d5808 | section | 6. Electrical
b2dcd8ef-695d-5a07-a1c9-d7a4c42cb637 | checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
d2a5d551-016e-5c24-aaed-9a6546efb65d | checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
a3dea501-b49e-52a0-b686-be4f3b199e32 | section | 7. Hazardous substances and dangerous goods
28f006f5-6133-536c-83c5-e5fd046e9474 | checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
d9654d68-e223-5e2a-a924-23ef86d304da | checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
569fad8c-3f02-54bb-9e8d-8a513e63a228 | checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
73d14d34-271c-5e50-a0cd-036c9275e063 | checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
a5f93861-409f-57a4-9892-aad365d82b0e | section | 8. Corrective actions
a3895f4e-c7f0-509b-ac43-872a6873bc7e | checkpoint | Corrective actions
fefdfa68-8ae7-5784-8f52-ff31386b2624 | section | 9. Inspection sign off
19075f73-f3d6-5581-b9a9-39135e1c7056 | checkpoint | This workplace inspection checklist has been completed by;
4b32712d-5eb5-5f21-8318-9f10d9fee1e3 | textbox | Name:
8f6f1e26-c9d1-5d5c-beb5-fb775c1e28a2 | date | Date:
75e3ab6c-26b3-5c04-9c56-ec536230e4ac | signoff | Signature
690502ea-7da5-5119-ba91-b2aa394089de | checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
be7ee8f6-2fdf-5e61-aee6-adf9bbb71704 | textbox | Name:
f58dc23b-c6d5-59c2-9d2a-57694b8eff87 | date | Date:
3e494399-cc9e-5e9f-964d-deff12bc6678 | signoff | Signature
7bd28543-904f-5683-acd7-cdd9184635f4 | checklist | CHECK-003 Site Establishment |  | CHECK-003 Site Establishment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint-no-value | Details:
a9f0eb07-3912-523a-be5f-a802d6ff641b | textbox | Project Number:
be704f51-8345-5d07-82ad-4691b8d46bd7 | textbox | Project Name:
55438198-cfca-5417-84b8-414b08417475 | textbox | Project Manager (PM):
cecfc96f-5250-5907-bbf1-e0562cea155d | textbox | Project Address:
71a86034-b956-5203-b873-8d6f798b33ad | textbox | QA Platforms used:
d76c3f2b-8320-5708-a9da-38fbd066c69d | checkpoint | In house, FER & Specification Numbers
62d9c92d-c1ab-5446-89b1-bf80cbc0d1a4 | date | DATE:
087bf1f2-2a91-5ac0-811b-92888709522d | checkpoint | Site visit & survey
9d598589-23f2-5739-abd1-38084d2be5a8 | date | DATE:
f40bf70e-7c03-562e-9e73-8fbcd929c861 | checkpoint | Review Drawings & print for site
767f52ec-aec3-5775-a064-7229f459323b | date | DATE:
86a71627-b83a-5fe5-827a-1173c7cec5b0 | checkpoint | Review Fire Engineering Report
0d7909f1-54e9-5c90-92e6-074eee42c7aa | date | DATE:
eb035cf3-e47b-505b-b522-f71e191c12e9 | checkpoint | Allocate labour
0a895642-a262-5e46-a17d-2bd265707331 | date | DATE:
dae330e6-ef9c-57c6-9197-103abfd54f8e | checkpoint | Review Principle Contractors (PC) proposed baseline program
1692f978-f249-5f30-958a-396ff70c258b | date | DATE:
a55f05f2-ebad-534b-8cbf-1758e22f0184 | checkpoint | Create Fire Services Proposed Programme
07f60850-c8ec-5c07-8cb3-4760f7a199c5 | date | DATE:
7a356f7b-71e1-5c53-87a9-49ac25d117b8 | checkpoint | Upload to ALL necessary QA platforms
b5b18c80-8662-5430-9ca2-81c6feb62800 | date | DATE:
e81b739e-4825-5367-841f-3db753c333bf | checkpoint | Save softcopy in GM Dropbox
c65d94ba-f3ef-5124-bde6-1efbcc2ca74a | date | DATE:
c2e6bd69-c405-5afe-b004-c8b107fec18d | checkpoint | All employees have attended Induction
f2578d06-522d-52c8-91f5-609e406fe43b | date | DATE:
2630ff26-4768-5012-85c8-d89b8e40b4dc | checkpoint | All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
ccf4434e-fcc7-5408-8a54-c9b9b3f5816e | date | DATE:
5674c7a7-848b-557d-a867-52fce0b2bfd9 | checkpoint | PM Signature:
1ec883e5-6967-525b-ae22-80125604b1fd | date | DATE:
c87607a0-8578-5433-aab2-734b6f931e89 | signoff | PM Signature
704a9562-06dd-5402-9212-b828fd7ef1b5 | checklist | CHECK-004 Prestart Plant and Equipment |  | CHECK-004 Prestart Plant and Equipment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
c790d9ab-95c0-5ad7-8744-65d0a45a7416 | date | Date:
ebf95f13-e705-5ded-b46f-5aecf174754f | textbox | Time:
a0b456f5-186d-5d77-9da1-ab467eef3435 | textbox | Location:
9e9fa52b-17ed-5e2c-965a-e3ad36446e27 | textbox | Supervisor Name:
0b454d7c-2ee3-5e46-a2c9-e543b923b322 | checkpoint | Plant or Equipment
db1723d8-8575-5aa4-8ba8-d4f8f82cdec8 | textbox | What Plant/ Equipment is being used?
09b2f402-8ed5-58ca-b9db-e52985b82545 | textbox | Person operating today:
5eaca82b-69c5-5490-801e-9b3183d95168 | button | Is this person competent and licenced (if required)? | Yes, No
c9ef7bda-72cf-51d4-94bb-b2440b331909 | button | Is the operator under the influence of alcohol or drugs? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
518d1d85-0aef-5b66-81e7-45a6c9f53066 | button | Is the operator tired? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
93b7dbe2-94d4-5ee3-99ab-a64e0892fe92 | button | Have you added this to REGISTER-007 Plant and Equipment (located in Dropbox) for this project? | Yes, No
a62beb93-c005-5cfd-ae51-90e3a15bc011 | button | Have all relevant SWMS been completed? | Yes, No
f9910de1-77f1-541c-876c-35b08d530ef7 | checkpoint | Plant and Equipment Checks
dc00945a-82f6-5d92-88ad-74060ae94cd4 | note | As per WHS Regulations 2011, s206 the person with management or control of plant must ensure the plant is used only for the purpose it was designed and ensure that all safety features and warning devices are used in accordance with instruction. Please check the following:
aa4ad773-a010-5ffc-86c8-792d5aebf66b | tickbox | Electrical switches, traffic indicators, front and rear lights are working
5736c79d-ff53-5db3-9307-f44755dd7dd6 | tickbox | Guarding is of solid construction, unable to be bypassed or disabled, is appropriately fixed and operates correctly (check latches/ locks and interlocks if fitted)
3039ef7a-4edd-5d09-b45b-00f40301ef64 | tickbox | Engine, fuel and lubricating systems are as per manufacturers specifications
7ad75afd-3c7f-5358-bfb2-fdb29bfc8f45 | tickbox | Tyre pressure is as per manufacturers recommendations
02292e33-9dbe-5cf3-a05e-966d22a45ea4 | tickbox | There is no risk to the plant colliding with any person or thing (i.e. workers, other vehicles or plant, energised powerlines)
a8151e18-2938-5540-a3e9-3dbcc0f79b36 | tickbox | There are no mechanical or other failures (e.g. hydraulic failures, release of hazardous substances)
9c13abdb-7be4-555b-929c-f953a23051d1 | tickbox | Seatbelts are available
63bb5054-bbe9-5be0-ada8-170818ec77ad | tickbox | There is no damage to switch gear and controls and that controls can be locked off
61d02160-bc39-5332-aad5-98dc1b906242 | tickbox | Emergency stop controls are marked, accessible and coloured red
ecfacbba-456c-5a92-ab1f-c4658915a976 | tickbox | Warning devices are positioned to work effectively
615fa2d1-e34a-50cd-a4fb-499eb7a0dabe | tickbox | There are no hazards to the operator (e.g. things that could fall on the operator)
1d68b3b5-7114-5143-848b-f175aaf07803 | tickbox | There is no hazard or risk that could caused the plant to overturn
f49c433d-21cd-5f5c-be4f-26a3c24d4dc1 | tickbox | Maintenance and inspections have been carried out
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
d7295a42-11dc-51c1-80d1-cf9ed24c9857 | checkpoint | Operator Signoff
c685b88b-9455-5eaa-8271-b512fa65c130 | signoff | By signing I confirm I have participated in this prestart and understand my duties. I know what PPE I am required to wear whilst operating, the load limits and I am aware that it is my responsibility to leave plant not in use in a state that does not pose risk to others.
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
411f2708-55c2-5469-af77-82675a4393a8 | signoff | By signing I confirm I have conducted this prestart with the operator (above).
58743d45-bc4b-5914-ad8c-dd73f1316a5f | checklist | CHECK-005 Site EOD |  | CHECK-005 Site EOD
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
e7f3c29e-5e50-58c0-b5bc-209b95434737 | checkpoint | KPIs
035f7c1a-ea25-55de-950c-d042a33c503f | textbox | What area did you work on today? Specify level(s)
9fa426b4-4776-58b7-9889-b15b65137495 | tickbox | Detection - In Slab Conduits
93e8c10f-65f4-53c5-a389-af2e986d15ee | tickbox | Detection - Rough In
ee59a920-9789-592d-b301-bec8b0270bdd | tickbox | Detection - Fit Off
0fcff527-122d-56ca-9d55-fb283c029585 | tickbox | Sprinkler - Rough In
316bba3f-90e5-524f-879b-fd51fc6edcf9 | tickbox | Sprinkler - Fit Off
f9cc44fd-93c0-5e67-b517-5d5412d51f91 | tickbox | Wet Weather Stand down (List names and duration of stand down per person in comments below)
987f19cf-c0ba-5e71-86f2-700cb1617ba7 | tickbox | Safety Stand Down (List names and duration of stand down per person in comments below)
c16a2a74-dd2d-5d1b-884e-153088ea0604 | tickbox | Industrial Action/ Techs chose to leave site (List names and what time they left in comments below)
d6aa768d-18cb-5397-9287-98d25f058d4d | checkpoint | Productivity
fe16c117-6b62-5e0e-b297-3bb812c03098 | textbox | In terms of production, did the team meet the site goals today? | Yes, No, Partially
bd402f12-5188-5258-95bb-04843f13dbad | button | If 'No', what hindered the progress? | Time management, Lack of training, Fatigue, Equipment issues, Other
f60fe192-fe44-5ce0-a896-807887b18a88 | textbox | If 'Other' provide detail:
0da64418-8a08-5008-a58c-e5368b811be6 | checkpoint | Clean Up
dabfd603-b818-5e2b-889f-e6da69448774 | button | Is your work area tidy? | Yes, No
77dc2b8c-e46c-5633-a114-6401ab7d0e6f | button | Have Chemicals used today been returned to secure storage? | Yes, No
8ca30072-969d-5ec9-9f3e-457472da7db9 | button | Have all tools been returned to toolbox? | Yes, No
c6ec1d8e-5d5a-5f43-8e7e-6742c49875b8 | button | Are all tools (including site iPads) charged and ready for tomorrow? | Yes, No
d3977e5c-db54-51b4-8527-3b17c732206d | button | Have you completed all necessary QA paperwork for today? | Yes, No
d19615df-d297-5a4b-a682-e27077454f40 | button | Are all employees aware of where they are working tomorrow? | Yes, No
bbe829b3-6aa5-5542-b6ba-807198ef173c | note | If 'No' contact management now
d5fda9e0-608b-55d3-bf92-80ad7afe5a6a | button | Were there any incidents, injuries or near misses on site today? | Yes, No
df6d65e3-f042-5507-a30f-559d3c435e86 | note | If 'Yes' complete the necessary reports
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff and CLOCK OUT
5d29489d-1335-55db-945d-fe7621bce49f | signoff | This EOD has been completed in consultation with our employees and has been read, understood and signed by all employees on site at the EOD today.
7942b527-1ba9-486a-a7ba-17ad834e1398 | checklist | CHECK-006 Daily Prestart |  | CHECK-006 Daily Prestart
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint | Details:
c67a5ad6-470a-5e2f-997a-f5f60b5e37f6 | date | DATE:
be60c24b-9584-50b3-85e7-c97aac850d9f | textbox | TIME:
5309490c-3518-5494-8898-6b41003721aa | textbox | SUPERVISOR NAME:
694414d8-1e1b-5f09-a0ec-7b8d590ad762 | checkpoint | Issues
29d3d625-f08c-54b1-bf3c-b22dfa3fbd75 | button | Are there any issues arriving from yesterday? If YES, detail in comments below. | Yes,No
88bc1641-daee-577f-b7e3-efc84c9a3236 | note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
0662f670-ac3d-5439-af86-c1336a2b3861 | checkpoint | PLANNED WORK ACTIVITIES / TASKS
89e3b170-750e-51d8-a682-a426806358d3 | textbox | ACTIVITY / TASK
63009163-b71f-5d74-88ab-182d0339fbec | note | SWMS that relate to today's task/s
3217cd42-d7b4-5c06-8925-f508bd3b2eb4 | tickbox | 001 – Working with elevated work platforms
4e6ff252-595a-527a-99b7-8b0d317de7fb | tickbox | 002 – Wiring Rough In Minor
cd7e73e3-d703-52b7-9d32-c59cb15791e0 | tickbox | 003 – Fit off fire alarm system
b8ad95df-8b35-52b0-9faa-5efb930c096d | tickbox | 006 – Installation of pipe and fittings
2fc333ec-8649-5094-9bac-e7db22722260 | tickbox | 007 – Manual handling
793477a1-ebab-528d-ac0f-4cf5e41a28fa | tickbox | 009 – Pressure testing of pipework
abf682f7-668c-584c-add3-69603f01ffe9 | tickbox | 051 – Using platform ladders
aab532fe-44ab-58ce-84b2-320c641c1eca | tickbox | 060 – Inhalation of Respirable Crystalline Silica
55efd7fe-fc29-5217-af4c-3858f7a3124e | tickbox | 061 – Working in Major Area of Concern
774a66c3-3fea-5200-a769-32e4e0d72e01 | tickbox | Task-specific Safe Work Procedure
23c8da75-1795-5395-a9d2-b738a880bbe9 | checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
018251a3-fdc4-5187-821b-085ee9060fc3 | note | IF NO, STOP AND DEVELOP!
ebf4ce4a-0774-58f0-a144-522ec96b5a15 | checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
95fe8c17-73e5-5a12-84ab-0e88db6ce7aa | textbox | If YES, please list
279dbae7-8c1f-5553-98d3-d60918e8eade | checkpoint | Permits
ccbee4d0-b0fc-50f9-aba7-187627b00d3a | button | Isolation Permit | Yes, No
e9e5dd68-707a-5644-8f38-af984c59f3e6 | button | Have conditions changed since permit approval? If YES, please note changes below. | Yes, No
498988e2-fa90-543d-abe2-62bbc0b59d3d | button | Hot Works | Yes,No
49f83c80-5eec-5445-acf1-c5c9e01af072 | button | Permit to cut or drill | Yes,No
26129dde-acee-57f3-b54c-c083077e591c | button | MAC Permit | Yes,No
1d20b088-7c9c-5436-8f27-c1ecd33f79fd | note | Please list Permit numbers with description below, and upload photo/ attach file if available.
cae12b06-72bd-55e9-a701-9b47a7fdd5d7 | checkpoint | Environmental Risk
d043a4ae-8752-53fc-bcd7-920e72521388 | note | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust?
be468b16-df19-537b-854e-46bbd3df7b89 | tickbox | Clean up the general area
03b3f67c-e939-50e1-8cb2-87e19dbe9fd7 | tickbox | M-Class vacuum
054df62a-5657-559a-8159-5ed36c7947b6 | tickbox | Fit test and appropriate fit mask
3640b7ac-10ad-5ec3-ab6e-ae1284393ae1 | tickbox | Spill kit onsite
9bbc93b8-7fb5-5515-8c51-902ff1a50612 | tickbox | Other - detail below
903e1008-c734-5d92-8e65-be1215f53964 | checkpoint | Checklist for Activities
f1e2b79e-aefd-53e7-bcd3-7868bdf06e49 | number | Number of people in your Work Group
57c8c5eb-69d5-5928-bcc8-b3fe0690aa3a | button | Daily Risk Assessment Completed | Yes,No
d198e689-340f-595d-aa6c-5796b9e55eea | button | Qualifications/training of staff adequate for work activities | Yes,No
a89c730d-f0a5-5583-9141-f6861600debc | button | Plant and Equipment on/off site | Yes,No
c2abc099-5048-5862-be7e-69276e515d47 | button | Equipment safe to use | Yes,No
c35b1cc8-2353-5462-9376-b66fbffbe2eb | button | Work area inspected and safe for staff to enter and work in today | Yes,No
446e2139-b3e3-5032-b3b7-4b2ecf6682f2 | button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
1297b9fc-83fc-5f03-8c96-a7ef0df8cad5 | button | Weather conditions for work to be conducted assessed | Yes,No
50775e4c-331c-5bcf-9d61-90de79b49eb6 | number | How many workers have been allocated for today’s clean up?
31b028e3-39b4-5b10-96c0-301d4210e7d4 | button | Pre-start communicated to all work teams including all trades & subcontractors | Yes,No
00d26647-1805-5512-8e68-9d14a06237f7 | button | I acknowledge that all Plans on my Dropbox shared file are up to date and I have confirmed this with management | Yes,No
f21451ba-8bea-5c8f-a381-24f716ce840c | checkpoint | Builders Briefing Notes
96ad1a92-eed7-5574-b446-3263c628aa29 | note | Attach a photo of the builders brief
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
df4aed2f-f262-4069-9273-2461389b88de | checkpoint | Mental Health Check-in
cd31bf4e-e2d5-5d58-b35c-fd75f58de3c1 | note | Prior to commencing work, ask your fellow workers: Are You OK?
0c6ae895-4776-5618-ae00-20be5d041a11 | note | Mates in Construction 1300 642 111
bd2c90e5-3cd6-5a5f-aefc-f4f34c1caf48 | note | Beyond Blue 1300 22 4636
3ecf9d4d-a367-5b79-a67e-d473daee966d | note | Gambling Help 1800 858 858
065e825a-d2be-5f52-accd-f30095264611 | note | Drinkwise 1300 858 584
462a3bfd-f982-5f3f-95bf-2a3e5632bbde | note | GM Fire Management 07 3519 7573
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
2c27aaf3-a648-56ea-92c9-e1e22f200a26 | signoff | By signing I confirm I have have partipicated in this Prestart and I understand my roles and responsibilities today.
f0a4a5de-75f3-4297-b4e6-f0b3704d007f | checklist | Communication (empty) |  | Communication (empty)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5b56ae07-2890-4126-9d9b-f05befee543f | checkpoint | Communication
251f0a8c-79cd-5265-ba29-9d338584287b | note
127dacb5-d0f3-5005-8b8c-418d2bbccc30 | checklist | FORM-001 Tool Box Talks |  | FORM-001 Tool Box Talks
0e50f726-5e25-5b32-be5e-0af50c2a4fbb | checkpoint | Tool Box Talk
e3272aff-5ad7-5584-9f05-601db13efeff | note | Project: Ripley Hospital
c4982672-0b0f-5087-ad36-2079a30053d4 | textbox | Tool Box conducted by:
b862c72d-bb88-5890-9585-9eb1d66d73f3 | date | Date:
201ee0d5-9875-55e5-a6b4-cf9a175f45ee | textbox | Attendees:
272ef767-b0f9-5d40-860f-37667165b540 | checkpoint | Electrical tools Tagged & Tested
de358699-2ee1-5f01-a52d-02e78a8f5dcb | note | ACCEPTANCE CRITERIA: Completed Onsite
9031bd57-1d4e-547c-b0ec-b6fb0b1da5db | date | DATE:
605677f5-661a-5bc3-a836-02384d30df5c | checkpoint | Tools checked for wear & tear
d34b0a75-d62c-564d-93ac-a1912bd32f6b | note | ACCEPTANCE CRITERIA: Completed Onsite
8aa8c1f1-8235-59cf-9f29-b950ab07c005 | date | DATE:
acfc8acb-9e64-5733-af2a-b8ca4ea1ea81 | textbox | Items for Discussion:
eabcda0d-be6f-512a-b32a-8bddf5fcbc83 | textbox | Items for Review and discuss at next meeting:
95cb37b4-7a6f-5ffc-99b0-5d11fbc535e8 | signoff | Signatures
cb875ba2-3bfb-596d-9e7c-4f84a85d6613 | checklist | FORM-002 Tool Box Talk Platform Ladders |  | FORM-002 Tool Box Talk Platform Ladders
106e79f1-1888-598d-99d2-b5a1def7ffd3 | checkpoint | Tool Box Talk - Platform Ladders
887bab57-3216-58e7-9dd5-6974b3a623f9 | note | DO NOT use platform ladder unless you are familiar in its safe use and operation.
ac68153f-7547-5f9f-b14c-f8801309e330 | note | Always complete as much work as possible at ground level before using the ladder.
3271903a-2c15-5d14-ac31-800aa151f93c | note | Make sure the platform ladder is stable before climbing.
5c4a49ee-d931-5509-bdad-bc64c1ca1617 | note | Project: Ripley Hospital
00a320e9-986f-593f-bfe8-d25f2931da45 | textbox | Tool Box conducted by:
d0208122-f03a-5610-bde4-6bcb1a760f97 | textbox | Attendees:
da9865ac-d3b6-579f-bb6b-472d8b97b3d7 | date | Date:
fe834967-5fae-5142-ad41-d9de6147f88c | checkpoint | Potential Hazards
3674f2b7-e39a-58bf-b062-1209a407d5a0 | note | The folllowing potential safety hazards and risks have been explained to attendees:
5ea57c24-c9ef-5ac2-aae7-14b6543b15e5 | tickbox | Falls from height
e35ecb4b-a22f-5bcd-833f-fe852d10554a | tickbox | Falling objects
a3d70cbf-4729-5583-aee4-bcf73f29102e | tickbox | Awkward posture
016ab889-7fd8-5c55-95e3-1cf5f8ca44c5 | tickbox | Duration of task
674a0483-b78e-5388-ad6a-db7ac2554b1c | tickbox | Repetition of movement
3f4946f8-8fdd-526a-bb60-7b0d27db4098 | tickbox | Sprains/strains
a6af3874-9657-5afa-ac7b-5c30211f6885 | tickbox | Over-balancing
75d35ab2-1c77-568c-80f3-d9d45ae93ef3 | tickbox | Slip/trip/fall
4a7ce000-11b4-5942-9d59-57beec09de90 | tickbox | Electrical hazards
70790ef5-6074-57a2-b56e-987747b11967 | tickbox | Climbing with loads
1bd92719-b7cf-583c-a096-9b04e390c7ae | checkpoint | Pre-Operational Safety Checks
6ffbd377-bf17-5fba-98aa-8caef52856d1 | note | 1. Familiarise yourself with the safety instructions on the ladder.
a2ea6641-1eb7-56a0-a6e1-7e49d7e16115 | note | 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing
aaf65bc0-57d6-5a03-b04a-8610a6416a50 | note | 3. Do not use if affected by a medical condition or medication.
2ba95fdc-b818-55eb-8e98-76f82b92f60b | note | 4. Keep ladder clear of live wires, electrical hazards and ceiling fans.
2c22d256-80a1-5046-8b5e-69ef43b328e9 | note | 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards.
93412ad9-195b-58ad-a5cc-688db75dd770 | note | 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing:
ffc562ba-2d4e-5c0c-923b-aee111b51e69 | note | • joints between steps and side rails tight, all fittings secure, moving parts operate freely
639c69e6-a3c5-5051-a7d0-e2ca755bc18b | note | • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and
5dc33034-ebb6-5e46-8386-62410b6d7321 | note | • all components of ladder intact including side rails, rungs, platform, feet, hand grip.
c1ec81fc-3779-5bbb-99e7-d74bdce4d420 | note | If any component is found to be worn or damaged, rectify any faults before use.
b6eb527a-c4c7-5a69-bb85-a66da835bc7d | checkpoint | Operational Safety Checks
df307b10-6066-5dfe-b2be-ccdabe4b711c | note | 1. Complete as much of the task at ground level as possible.
50ceb36d-3a89-51e0-a79d-8e7534c96b76 | note | 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder.
2b10f449-9e31-58fa-8e70-0fe01b8c3789 | note | 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed.
37b91bc5-cb01-56fc-9108-0102c7c4058a | note | 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing.
7cac46ae-5fc7-5ee4-994f-75dd2980ea6f | note | 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free.
64f23374-768a-5597-b8a4-9427fc451328 | note | 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder.
cea9f832-60c9-5a6a-8373-7c2c02db8309 | note | 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform.
c5338561-5326-55d2-8865-025c5fc7aa76 | note | 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform.
6a5bcd9f-5002-5193-afd2-5687e1f860a2 | note | 9. Do not ‘walk’ the ladder while on it. Always get off to shift position.
19c1d6b4-49ea-5f94-9658-6f1b832f0141 | note | 10. Before moving a ladder, take care to ensure that all tools and other items have been removed.
2d257990-358a-561e-bc89-f01924822341 | note | 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
9d5b0bf0-53b6-5af8-a766-a7d78d594580 | checkpoint | Housekeeping
b7b52c7c-7b6c-5b22-8666-70b57f43c8ee | textbox | Items for Discussion
5c711e95-86eb-5f70-9f58-45404bea1e34 | textbox | Items for Review and discuss at next meeting:
0d24abf6-09a7-54db-913a-af58fcfdb176 | note | All attendees have been made aware they should:
fdb2ffa5-48c5-5b86-a475-b5e212b244b3 | tickbox | Return ladders to secure storage in a clean and in safe working order
ac8f4780-7d87-5234-98fe-0fee60585788 | tickbox | Regularly check ladder feet for excessive wear.
61838543-8502-5082-8baf-f0fa703ab465 | tickbox | Enter any maintenance in an equipment maintenance record
3015ae9e-0d1b-58a3-bfcd-57a87f411d9a | signoff | By signing I confirm I atteneded this ToolBox Talk.
02d1450d-190d-5aa4-987f-be5245f64771 | checklist | ITPS-020 Comms Rooms Fire Sprinkler Systems | itp | ITPS-020 Comms Rooms Fire Sprinkler Systems
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
4293bbf2-8bdb-5ceb-ace2-5b9162122951 | checkpoint | For Equipment Rooms (ER) ensure dry pipe system is installed TAKE PHOTOS AND NUMBER IN COMMENT BOX
cb0777cb-1ab7-5846-aa99-0054eda7be0a | date | DATE:
df672989-592a-595f-8a0e-4016c10640d4 | checkpoint | 2 - For Equipment Rooms (ER) and Telecommunication Rooms (TR) - TAKE PHOTOS AND NUMBER IN COMMENT BOX
59f175e4-146f-5160-909a-e20434835f06 | tickbox | a. Check pipework is not routed above equipment cabinets
0b42cf35-8f4c-592d-978c-84ed745fab51 | tickbox | b. Ensure no t-pieces, elbows or bends are above equipment
2983edb9-3576-528e-b675-59b74332ce09 | tickbox | c. Check no pipe is installed within 1200mm of sprinkler pipe
ede5e022-9019-56ff-8060-4f16c82e530f | tickbox | d. Check the sprinklers are high temperature heads
a2ceb093-2ead-5e6a-a16e-033d2ad84b5a | textbox | i. What temperature
0b714a48-1aa2-52cf-a683-4152a36e3aa3 | tickbox | e. Check sprinklers are installed with wire cages
83e6dd5e-de42-53ab-9fc4-b38934a42448 | tickbox | f. Check all sprinklers are upright sprinklers
620009dc-765e-581d-9d00-988d98021219 | tickbox | g. Check a floor drain is installed
b2562e40-4f58-524b-9695-a1a1ff878468 | date | DATE:
00c8164d-471b-5e4e-8249-1b4ddd19d617 | textbox | GM Sign Off - Name:
2123c370-a2a5-58b5-b49f-e31fc4555fe5 | textbox | PC Sign Off - Name:
50c3dfbf-555c-58cc-9c02-e88c74aef70f | textbox | CS Sign Off - Name:
3f9531ce-bbcd-5a01-aaf1-8875887bafb0 | signoff | Signatures
7db018c8-a151-492a-954e-75ac217ef641 | checklist | ITPS-100 Cast In and Penetration Installations |  | ITPS-100 Cast In and Penetration Installations
b8b6264e-b769-4aa4-9a1c-f5f661e868e7 | section | Details
6c14b95f-6420-4cb7-9161-37d41ba0634b | checkpoint | 1. LOCATION - ENSURE
ec77578c-4db3-5557-8eeb-854fa1b13043 | note | CIBSE C5.2.2 Set Points
d2674823-9f79-56e7-9d83-1a73b4a48a45 | button | Is the device setout correct and accurate as per RCP and installation plans? | Yes, No
197a3930-235e-53ee-8094-d5ebad741fe2 | note | Add Photo
5dbbc944-93c2-4a2b-8697-084e307fb679 | checkpoint | 2. CONDUIT INSTALLATION - CHECK
bd82342b-20e4-5531-ab6f-99a869b83d57 | note | AS1670.1, AS1668.1, AS1670.4 and AS3000
6a16af88-d35d-5422-b521-95b5f5bab3ee | textbox | Drawing Reference and Revision Number:
3cd092dc-53d3-587f-a0df-13bd3af36915 | note | CIBSE C5.2.2 Set Points
019733ca-ec97-58fa-b4ae-245eb917313a | note | Are Conduits routes are correct as per IFC Drawings?
b6fcb50e-a6e9-5c1e-b7d9-6f049b6781fb | note | Are Conduits are joined correctly and glued using approved PVC piping and glue?
f1f996df-2d7a-50b7-aa88-5e6c249a7742 | button | Are Conduits are tied in properly to prevent movement and damage? | Yes, No
a1057eec-ab5d-54b7-8528-1d83d4e23f26 | note | Add Photo
38198e9c-552f-4600-8af8-9b7f5d2f7fa4 | checkpoint | 3. SLEEVES AND PENETRATIONS - CHECK
7cbf095b-098e-5697-8b73-a53e21729d5b | textbox | Drawing Reference and Revision Number:
f4eaf9d9-387c-5054-9aae-89bb7d1ecad9 | note | CIBSE C5.2.2 Set Points
c1bd51be-1eec-527c-95ae-00226e2133df | note | Are sleeves the correct type, size and quantity as per penetration drawing?
fdc240e8-6179-5b76-bbfa-ce1b8ff65dc0 | note | Are sleeves routes correct as per IFC Drawings?
2ada97fa-d795-533e-9e66-953ecc3b971b | note | Are conduits joined correctly and glued using approved PVC piping and glue?
0bfa0694-31c3-5f91-9a5d-a997f4f62ce3 | button | Have sleeves been tied in properly to prevent movement and damage? | Yes, No
1d880b23-b90f-53a3-9ded-49181e624ec7 | note | Add Photo
cde10022-804f-47c7-b9d9-9889d79ad084 | checkpoint | 4. PRINCIPLE CONTRACTOR - CONFIRM
4a06c288-f644-50a3-8fab-c3e9d756adec | note | CIBSE C5.2.2 Set Points
aa7c3daa-1a09-5406-b4ab-3dc6b9d0b561 | button | Is the Principle contractor's sign off required prior to pour? | Yes, No
250a2975-9b04-50eb-975b-b9e6e2acac89 | note | Add Photo
8bf48efd-1ddb-4978-8deb-bd6c164f7508 | checkpoint-no-value | GM Fire Sign Off
e5511b97-b04e-431d-9a54-558350488ef5 | signoff | GM Fire Sign Off
cd90ebe5-0e3a-4441-97a8-d9a7e8f70dcf | checkpoint-no-value | Principal Contractor Sign Off
ad5b70cf-1ab8-4ef2-8f6d-8b24ab41c633 | signoff | Principal Contractor Sign Off
a1a1522b-ea34-486f-a8da-69f9e3e64361 | checkpoint-no-value | Consultant Sign Off
e71e5404-a079-4f4a-9147-d663d104812b | signoff | Consultant Sign Off
7fc90e35-c173-4b6f-93a0-2bbbaee07b3c | checklist | ITPS-101 Fire Alarm and EWIS Rough In |  | ITPS-101 Fire Alarm and EWIS Rough In
0ea49f80-22f2-4c58-93f0-a4e234f70f06 | section | Details
de3232e3-2197-448f-86a5-eff082473262 | checkpoint | 1. CABLE - CHECK
72f3ed6d-f7a8-569f-b818-be8fcc23cf98 | note | CIBSE C5.4.0 Wiring
2b7da899-886e-5254-9474-c87e4c2d8385 | note | AS1670.1, AS3000
6db90e9e-27d5-5034-ad80-81a264ebde2b | note | Is cable installed the correct size and type?
c5c6f879-17c2-51b9-9f0c-629ff3585ce5 | button | Is cable secured at regular intervals? | Yes, No
e1d1c407-6986-568d-89bf-5468de22ac5a | note | Add Photo
436abd69-8a0d-5c4f-a5e8-281e4b2a5d72 | button | Have you attached a photo of cable markings for Green Star Compliance? | Yes, No
baa32cd1-938c-58f1-ae19-9694fccd8d7e | note | If no, stop and attach now
171ac922-1280-41fc-bca6-ca6686b873ba | checkpoint | 2. FIRE RATED CABLE - CHECK
34bc313b-eacd-5d98-9674-dd0677d60343 | note | CIBSE C5.4.0 Wiring
eaf2d97a-3d42-5840-b6e5-207911a9f5cf | note | AS3000, AS1760.1, AS3013, AS/CA S009
33f81a2b-7d7b-5cd6-bc9e-958b4728e5e3 | note | Have fire rated cables been secured with fire rated fixings at a minimum of every 1200mm?
01b46233-8f79-5056-ad07-4a0bb8b80429 | note | Have compliant fire rated cable and fixings have been used for required circuits?
43ae66d0-7736-58f6-a1d3-afdcc13cfde1 | button | Are fire rated cables installed as the highest circuit? | Yes, No
da27d600-8369-576e-84bd-8f70fc60ef60 | note | Add Photo
99b6cdd3-9ef9-448e-8252-513d8bc2a462 | checkpoint | 3. CONCEALED SPACE DEVICES - CHECK
735fa3d4-d7f8-5514-87c1-9f6cd4017fc3 | note | CIBSE C5.6.0 Sensors/Detectors
999808a6-70e3-598f-8a6f-cc788a9f66d1 | textbox | Drawing Reference and Revision Number:
7eecdde4-494d-528f-8d96-75718e2b632f | note | Have all concealed space devices been fit off?
718ea4fb-7222-5b69-90a6-9fc7f0fd777d | button | Has remote indicator cable been left with adequate length? | Yes, No
d0cb9331-f703-5e91-9fe9-52413cf57b7f | note | Add Photo
ede0362c-709a-4fc9-ae85-3f73d07bd322 | checkpoint | 4. ROUGH IN - CHECK
74516c7a-481a-519a-b3f8-263c2d1c9227 | note | CIBSE C5.2.5 Control Loops
5512a3be-c0d7-521e-bfb3-adf5301e652a | textbox | Drawing Reference and Revision Number:
924ce6d7-9bea-5903-9ae2-ed7c1b8a5afd | note | Have all devices been roughed in?
24cf56a7-b6e2-5eff-8c99-03deae69d5cc | note | Is there adequate length left for fit off?
da181c9f-ef16-55cf-98d1-ba04f2ba04a2 | note | Are device locations accurate as per the latest RCP?
0db93df8-51a2-508d-abf4-b1feaad50ea3 | button | Have circuits been metered for continuity? | Yes, No
fe15935f-2d1a-5fd5-b97a-0fcbb8578317 | note | Add Photo
bae34d5f-2d2e-4d17-9c9d-9ac184d610bd | checkpoint | 5. MAG DOOR HOLDERS - CHECK
0634c013-139f-5265-ac72-7005c6c0949c | note | C5.2.2 Set Points
290e49b4-f920-5dcd-8e74-9720b1b159b4 | note | Have wall noggins have been installed?
4f51ae16-fc41-5516-831a-4e47d1938194 | button | Are cables roughed in to the correct location in wall? | Yes, No
37ffd9e8-c7ba-45ae-86ac-be2a98fd5967 | checkpoint | 6. SEGREGATION - CHECK
bfde7a38-9189-592d-b844-42614b7be773 | note | C5.2.2 Set Points
6b0f0075-1ab2-5e38-b211-2acbeb32ba5c | note | AS3000
5c136c77-40b3-5ffa-a312-b5579ffd20c7 | note | Is there a Minimum of 25mm from water & gas pipes?
b1d61c8d-9a84-59eb-891e-0aeb355f56de | button | Is there a Minimum 50mm between ELV & LV installation or a physical barrier? | Yes, No
053e0763-5beb-4a7b-b67e-e1490e7b9b5f | checkpoint | 7. AS WIRED DRAWINGS - ENSURE
8625b850-9b1b-5a49-baa3-d16bdf48313f | note | C5.4.0 Wiring
c8319ab1-1cdf-5a88-9e1c-b0147453a9dd | textbox | Drawing Reference and Revision Number:
7afb24bf-78a8-5ed4-b20d-4a58adc46915 | note | Are As-wired drawings complete and accurate?
7313e766-3177-581b-b7b3-8c1aaf7c556d | button | Have photos been uploaded to Dropbox? (as well as below) | Yes, No
a1c36c17-e784-5564-a839-e30b5cdd943b | note | Add Photo
8e3e6182-36b6-4187-af26-9be956592547 | checkpoint-no-value | GM Fire Sign Off
4e213ee1-8819-42ee-a90d-2aefda9c1029 | signoff | GM Fire Sign Off
04629065-6caa-4514-8e38-e8e849486cc9 | checkpoint-no-value | Principal Contractor Sign Off
c6d0de81-fed9-4a37-a4d3-bd466432c941 | signoff | Principal Contractor Sign Off
37720a82-a1f9-4244-b8e9-f999506b0edc | checkpoint-no-value | Consultant Sign Off
95895b02-2853-451c-98dd-238128cf575e | signoff | Consultant Sign Off
96597899-0b25-4e37-9f3e-d0a5d9b289e3 | checklist | ITPS-102 Fire Alarm Fit Off AS1670.1 |  | ITPS-102 Fire Alarm Fit Off AS1670.1
8cca375e-abc4-4b20-8d10-f73a144b873d | section | Details
c63c5ed3-af06-4b17-8557-521da73fac8e | checkpoint | 1. DETECTOR TYPE AND LOCATIONS ARE AS PER THE LATEST RCP
1d3a80c5-82a2-513c-8219-05b20c913a2d | note | CIBSE C5.6.0 Sensors/Detectors
dd7d969b-4885-52eb-b4b0-e8985a1e7e51 | textbox | Drawing Reference and Revision Number:
6631d08c-6f02-5285-a345-cfc171ad08f9 | note | Add Photo
09e980fe-0835-4a7f-9778-6d88fab1f7f9 | checkpoint | 2. DETECTOR ADDRESSES ARE MARKED ON AS BUILT DRAWINGS
a5f3557d-54b2-5a88-aabc-7324be0fdc1d | note | CIBSE C5.2.2 Set Points
1e636a41-9d03-504b-8f1a-b67b7d51e209 | textbox | Drawing Reference and Revision Number:
fcac1619-dc06-5fad-827d-c124b4046100 | note | Add Photo
317b7f17-370d-4814-b579-eec629262464 | checkpoint | 3. DETECTORS MAINTAIN MINIMUM CLEARANCES FROM WALLS, PARTITIONS & AIR SUPPLY OPENINGS
2fb8668a-2f76-508f-8085-1de9c6af03e2 | note | CIBSE C5.6.0 Sensors/Detectors
6b7e150e-998f-535f-a519-144fe2534739 | note | As per AS 1670.1 - 2018 - 5.1.4 & 4.1.4;
9ea00a45-39da-5788-beed-db87beff22a9 | note | Is there a minimum of 300mm from walls & partitions?
311f5c0f-80ba-581f-93eb-ba0aa5e85de1 | button | Is there a minimum of 900mm from air supply openings for smoke detectors & 450mm for heat detectors? | Yes, No
cb8acc2c-5f4e-5c06-b347-a15647b58f28 | note | Add Photo
dacc3dec-7e0c-493c-bab1-c751260302db | checkpoint | 4. DETECTORS MAINTAIN CLEAR SPACE AROUND SAMPLING POINT
8fe12945-97be-565f-ad3b-03d9d705e08a | note | CIBSE C5.6.0 Sensors/Detectors
2e4dbc87-b57c-57ea-a4c7-e0c0601ba736 | note | As per AS1670.1 - 2018 - 3.27.1;
0ab9f53a-8ab5-5fe3-96dc-d688f1e908a8 | button | Has a clear space of at least a 300mm radius and 600mm depth been maintained from the sampling point? | Yes, No
3c816099-fe07-57af-8409-3ed8c0f7347e | note | Add Photo
13adf851-0fef-4fad-a977-d461a7b45b39 | checkpoint | 5. PROTECTIVE CAPS ARE INSTALLED ON ALL DETECTORS
e1ae9552-9604-5c72-82e1-ba6634a6fafd | note | CIBSE C5.6.0 Sensors/Detectors
f9cd3dba-c292-5f73-bc2a-b18d79ad05b8 | button | Have dust caps have been installed on detectors to prevent contamination from construction work? | Yes, No
9ad44e7d-eac4-52eb-82bb-79c6ffe2a457 | note | To be removed once dusty works are complete, or at commissioning.
83654a31-d312-56e6-9b15-a251463b5511 | note | Add Photo
5e4f6144-5441-4d0d-93ee-95ac4e5e5c26 | checkpoint | 6. MANUAL CALL POINTS INSTALLED AS PER LATEST IFC DRAWING.
4013af6c-603c-5114-b14f-8e39582d978b | note | CIBSE C5.10.0 Manual Call Points
ff73d52e-96a7-56ae-9a3f-b72614c1e404 | note | Have MCPs been mounted between 750mm & 1200mm above floor level?
8c30564e-00c8-5195-9224-81600972d48a | note | Is there a clear space of 300mmm on both sides?
168dd84f-40ef-5500-a124-5e6e88cae841 | button | Is there a 600mm arc directly in front of the MCP? | Yes, No
cf956491-35cd-5f9f-98cb-2d564ba06a0c | note | Add Photo
8b7c8c05-4f1f-4e9d-9581-e81d684c2a22 | checkpoint | 7. MANUAL CALL POINTS SPECIFIC LOCATIONS
d5960f3a-65f1-546f-9522-d3c123d7742b | note | CIBSE C5.10.0 Manual Call Points
b0f78769-754b-5715-a033-e22d569742a1 | note | As per AS 1670.1 - 2018 - 3.14.2;
28196aee-069c-5904-b20f-dbaf878ad3ce | button | Is at least one MCP installed in a clear and readily accessible location in the circulation space of the main entrance of the building? | Yes, No
1512a916-d803-50a2-ba9f-9f8ebeff4c08 | note | As per the NCC2022 - S20C4;
1a830fdc-2a5d-5d9e-976f-10e1520d4f6f | button | If in a Class 9a building, have you ensure MCPs are located in evacuation routes so that no point on the floor is more than 30m from an MCP? | Yes, No, N/A
ae18020a-6ea6-55c5-96dc-1fc6b80bb80f | note | Add Photo
d719fef0-8f89-4457-9cfd-c2af7fef2591 | checkpoint | 8. FTRS
784ba0d5-a104-5da3-907b-d97a8d752798 | note | CIBSE C5.8.0 Modules Input/Output
8acc71e3-cfd3-5515-80ca-b80a510f7adc | note | Have all FTRs been installed in correct locations as per latest drawing?
1abe1248-a70b-5a91-b647-3ea4a922e0fd | button | Have the right quantities been installed to ensure correct operation as per the fire & mechanical matrix? | Yes, No
7f1493c3-d132-543f-b6e3-2624819501e9 | note | Add Photo
7d6b8299-1eb0-48cb-82eb-734ce6229b10 | checkpoint | 9. MAGS
1c044526-1f61-5349-ac34-8a78bae513c1 | note | CIBSE C5.8.0 Modules Input/Output
d133c791-6199-503d-80c5-ff4036c0d92c | note | Have the mag door holders been secured properly to withstand the weight of the door?
6f2cd359-e283-51b5-9ec0-cdadb28eb413 | note | Have they been installed at a uniform height on each door leaf?
45750d18-1889-5011-b330-a3358fe99ebf | button | Has a release switch been installed? | Yes, No
610054e9-86b5-5421-82f5-1735a525d97f | note | Add Photo
c9411957-aa0e-4c76-b7d4-54105fbb8dca | checkpoint | 10. MASDS
66ef6090-c50d-5f2e-80e1-6eaf4f2acd12 | note | CIBSE C5.6.0 Sensors/Detectors
5f9a8dc8-fe88-58ec-9152-267f279292c0 | note | Has all pipework been installed in line with the Aspire calculation & design?
91e4dd36-4876-544e-bac9-5e63c81a3c98 | note | Has all pipework been glued?
15031479-83b3-5656-b6cd-106987d06085 | button | Is the head end unit installed in an appropriate location? | Yes, No
841716f4-d46b-52db-8510-343ad615576f | note | Add Photo
d7189ca6-4307-4f39-824a-e7972649deac | checkpoint-no-value | GM Fire Sign Off
08e68876-bd91-479b-8b28-b9a6bbf019dc | signoff | GM Fire Sign Off
73a231b0-23cb-4d4a-90c9-9c6e7a4dcaaa | checkpoint-no-value | Principal Contractor Sign Off
4a17a840-61c3-45ea-82a1-abc74fb228e3 | signoff | Principal Contractor Sign Off
c3390aa0-697e-4687-a416-6eccc8eb2094 | checkpoint-no-value | Consultant Sign Off
602c8995-9060-4f38-b312-2fa8dc2d8eff | signoff | Consultant Sign Off
91d51257-7d30-49d2-8e4a-a61b56bce229 | checklist | ITPS-103 Ewis Fit Off AS 1670.4 |  | ITPS-103 Ewis Fit Off AS 1670.4
70dbe825-29f6-4808-94cd-698d47483dfb | section | Details
e4d5d30c-3ba9-4ce1-af47-4076fd278338 | checkpoint | 1. WIP
bc8a8c3f-1b5c-5fed-aa30-a744d467e23a | note | CIBSE C6.2.8 Warden Intercom Phones
67b39111-5e48-590d-92ef-14389e314eda | note | Are the Warden Intercom Phones mounted at a height of not less than 1200mm & not more than 1800mm?
434177c9-253d-5d2a-8b29-96e3ffac574a | button | Is there one WIP per EWIS zone installed within 4m of the exit? | Yes, No
d1707ea1-e29d-500c-9b33-8392262f22c5 | note | Add Photo
7b0ea2e6-846d-4428-bcf2-4d30815031c2 | checkpoint | 2. SPEAKERS
cae1fbab-0b5b-5e10-a243-6a7a8e0bad14 | note | CIBSE C5.2.2 Set Points
998841bd-c99e-59f2-829e-5ab4b38b5480 | textbox | Drawing Reference and Revision Number:
05bc6815-0e9d-59d9-a1e2-0b1d413e0ab0 | button | Have all speakers been installed to the latest RCP? | Yes, No
ef9446aa-9b14-52e8-8696-b3b36f4f3496 | note | Add Photo
d3ca720b-09cb-4261-82da-4359cef0725a | checkpoint | 3. STROBES
c8e1a93e-23ac-53bc-9203-faf875fbb76f | note | CIBSE C5.2.2 Set Points
91fe789c-2df2-5f5b-af93-81c05019ed61 | note | Have all strobes been installed to the latest RCP?
41a7f23e-04a7-563a-a06f-325bc8707fb8 | button | Have all strobes been labelled "EVACUATE" with 25mm lettering? | Yes, No
5ae30475-da18-534a-983f-8a7851260cf0 | note | Add Photo
9002276f-b34d-407e-bc11-7184c3e266e8 | checkpoint-no-value | GM Fire Sign Off
bcc40b8f-4035-4a68-b75a-39d769a9cb06 | signoff | GM Fire Sign Off
1f7d21dc-cb4b-4b5f-8bc0-9b06e8c73257 | checkpoint-no-value | Principal Contractor Sign Off
060cd70e-3d97-4837-ba1d-70ada9adda63 | signoff | Principal Contractor Sign Off
41e590ff-6a8a-435f-944b-4a67139583be | checkpoint-no-value | Consultant Sign Off
64c0d3ab-5ad5-471e-8980-2e9aac722e5b | signoff | Consultant Sign Off
2ca40b27-6636-46f1-b00a-dc608940b280 | checklist | ITPS-104 Fire Alarm Cable Tray |  | ITPS-104 Fire Alarm Cable Tray
b05a00e2-9d04-4b73-aebd-46a39308e9f6 | section | Details
e5d52aec-0716-4505-9e15-f0264fb01441 | checkpoint | 1. LOCATION & INSTALLATION
d438f19f-d23e-5fc6-a1c5-adf5df0222ad | note | CIBSE C5.2.2 Set Points
5d6cb010-5a24-5089-9baf-0d5ff76fde3b | note | Is the tray as per drawings and model?
a0858064-00d9-5376-a8ed-83295c2b5957 | note | Have all sharp edges have been removed to prevent injury or damage to cables?
7cdf3082-934f-5c88-be36-0bb78d5a4f6c | button | Is the tray supported at intervals of no more than 1m? | Yes, No
91187cff-a237-5fa4-b02f-63f8a91f273a | note | Add Photo
c686c57b-f202-4cdd-a425-c1ae2d629ae4 | checkpoint | 2. FIXINGS AND FITTINGS
73f4b19f-42aa-5ab1-8535-9d5fc7dc2eb7 | note | CIBSE C5.2.2 Set Points
87380cdf-8d10-57aa-9fcd-e9357705e072 | note | Have the appropriate fixings and fittings been used (for indoor/outdoor use as applicable)?
241f210b-4a9e-5531-b4e3-95164d744204 | button | Are Seismic fixings as per the design documentation? | Yes, No
7219ab8e-38aa-5d44-8b46-c44a687ce46c | note | Add Photo
2d86f7d5-1ebb-45ee-b430-880a5758234d | checkpoint | 3. CABLE SPACING
cc1f6539-0098-5eec-9276-8b93fdd7e9a6 | note | CIBSE C5.2.2 Set Points
364ff1a8-bb8a-5319-8aaa-a223cc4eff0c | note | Generally, where possible install in the following groupings:
a783ef76-bb35-56f8-abf9-c8b172355f21 | note | Detection Cabling & 24v Cabling
9418c269-0884-5369-890c-d155eaa08cfd | note | EWIS/OWS Cabling
60b53d4b-e9c0-53fb-8720-58912b1633a6 | note | WIP Cabling
5bab7e83-fce4-59b6-ba9f-00d109dafb3d | button | As per AS3000, 3008, and S009, is the segregation of ELV and LV cabling at least 50mm? | Yes, No
bf8568a8-acd3-5a9a-be20-e190c81ef20c | note | Add Photo
5517d1cd-6d8f-46c0-aa10-af2d3515698c | checkpoint | 4. SEISMIC
89421a74-a27d-509e-be69-327b2a9b8875 | note | CIBSE C5.2.2 Set Points
087bf3b8-973f-5204-b71c-9ed3e17e74e5 | button | Has the cable tray been installed as per the seismic drawings provided? (Use of stablity strut or catenary wire may be required) | Yes, No
ca660ed8-c27a-516a-8373-9538dc6e628e | note | Add Photo
d78e87f2-bd05-435f-939a-154d682ed8fa | checkpoint-no-value | GM Fire Sign Off
acdb9ede-52e5-40ad-a96a-bd810899edd1 | signoff | GM Fire Sign Off
f02f279b-cf84-4dc4-88e5-dca69a4dae8c | checkpoint-no-value | Principal Contractor Sign Off
4f70428e-ec8a-4de4-9696-58df5d0f9103 | signoff | Principal Contractor Sign Off
3d19540b-2567-4e8a-be4d-035eecb02e28 | checkpoint-no-value | Consultant Sign Off
bf89d14b-eccf-4249-9612-7c469f82c166 | signoff | Consultant Sign Off
87fcaf15-a142-45e9-9cc6-7f16b40d294d | checklist | ITPS-105 Fire Indicator and EWIS Panel Installation |  | ITPS-105 Fire Indicator and EWIS Panel Installation
9452938a-ce92-44fb-9c1e-8c725c3b38ab | section | Details
f0d29fe6-66b8-451c-bbbb-fba67f0ed4d6 | checkpoint | 1. LOCATION
2427f205-eebc-58a9-b82a-5b2d47efd5e4 | note | CIBSE C5.2.2 Set Points
808efaf8-a316-5b28-a29f-3c68ac7b0f25 | note | AS1670 (Section 3.9)
31ee6f6c-f262-54c6-ba41-b666be460352 | note | Do you confirm the CIE is:
6884749e-6d7b-51cf-8b50-4b6f9d007879 | note | Not in an area used for storage of combustable material; and
ae354937-cf1b-5471-8b9b-d2014f88da25 | note | Not obstructing evacuation of the building; and
43cdfe30-f01b-5f5c-8cbe-0d6e0efdabea | button | Not in a room containing sprinkler valves, pumps and motors? | Yes, No
fbf4570d-0f44-5982-aef1-7278951ca391 | note | Add Photo
e8b2ae31-88b4-4e58-90a9-ca4863e55241 | checkpoint | 2. LOCATION
17819994-01e9-5821-b0e4-6bedbb1db876 | note | CIBSE C5.2.2 Set Points
448b301b-43d4-58f7-860d-64c84cf838b6 | note | AS1670
5cd21124-f6ef-53e5-ba44-27885ed17801 | note | Has a minimum clearance of 1m in front and 0.5m to each side been maintained?
699a8cfd-f2ca-532f-bc5c-d82512c6e4a2 | button | Where obstructed by a door, are the words "FIRE PANEL" in contrasting colours? | Yes, No
78ebd9f9-2680-5d5e-9857-c6faff2e446a | note | Note - Where the door reduces the sounder, an external sounder may be required.
55ef4704-0916-52e7-b60a-2664b73d0ef6 | note | Add Photo
f8f8a994-468e-4e3c-ae11-c86d3f8c1003 | checkpoint | 3. CONTROLS AND INDICATION
918f1be4-afb5-5a17-90c9-9bef9a61c061 | note | CIBSE C6.6.0 Brigade Interface – FFCP
3926c011-57ee-5823-b14d-833092bc4739 | note | AS1670 (Section 3.9)
3484dbf2-1939-5e7f-8a01-49b7afc505cf | note | Do you confirm CIE has controls that are:
a67b32e3-aeb4-5aa1-920f-35adef37114e | note | Not less than 750mm from floor level; and
e9129d3e-84f4-5a3f-8a3e-d3c41c66b679 | note | Not more than 1850mm from floor level; and
0fc3beee-dc28-50d8-93b3-ebce9620fba3 | button | The access to controls is not obstructed? | Yes, No
c647317c-a63e-5eac-831e-333911024956 | note | Add Photo
590595ac-de1a-4f22-8876-ce8cb6ea8cca | checkpoint | 4. CLEARANCE
e4702181-a4e0-5de0-9af5-92b5e370d216 | note | CIBSE C5.2.2 Set Point
c7256f8a-8a76-50a9-96f8-67ff7a116294 | note | AS1670
39ead5ba-347f-55b4-8f95-b262c3a0773f | button | Is there a minimum clearance of 1m in front and 0.5m to each side? | Yes, No
87aabc83-e2b3-5b98-826a-d1df4a1b995c | note | Add Photo
6b4046e8-9ed6-4fc7-91a8-afa4c067f4e4 | checkpoint | 5. EXTERNAL ALARM
bd9ebd23-ed53-5192-af34-a8f3b1ccf3a5 | note | CIBSE C5.2.9 Alarm Functions
387fa186-d0ac-5fc1-81c0-483d40da0139 | note | AS1670
321a2678-9130-5e4b-bf34-5911a4aa1f48 | note | Is an external wall mounted VAD is located on the front façade no more than 10m from the DBEP?
7077deef-41f3-590a-b8b7-324bdfabe648 | button | Is it visible from at least TWO directions, and mounted with the words "FIRE"? | Yes, No
6a8809a3-f6b7-5ee8-a19c-d9ed65750124 | note | Add Photo
e85a5720-3b9f-47f1-a814-cefc6de13e72 | checkpoint-no-value | GM Fire Sign Off
59035c79-8526-4182-86d6-f759c602ae69 | signoff | GM Fire Sign Off
a66d13ac-9fe4-44c9-894e-73074c83b94e | checkpoint-no-value | Principal Contractor Sign Off
51190074-8be8-41a7-b16f-3be3acca0d4b | signoff | Principal Contractor Sign Off
f968cdb4-6569-45c1-a60d-5636be32d8b8 | checkpoint-no-value | Consultant Sign Off
8f356735-97e8-4e1c-86ca-675a9a5fd125 | signoff | Consultant Sign Off
8449cf7b-9a46-4e15-8b1e-cb0a086a7af7 | checklist | ITPS-106 Sprinkler Pipework Rough In | itp | ITPS-106 Sprinkler Pipework Rough In
d74d0231-c177-4b58-ab00-76545fd4dbc2 | section | Details
236a894c-8bb9-4a0a-974e-5788674503b5 | checkpoint | 1. PIPE LOCATION & HEIGHT
2456b793-5c4d-52bc-ad14-7f84ac43c779 | note | CIBSE W5.2 State of the System
103126af-d0d4-59e0-8acb-bfec27832475 | note | AS2118.1-2017-Section 14.14
e7e81983-ede5-5e12-9f21-e615c8d012fd | textbox | Drawing Reference and Revision Number:
eb2f727c-8782-588a-9047-1b2b9dbc83c0 | button | Have you reviewed the Fabrication Cut Sheets? | Yes, No
f84cee1e-03f5-55a5-9f53-90f31851f688 | note | Is Pipework setout as per dimensioned install drawing?
71993d7a-e5f4-5c58-9578-68773c9254a2 | note | Are Pipe heights correct?
0cd3aaf2-7db3-5b28-a7c8-c5b16c60d903 | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
d7be83a7-4f8b-5a62-861b-64f0555f359a | note | Add Photo
c5308d2d-517b-4069-a306-d97b550b2ee7 | checkpoint | 2. PIPE SUPPORTS
ffec6e92-9fdf-59eb-95d2-0213e628a2c5 | note | CIBSE W5.2 State of the System
9650b54b-c3c4-51f6-a980-51cf58d835e3 | note | AS2118.1-2017 - Section 7.8
bf28ca8a-fdc4-58cf-bc2f-1d6808d05308 | textbox | Drawing Reference and Revision Number:
a2094162-6820-57e2-8394-54abf2078abc | note | Is the Pipe hanger type as per the install drawing?
1d5b9e78-f620-5daf-9475-4035cfc8bb17 | note | Are Hanger fixings as per the install drawing?
88f60037-7b43-54a5-a0b3-cf152f48332b | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
68dd7468-0905-5008-9190-6b208c12dfd7 | note | Add Photo
0b575eaf-1bdf-4e95-addc-9f82d337b209 | checkpoint | 3. CHECK GROOVES DEPTHS
0afdf17f-4bc7-528e-b630-2931fff732cb | note | CIBSE W5.2 State of the System
a1bc865c-d067-5c20-aae3-5bf4a924f017 | note | AS2118.1-2017 - Section 7.1
057f065b-a79a-5ee9-8fe8-5486281e6463 | note | Are groove depths within tolerance?
2621d0a6-2ba9-569c-bd0b-a295bb404232 | note | Are pipe heights are correct?
ab012590-d212-5f70-826c-c9f6f1751eca | button | Have any pipework alterations been approved and recorded for as-instaslled records? | Yes, No
938b5fc7-a5b4-5657-b395-e8930882cb6d | note | Add Photo
214c81b0-9869-40fe-9dfd-b002c478b36b | checkpoint | HOLD POINT
549d2444-79ae-5882-b955-8910378c19f6 | button | Confirm Safe to Proceed | Yes, No
1326686e-56f6-48c4-89e9-11f0239c0bb1 | signoff | GM Fire Sign Off
77ce082b-a3b7-4a34-8aa4-6b76cf5467b7 | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
24243350-861a-5b45-a8cd-a1d1aa99ecca | note | AS2118.1-2017 Section 7.10.2.2
b1f342cd-caef-501a-8381-a8ce70617e25 | note | CIBSE W5.2 State of the System
a8f5a5d6-a868-5d0c-8c93-33f35c447bd2 | button | Have ONLY Victaulic brand couplings been used? | Yes, No
2476a14a-762e-5e17-ab29-15a088995b02 | note | Add Photo
f462feed-979c-480b-a9e2-86cfae6191ea | checkpoint | 5. CONCEALED SPACE SPRINKLER HEADS
99b60d61-72d1-51fb-bb45-fbc6a9ef3593 | note | CIBSE W5.2 State of the System
5efde3c5-d3fc-548b-bc05-e3fa839c3808 | textbox | Drawing Reference and Revision Number:
7fe7703c-7764-5086-95cf-b6f680dc836a | note | Have ALL concealed space sprinklers been installed as per dimensioned install drawing?
09374021-3b3f-5388-b16a-8a1852700b19 | button | Have the correct sprinkler types and temperatures been used? | Yes, No
9e506230-037b-5d70-80d7-b032cd345d4f | note | Add Photo
75e98c17-6b5e-431e-a28f-ec8c77750360 | checkpoint | 6. EXPOSED SPRINKLER HEADS
a33a88ef-1278-5f05-80c0-399141f2375d | note | CIBSE W5.2 State of the System
0f435fa7-2c9b-5587-9bad-469a8670c3b8 | note | AS2118.1-2017 - Section 5
9a4c0045-5e1e-59db-bbbc-d282b4528dba | textbox | Drawing Reference and Revision Number:
5311e354-e02e-5a90-bc1e-735578ce4ba9 | note | Are exposed sprinkler heads installed as per dimensioned install drawing?
c071230e-24fd-5243-a45a-ff7d7a60e746 | note | Are sprinklers clear of obstructions?
f1223593-b988-534b-b7b3-a5c37e58c7cf | note | Have the correct sprinkler types and temperatures been used?
a581b323-f5a2-507a-aa5d-e6fb0ebd9dce | note | Confirm sprinklers do not exceed the maximum distance from the soffit?
941aff0c-bea3-52e3-82bc-96678fb9a25f | button | Have sprinkler guards been fitted where risk of damage exists? | Yes, No
087ce181-e5c0-5652-9445-86a79ddbcb88 | note | Add Photo
a16bdf77-25a6-442f-a648-f5ac36895585 | checkpoint | 7. FLEXIBLE DROPPERS
0b505266-b9be-53dd-ba3a-f9872c8b5c8b | note | CIBSE W5.2 State of the System
03646378-3a82-571c-aace-671cb271581b | note | AS2118.1-2017 – Section 7.6
4ec3b32e-e966-517b-935b-9994f9d736ba | textbox | Drawing Reference and Revision Number:
beb0e5bd-bdfb-5d8d-bb5d-d00c4d96a6fb | note | Is flexible dropper installed in correct location?
8cdc007c-6623-50f4-abbc-acd98c488c01 | note | Correct sprinkler type and temperature?
ba37b792-5c51-5fc8-aaa8-e342bda6713f | button | Is there sufficient length to reach on-ceiling location? | Yes, No
3032f320-4bc6-5609-b933-f54bbe640c93 | note | Add Photo
f59f090b-5868-4144-b35a-069f55622464 | checkpoint | 8. SPRINKLER INTERFACES - VALVES, & MONITOR SWITCHES
6e42df11-50df-5605-822d-0815e00955d6 | note | CIBSE W5.2 State of the System
6414b438-b1d7-51cc-82c4-8bc48c2c0b38 | note | AS2118.1-2017 – Section 8.13.5
7808d383-1bbf-52d8-b634-957844b19890 | textbox | Drawing Reference and Revision Number:
0ee5f057-7fc0-5867-b0a4-3682726e5099 | note | Have Isolate valves & flow switches been installed?
c58023c3-f013-515e-8668-abaca51d459c | button | Have labels been installed? | Yes, No
b9bffa83-79f6-507f-bfa6-13cc64aaf5a5 | note | Add Photo
e30f05e9-38e8-42dd-9c05-887ee73ad277 | checkpoint | 9. REMOTE TEST DRAIN
f49a89af-f050-55e6-a85a-7f2ebb0bb4e8 | note | CIBSE W5.2 State of the System
e00600a8-f995-5ecc-906b-5efc62f99334 | note | AS2118.1-2017-Section 8.14
d5abe50d-e0eb-5717-b5a7-faf05abfcc99 | textbox | Drawing Reference and Revision Number:
c5a6ae9c-cc87-5c46-8edb-c4b627f6fe6e | note | Is the Remote test valve installed as per dimensioned install drawing?
15968b85-15f2-5675-8c04-458317e41e2b | button | Restricted orifice installed? | Yes, No
b7c411da-663b-5eb5-a640-5211855b2874 | button | Have labels been installed? | Yes, No
02251282-0003-5fe6-a3c4-68fdb7311ca2 | note | Add Photo
f0dbb889-f879-4c98-a710-0a9f727bef7c | checkpoint | 10. SEISMIC
39fee1ca-1592-505c-af14-e46d1392ca23 | note | CIBSE W5.2 State of the System
0d252389-679e-5d9d-a381-d75b15db706c | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
0c810cce-60d1-5ab1-97a0-f5e75cba7a63 | textbox | Drawing Reference and Revision Number:
1806d7f8-8a21-56c0-a775-6453da08f921 | button | Are Seismic braces installed in accordance with Engineered drawing(s)? | Yes, No
5a5a38f3-ba03-5e83-8db9-82cfbfb297d8 | note | Add Photo
c01d7e0b-9ea4-56f5-9130-b7290cac4075 | note | CIBSE W5.2 State of the System
fdae0b2e-3b69-52d8-972a-8e496ace94cb | note | AS2118.1-2017 Section 7.9.6
ed4b0364-86ce-574b-8788-2514e92f2882 | note | Has painted pipe been inspected for damage?
d2951560-9fec-5f46-96f3-db7702a335df | button | Have Repairs to paint been completed where required? | Yes, No
97973bc6-e3bb-539b-93ac-95bccf83bdbf | note | Add Photo
f74fae8b-959b-4ecb-868b-6d30bb1f337b | checkpoint-no-value | GM Fire Sign Off
cd2b9f40-ff85-47d2-80f2-7a2dde2b932b | signoff | GM Fire Sign Off
64d7a32b-2e5f-467e-9a4f-48b9875140c8 | checkpoint-no-value | Principal Contractor Sign Off
2baaf444-06f5-4ab6-bfd1-fa8107c8697e | signoff | Principal Contractor Sign Off
0001ab40-9f96-4785-bc74-487f596f9ac3 | checkpoint-no-value | Consultant Sign Off
8793dde9-89ef-4716-a0c6-e0dbe1a43f48 | signoff | Consultant Sign Off
0c795e49-bee7-49c0-8cbc-1df18658b350 | checklist | ITPS-107 Hydrant Pipework Rough In |  | ITPS-107 Hydrant Pipework Rough In
3e59a1e0-4d8f-4599-a92c-039df9ba78e5 | section | Details
0ac23c52-44a7-4a59-ab08-467678ed0fe5 | checkpoint | 1. PIPE LOCATION, HEIGHT & SIZE
f958e15d-1106-5df9-86f4-f34234792a43 | note | CIBSE W5.2 State of the System
55b693ff-59e1-5ebf-a796-47f1901ba165 | note | AS2419-2005 Section 2
d61337e4-23f1-51bd-a0f2-25804c460737 | textbox | Drawing Reference and Revision Number:
706f50bf-7ad3-5c42-adcc-7b07bee3c4de | note | Is pipework setout as per dimensioned install drawing?
9b109aed-8680-5315-88a4-a604f63b705f | note | Are pipe heights correct?
388bd8bc-c3fc-5461-a98e-ac0ddcafa336 | button | Have pipework alterations been approved and recorded for as-installed records? | Yes, No
99247b0a-1a86-5eb6-bff0-099c7ac7858d | note | Add Photo
c5db8666-978e-402a-a115-f800edab7acb | checkpoint | 2. PIPE HANGERS
99161286-bc39-5a66-b12f-597ef1a0763f | note | CIBSE W5.2 State of the System
f769741a-bb45-5752-a00e-a16228ee8f93 | note | AS2419-2005 Section 8.7
7dea36c3-8476-55eb-9b76-037912403ae0 | textbox | Drawing Reference and Revision Number:
f3252a7e-d956-58da-8076-e211e9b932c4 | note | Is the Pipe hanger type as per the install drawing?
0f5e7f32-fa13-52d8-a450-dab080a97867 | note | Are Hanger fixings as per the install drawing?
af24b6d1-2b50-5643-8274-3ae4797259be | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
0dd543d0-486a-5890-94f1-8b3cd87afdbb | note | Add Photo
66290174-5639-49be-8555-429f6b7d1404 | checkpoint | 3. CHECK GROOVES DEPTHS
d2f4df57-8a75-51e5-8f4a-fafd624a0ee8 | note | CIBSE W5.2 State of the System
a2b53600-f5c9-56c3-a643-11a922624350 | note | AS2419-2005 Section 8
9ce27506-0534-5e74-8ab7-763de6362050 | note | Has Victaulic Groove Tape been used?
e0b34068-d49b-5027-b667-6d3342295d9b | note | Are Groove depths are within tolerance?
12ef2c43-37cf-5c4f-bdce-79714d3fcf29 | note | Are Pipe heights correct?
3d108c13-f928-5476-9e69-68582531249b | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
64ce0667-b55d-5fee-8a09-843f1806deb1 | note | Add Photo
19fe45a8-dff5-4e6e-8b35-70f716b1f2ee | checkpoint | HOLD POINT
49e630b0-ad18-5b7a-aeac-dc437321711c | button | Confirm Safe to Proceed | Yes, No
1ffabab8-0896-424d-8e7c-623b8507eb48 | signoff | GM Fire Sign Off
7d5ad85d-1b03-4798-9127-a3f87726ec22 | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
6b1a79e9-0d4e-5d67-a88b-38dd2e087d66 | note | CIBSE W5.2 State of the System
5fcde182-2038-5f3a-a9e8-3b07f5a6cf2a | note | AS2419-2005 Section 8.3.2
2a8d7cda-a75d-54f1-a81d-f2f2859d90ee | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
ad837ae0-3fc0-5583-a52e-e1f41b41ff76 | note | Add Photo
cad45cd6-3fc0-4554-aad7-3eef05fb9ebc | checkpoint | 5. ISOLATION VALVES INSTALLED
2c17cbc3-068f-52f0-86a9-5d4845179e3c | note | CIBSE W5.2 State of the System
e8a36230-b066-5ed0-840f-d3d8ba063e2e | note | AS2419-2005 Section 8.5.8
127c4780-d043-5688-a78d-d254e90eeb41 | textbox | Drawing Reference and Revision Number:
6c77b3fa-b447-5661-85a5-6c4292c9cb9f | button | Are Isolation valves installed as per install drawing? | Yes, No
40132b89-3ab5-5d0e-a1fc-290e390aa153 | note | Add Photo
45c0f39c-8870-41a0-b466-e5206e6f028c | checkpoint | 6. SEISMIC
e3a23e3e-aeaf-52ad-83ac-fd65b52b4c8c | note | CIBSE W5.2 State of the System
65e82f84-3b29-5af8-93d7-c53bdf745f32 | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
3029755b-9bce-573b-b1ce-d0c88c8c3869 | textbox | Drawing Reference and Revision Number:
e6cb9f3f-0d7f-5fc9-a209-dcf78ee0dc98 | button | Are Seismic braces installed in accordance with engineered drawing? | Yes, No
1cd5e4ae-c417-5e7d-8ce0-2d58cea1a4d1 | note | Add Photo
2a11a4cc-75f3-4368-8259-b75dc8d7ee6b | checkpoint | 7. CLEARANCES
3ab3442b-382b-5252-a068-eb40374a5bd3 | note | CIBSE W5.2 State of the System
87bccf8d-0f9a-525b-ade0-26ef083d6de8 | note | AS2419.1-2005 – Section 3.2
776e17f3-0dae-54af-99db-b012d8072230 | button | Is the Hydrant positioned so it does not obstruct required clearance for egress path? | Yes, No
deed3c27-349b-5e8d-b420-a1d542ec963d | note | Add Photo
dc9cd66d-34d3-403c-80ab-9ed846d6d326 | checkpoint | 8. LANDING VALVE FIT OFF (CLEARANCE HEIGHT/ ANGLE)
43904bfe-c53f-5f5e-a55b-2365fa4d2979 | note | CIBSE W5.2 State of the System
e3feb5db-1ecf-596e-8a29-04a5a9b265ac | note | AS2419-2005 Section 3.5
e5a3df6a-ac4f-5ce6-8fe9-2e129e26f90f | note | Have you checked:
6d3a65e6-b3f1-527f-b870-2bbcfa14d7cb | note | Landing valve height; and
7e95dac2-8a64-5a84-874f-0968ec1e9d79 | note | Landing valve is at the correct angle; and
e0394934-1d21-57f0-87f7-d11a00246070 | note | Coupling angle and orientation is correct; and
946c8c20-7ec8-558a-a502-e224802c0e53 | note | Required clearance for the handwheel has been maintained; and
2d49c3bd-1787-52a5-b096-5e7889a34fa7 | button | The required clearance for the nozzle has been maintained? | Yes, No
d66e4f6c-3960-5b23-bfc4-774ac9bce0e8 | note | Add Photo
3c2bc4f8-1a65-4d12-9fb4-89652a6568dc | checkpoint-no-value | GM Fire Sign Off
e8052464-3366-4a4a-b71e-a5d2c32924c4 | signoff | GM Fire Sign Off
f706ef9e-0ce5-471e-9cb6-cc809899aea5 | checkpoint-no-value | Principal Contractor Sign Off
cccca1a4-195a-4d21-a21a-603f22184ece | signoff | Principal Contractor Sign Off
a6ba95c5-5693-4d78-b439-5b8220b87a3c | checkpoint-no-value | Consultant Sign Off
e62754c6-20e1-4c96-ae67-449460096d58 | signoff | Consultant Sign Off
5a40887b-a75a-4fc0-a796-0274cae3183f | checklist | ITPS-108 Sprinkler Fit Off |  | ITPS-108 Sprinkler Fit Off
234b3da1-9b11-45e2-9b22-e04d3c9e1876 | section | Details
70a7f72e-9153-417c-9d3c-6db0d34c767a | checkpoint | 1. SPRINKLER LOCATION
2e0be333-4007-5a63-aa55-9fef3c1f22b4 | note | CIBSE W5.2 State of the System
e8d7148b-7cf0-532a-a050-41ee5dc65e80 | note | AS2118.1-2017
7a0d9ca2-9e76-55cf-a3d3-a8d8d4d42639 | textbox | Drawing Reference and Revision Number:
747a5e6c-1161-59ba-b571-a17c2a56ef44 | note | Is the location as per dimensioned reflected on the ceiling plan/ install plan?
07c823ea-3ed5-579e-a623-7fe491e20767 | note | Are the Sprinkler temperatures and finishes appropriate for the environment?
6651626a-feaf-591f-aaa6-3c479620e2f8 | note | Maximum spacing from walls is not exceeded
05fa06cc-20ff-5a84-8be2-07e8dc37133c | note | Is the wall spacing within requirements?
fec7f738-bfc1-5346-ae66-2cd3081cb311 | button | Is the spacing between sprinklers within requirements? | Yes, No
d3d26620-3cf0-5737-9353-631e4b94e25c | note | Add Photo
233b4f66-dbcf-4337-ba87-ad98fe621759 | checkpoint | 2. SOLID SPRINKLER DROPPERS
692a1941-7372-5357-9a90-0da04d79fe68 | note | CIBSE W5.2 State of the System
2ef2793b-6a30-5497-bdee-872c8421ca69 | note | Is the arm piece supported by hangers?
ee398756-7097-5cd9-aa28-92ef7cc1598e | note | Is Dropper square?
59a1591d-869b-5a36-9269-bfe7f546d2d5 | button | Is the finished sprinkler height compliant? | Yes, No
68c12985-17be-5341-aac5-b0d32fa9e02f | note | Add Photo
46c7177c-1e74-4475-8f17-b9e0cff4a667 | checkpoint | 3. FLEXIBLE SPRINKLER DROPPERS
928ff8e0-28a9-534f-b940-9263db0643d7 | note | CIBSE W5.2 State of the System
7ad4c85a-4d94-59b4-a554-baf707e152eb | textbox | AS2118.1-2017
e935086a-c315-5e84-afd9-1f52c70b9bda | note | Has the appropriate lengthed dropper been used?
39440161-9f7c-57d1-a1f6-8a131db66f15 | note | Are Sweeping bends within tolerances?
06180c21-2a81-5ac2-a426-f1104a72668f | note | Was the correct bracket used to secure nozzle?
9dfb913b-7da3-5c10-90af-d12b9a4d1e3f | button | Is the finished height compliant? | Yes, No
6f5b6d64-1635-56ac-883e-3fded0afea8f | note | Add Photo
04cb8383-72ac-4b7b-9669-61e3abea66ad | checkpoint | 4. OBSTRUCTIONS
7cf72482-2acd-5dff-ac16-561853964b9f | note | CIBSE W5.2 State of the System
90499cfa-c00a-56bd-93ae-86d1b1083bd6 | note | AS2118.1-2017
965c4f51-5789-5a4b-8c78-61273bfa8d09 | note | Has minimum clearance been maintained for 'On Ceiling' obstructions?
05a46692-515c-526f-abb2-8eac2a4a19f8 | button | Has minimum clearance from sprinkler been maintained for 'Below Ceiling' obstructions? | Yes, No
e7deadb6-e762-5b43-994f-46762bc3d4a7 | note | Add Photo
e21a7190-4484-4ee4-9f13-b80972283e02 | checkpoint | 5. ESCUTCHEON PLATES
aacc86dc-14cb-56eb-8578-4444ba597b95 | note | CIBSE W5.2 State of the System
014a4d7f-59f2-5194-a07b-a0c483f2d238 | note | AS2118.1-2017
90644d00-d3b4-5466-9a33-757c2c647bac | note | Have outer escutcheon plates been fitted?
aded4757-04ac-5d56-b697-c5d377097ed8 | button | Is surrounding ceiling clean? | Yes, No
7af5dc7c-4a62-523b-8bf1-4a6084675283 | note | Add Photo
ebf9c6d9-563a-4b6d-8018-d8506e719731 | checkpoint-no-value | GM Fire Sign Off
7b9df830-9c13-498a-bd5c-169ff50c8956 | signoff | GM Fire Sign Off
26b1e970-d89a-41e0-85d1-7862be81df97 | checkpoint-no-value | Principal Contractor Sign Off
7772faea-4539-45d1-8376-6db4f3712be7 | signoff | Principal Contractor Sign Off
d7cca11d-7cac-44f3-b711-1a592bb48079 | checkpoint-no-value | Consultant Sign Off
4a9feecd-adbb-4a29-8d0c-f7fb381801e2 | signoff | Consultant Sign Off
00dde9dd-68ac-48e1-9e97-99f012faefff | checklist | ITPS-109 Portables Fit off |  | ITPS-109 Portables Fit off
e12fa677-4a9b-490a-98a3-b6b322a1df3e | section | Details
f60e5fae-ce35-4f23-ab70-c6cd8ed9eed2 | checkpoint | 1. FIRE EXTINGUISHERS - GENERAL LOCATION
ad270483-b93c-5a2e-85ea-d97f74d49a69 | note | CIBSE C5.2.2 Set Points
167b9816-7d3f-5180-ad96-71c8caaddb02 | note | AS2444-2001 - Section 3.2 states extinguishers shall not be located in positions where access could present a hazard to the potential user.
cfcc54df-b677-53a9-bf9b-7a61b511364f | note | Is each extinguisher located in a conspicuous and readily accessible position?
a0f15f33-4548-5855-8c5a-62f742b0b5f6 | button | Where practicable, are extinguishers located along normal paths of travel and near exits? | Yes, No
33f0da4b-e099-5ebd-b6f1-5cdd6977a7f4 | note | Add Photo
1f66f425-cc37-4961-a56f-08b704b141a6 | checkpoint | 2. FIRE EXTINGUISHERS - MOUNTING DETAILS
111294e0-30de-5626-89d9-fbaed6aab842 | note | CIBSE C5.2.2 Set Points
ea5a4a2e-f209-56f8-ac94-90fb2fada9ba | note | AS2444-2001 - Figure 3.2
e2cf3205-9987-512a-a5d8-87ee8a1e60e1 | note | Have Location Signs been installed at a Minimum of 2000mm off the FFL?
b5ea8b7f-2849-5da7-8f6d-bba4299d50c5 | note | Are extinguishers installed at a maximum of 1200mm to the top most part of the extinguisher?
4bd85a16-bb55-52f0-b179-ce1f4fffd8c0 | button | Are extinguishers installed at a minimum of 100mm from the FFL to the bottom most part of the extinguisher? | Yes, No
643b6806-2b8e-5f6d-ac90-9243e5c1d89b | note | Add Photo
6c0c3126-cf75-43c2-baae-635d5ddbc84d | checkpoint | 3. FIRE EXTINGUISHERS - VISABILITY & SIGNAGE
a8a47905-1c5d-5551-9781-9f649b0b3244 | note | CIBSE C5.2.2 Set Points
2620ff91-d648-5f01-85e4-73ea77924d56 | note | AS2444-2001 -Section 3.4
952fc3bb-2205-5675-b650-b78119073206 | note | Are extinguishers, or extinguisher location signs, visible from a distance up to 20m in all directions?
52f4c80d-0823-55bd-a64b-3f6034015a8c | button | Are the location and type of extinguisher signs installed as required? | Yes, No
29a416e2-1b64-5170-8d18-67d1423d19c0 | note | Add Photo
d1761d17-3052-4242-b0b3-35caa98e35a7 | checkpoint | 4. FIRE BLANKETS - GENERAL LOCATION
7ad8e88e-e2fa-5377-bbec-9554781b8bc1 | note | CIBSE C5.2.2 Set Points
bdcf0e54-0707-5d15-adf1-8cc6929aeb39 | note | AS2444-2001 - Section 6
441e9b85-7bf1-5b6d-a796-9e3a88be514d | button | Are Fire Blankets installed in a readily accessible position, and not in a location where access could present a hazard to the potential user? | Yes, No
4a10e1b8-8677-5d17-a0b4-15f806c52ef4 | note | Add Photo
5bd262d6-1218-4c7f-834c-b2ed4b49e5e0 | checkpoint | 5. FIRE BLANKETS - MOUNTING DETAILS
935d0fda-8b75-5fc6-ae86-d69a2df159d5 | note | CIBSE C5.2.2 Set Points
dcd4d8a7-39f2-531a-8ea2-cbf1ca27f698 | note | AS2444-2001 - Section 6
40094666-7cf1-5861-a5b7-55c20e63e0fc | note | Have Fire Blankets been mounted to withstand the loads imposed when removing the fire blanket from its container?
077085ad-4334-5963-86c9-32333411498e | button | Is there sufficient room so that fire blankets can be quickly removed without impedance from nearby obstructions? | Yes, No
3dca33ef-3f1f-501a-80bf-a5f0317c31cb | note | Add Photo
11cb7020-9376-49d9-9b7a-eb5e8740f792 | checkpoint | 6. FIRE BLANKETS - SIGNAGE
1e243e16-84be-59d5-9a5e-dea153c09f57 | note | CIBSE C5.2.2 Set Points
6befe1f2-6285-5ad3-9c3b-0d8ae131452e | note | AS2444-2001 - Section 6
4f0cc6f9-f06e-5ebe-b4d2-b0742560fe48 | note | Are signs located above or adjacent to fire blankets?
bbb46cb6-0179-5f10-a955-18777f6ebf6c | button | Are signs 2.0m above floor, or at a height that makes them most apparent to the average person? | Yes, No
232e4324-7b2d-544c-b25a-c696a5edcd5d | note | Add Photo
fe93aff5-b77a-4d2e-937c-fb80dca9de0b | checkpoint-no-value | GM Fire Sign Off
66be7f49-e8b1-49cb-9403-9e15dd7500e5 | signoff | GM Fire Sign Off
c02b7b70-f9db-4c62-814d-d37fe27275ce | checkpoint-no-value | Principal Contractor Sign Off
dbd8ace0-1c41-4153-a42f-82908848ed06 | signoff | Principal Contractor Sign Off
802ec990-911e-4ce8-a6fc-b3bb55e6311f | checkpoint-no-value | Consultant Sign Off
9f01d9ec-e33c-45eb-a422-bcde93280eea | signoff | Consultant Sign Off
bb01ca36-863d-458b-a6a0-c59372d39213 | checklist | ITPS-110 Valve Set Installation & Fit Off |  | ITPS-110 Valve Set Installation & Fit Off
5cf0d1da-a6d0-4576-9434-c89d7efb547a | section | Details
e2a6b1c7-a04d-4ad5-b3ee-0dcb6d1d8c3c | checkpoint | 1. UNDERGROUND SUPPLY
b6374541-2542-533c-8a67-3b9b3ee948f3 | note | CIBSE W5.5.2 Flushing Procedure
9de304a4-a5ab-5919-89e0-31ef9da1ab61 | note | AS2118.1-2017 - Section 7.9.7
01c2aad2-42b8-5919-8e5b-ec0f9666a2dc | button | Has all supply pipework has been flushed by a hydraulic contractor? | Yes, No
212f121e-9b96-5258-ba02-e76d793fcb5c | note | Add Photos
26844a61-0064-44e1-abcb-136809248e75 | checkpoint | 2. CHECK GROOVES DEPTHS
53b54408-d2a4-5beb-909b-6ca5c49a1345 | note | CIBSE W5.2 State of the System
bd901d7f-e837-52f9-bcd6-622c0343ebb5 | note | AS2118.1-2017 - SPRINKLERS: Section 7.1 | Yes, No
afdac93e-09bd-5b42-8eb7-aa9cf291cd90 | note | Has Victaulic Groove Tape been used?
8805fef2-8447-571d-b71e-95a103deb82c | note | Are Groove depths are within tolerance?
169eae0f-9400-5cd3-ab11-24b031a11427 | note | Are Pipe heights correct?
46fc9fbd-acdc-5172-a6cc-32f893a59fbf | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
a58e39c3-9c6a-5961-9eb2-eb987cf91b2f | note | Add Photo
47e34741-7466-46d9-840b-ade0f1cb7e54 | checkpoint | HOLD POINT
5d00d0a3-c51a-57f0-9baf-9501fefac97d | button | Confirm Safe to Proceed | Yes, No
935ff6de-ce61-4a8e-a4e2-70a03cd2672a | signoff | GM Fire Sign Off
9aa6e61f-bc1d-4845-8a75-134e99c9f575 | checkpoint | 3. VICTUALIC COUPLINGS INSTALLED
f01cc90d-2c39-5820-a6d1-b69066e8600d | note | CIBSE W5.2 State of the System
137f6cca-a77d-5d39-ba04-761588742d67 | note | AS2419-2005 Section 8.3.2
6e25dcc9-75e0-525a-8242-eafcc5e8e239 | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
0ef408db-9333-5d18-8a6e-3966bde024d6 | note | Add Photo
57cd9de7-ac94-4b95-9ca1-1406829fa4e2 | checkpoint | 4. CONTROL VALVE ASSEMBLY
f13cced5-61d8-5a6d-8019-e554622677d1 | note | CIBSE W5.2 State of the System
28ef570a-f9b6-5566-9d42-13782bf60452 | note | AS2118.1-2017 - Section 8.1
b3c238c8-32fe-583d-a1d7-dac97bca7fb9 | textbox | Drawing Reference and Revision Number:
e5df0275-b626-52d2-bec6-3e019fe0c48a | button | Is the assembly is installed as per drawing? | Yes, No
e2fe0199-f4af-5dbc-9874-84d978867b32 | note | Add Photo
5d40cb52-6640-4fc0-acd2-4d15b99fb542 | checkpoint | 5. PIPE SUPPORT
b7fc8bf8-e824-586d-94a4-57f9941059d6 | note | CIBSE W5.2 State of the System
e21a5bfb-a103-5a33-aed3-7063111e7236 | note | AS2118.1-2017 - Section 7.8
03b4aa9d-b4a1-5212-b1c0-cae7271202a6 | note | Are pipework supports as per drawing?
b4076e7f-1109-5eb0-b811-af641c9d154a | note | Are the supports capable of supporting assembly weight?
d7f3bb2d-7785-516d-9e36-9393374f8741 | button | Are the supports capable of withstanding forces during operation? | Yes, No
daa04915-9b34-56ff-a605-be7f7351a54e | note | Add Photo
23adce76-6ba7-4a83-b5ca-1467811f7200 | checkpoint | 6. VALVES
36479684-f2d9-5605-ab21-1d9a3eaff86d | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
78f1815f-7616-5733-9ff7-b3c1a0322950 | note | AS2118.1-2017 – Section 8
b9553e4a-ce8a-5ae5-8049-cc5b6eb0d1ce | note | Are Valves installed as per drawing?
947a411c-c759-503e-b433-ab426b263b2c | note | Are valves are installed in the correct orientation?
7111a466-5f4d-5a58-a9f3-12b9041f100f | button | Does the clearance allow for manual operation and future maintenance requirements? | Yes, No
375c99c7-0d59-55ed-b521-236af471ba7f | note | Add Photo
8ad8d903-db36-4e7e-a026-9373682f5e36 | checkpoint | 7. INTERFACES
020bb157-d076-5585-9c5f-8003170664a0 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
71aef719-c807-541d-942e-53b69f13427e | note | AS2118.1-2017 – Appendix H
91303f7a-3f36-5fde-834a-85d2a7195efd | note | Are valves/switches installed for connection by other trades?
6a2bb1eb-2549-55a8-a9c4-7d76405be0a5 | button | Have clearances been provided for connection? | Yes, No
dbecf847-9221-5a4b-baea-409b37132d28 | note | Add Photo
e6980012-791e-4c50-b045-a9d114bf99db | checkpoint | 8. PAINT / FINISH
e1f641b9-2fc8-5b76-b831-1b4c018f63d8 | note | CIBSE W5.2 State of the System
6ec21ec2-8d6b-5b79-9e80-b28558a9ccc6 | note | AS2118.1-2017 Section 7.9.6
e88c1bcc-082b-560d-b117-b26d4e0a0734 | note | Are exposed mild steel pipes painted gloss red (unless specified another colour or galvanised pipe)?
bc8b729e-0441-5ffa-947c-95496850ac2c | button | Have threads been de-hemped and tidied? | Yes, No
fecf4cbb-e78e-57f7-b774-44e95879cd0d | note | Add Photo
147678b9-35ab-5716-ad6d-52ea3463155e | note | Add Photo
1abcc62e-233f-423d-9eea-696bce1ec04f | checkpoint | 9. SECURING VALVES
3390ba6f-15d5-59cf-af68-22beb56bf80c | note | CIBSE W5.2 State of the System
7ec5e634-3b7a-55db-8cdf-18c3aebd4b80 | note | AS2118.1-2017 – Section 8
6b9de9e7-5703-548a-a783-337d88ae22cb | note | Are valves secured by 003 locks?
a5c56a11-b7f4-500a-a870-bbaf2c0eed37 | button | Have straps and chain been installed? | Yes, No
a547e5db-5191-5a01-bbab-58fbacab23f7 | note | Add Photo
27e27933-53c1-4c4b-8c07-8c62ce541289 | checkpoint | 9. SECURING VALVES
c28bcd8e-3af7-584b-a30f-3d9a742767e1 | note | CIBSE W5.2 State of the System
8cf977ef-fe3d-537b-a146-19f1b8ba674c | note | AS2118.1-2017 – Section 8
ddb969a0-a8a0-5585-9bf3-c8a8af7e515f | note | Are valves secured by 003 locks?
a993617b-a652-511a-bbe5-0a45e316627c | button | Have straps and chain been installed? | Yes, No
eae0f18b-a4c2-54cc-8b1c-11f202833958 | note | Add Photo
cc9a759b-a812-410b-93f4-c1407cbc1ce1 | checkpoint | 10. LABELS & SIGNAGE
e4e11986-d51a-5eb7-8000-e0e91187a46d | note | CIBSE W5.2 State of the System
de658e3a-6cad-5377-ace9-5aa7abdb4d98 | note | AS2118.1-2017 - Section 3 (3.3.4)
599bf137-261f-5e4d-8fef-670ddac97289 | note | Are Equipment name labels secured?
602b5fe6-ce5c-585d-bf7e-2a3d85bf0cf3 | note | Are Valve position labels secured (normally open / normally closed)?
c12a5761-0dc0-568c-8d89-2c8d4f72bdc9 | note | Have "Sprinkler Stop Valve Inside" signs been fixed at the valve set enclosure entry?
ed4b3373-f338-510b-924a-b95a113d0a7d | button | Has the Sprinkler Block Plan been installed? | Yes, No
42d03394-8944-5c24-9872-f0cd757e5544 | note | Add Photo
c0b1f16b-8ae3-45cc-adcf-d98494a75d4c | checkpoint | 11. SPARES
b09f312f-2dab-5868-acba-0a1bcab760c4 | note | CIBSE W5.2 State of the System
bc9c1b9b-349d-590d-aeab-94680d1dafb7 | note | AS2118.1-2017 – Section 6.7
3cbf7fa6-4d8e-5bbc-b22c-fd1e94eb194c | note | Has the correct size sprinkler spares box been installed?
fde51ba3-6873-5a1e-9ec5-f0094fb5be94 | note | Have the correct number of sprinklers been provided?
05320163-ea7e-531e-8ba8-bd22307eaa4f | button | Has a sprinkler spanner been provided? | Yes, No
8fbadea2-f86e-5edd-a0ab-9e98cd094b4e | note | Add Photo
4250d7e1-97e6-45bc-967e-ee95b6d5ea7f | checkpoint-no-value | GM Fire Sign Off
455c5c6c-b860-47bd-88d0-0fe376eb45ac | signoff | GM Fire Sign Off
9507a9c1-d791-447a-89f4-2d7df55e316e | checkpoint-no-value | Principal Contractor Sign Off
9cc409f0-2d9f-44bb-acce-067d7fb4cd0b | signoff | Principal Contractor Sign Off
75f95d14-2601-4a4e-a7a8-5714e330d1a6 | checkpoint-no-value | Consultant Sign Off
dac654ef-30fb-4cd8-9110-d297acdc8103 | signoff | Consultant Sign Off
ed268f41-5a3d-489e-8b57-75575f55d67c | checklist | ITPS-111 Tank Installation |  | ITPS-111 Tank Installation
623a716b-0011-4d8e-848b-5d16d5b0f346 | section | Details
6dfd4879-eed6-4b4b-bf69-a8c6abc8782f | checkpoint | 1. LOCATION, CLEARANCE, ELEVATIONS
8fd7ad17-bf8f-50b6-9fc3-395acbff39a8 | note | CIBSE W5.5 Pre - Commissioning
1110ce44-fc78-5875-aba6-708f44accde1 | note | AS2304 - Water Storage Tanks
0ce0dd84-8408-5905-8e23-d249de79d029 | textbox | Drawing Reference and Revision Number:
8c5d09da-54ca-5178-81d1-7d26c66c5078 | note | Are Structural Elements as per AS2304 – Section 3?
62c92cfe-465b-56e9-bdf6-f2a766f9a072 | note | Is the correct Installation drawing onsite?
ce759f85-d4fa-5416-aca4-db4c5a46860d | note | Is Ladder selection and orientation as per the submitted design drawings?
b5612982-50b2-53fd-8c7e-12dacf4047c3 | note | Is Nozzle selection as per submitted design drawings?
de340f73-5c60-564f-8da5-e98e0686cb9c | note | Has the poisition of the Tanks been confirmed with the Principal Contractor onsite?
dd386b77-beb5-5d93-b7c2-426fe3abc4bb | button | Have you check the subcontractors Competencies and Authority to work? | Yes, No
1d8a5e44-da29-5dc7-a003-ee62a7cac81f | note | Add Photo
70f863a7-918d-4141-b3c4-18b8cd715d35 | checkpoint | 2. COMMISSIONING
965d0af8-9865-5eb5-8526-1db4cc45ab76 | note | CIBSE W7.10 Commissioning Certification
befc5e84-0d36-5e52-833b-9aeb8fb91eab | note | AS2304 - Water Storage Tanks
07b5ef77-16ce-5f5d-b3ed-59df2ed3c1fa | note | RECORD, CHECK, INSPECT
677376a2-3882-5ac9-8a65-1cd21b4d5cb5 | note | Structural inspection was complete prior to filling; and
121f906a-01ef-5f0d-986b-e05c4af296be | note | All ladders have been inspected for conformance and clearances and position of tank accessories (AS2304); and
a431b4b2-d743-5626-afc3-41f6c25d54cf | note | Hydrostatic inspection was performed after tank is filled to maximum capacity; and
a6944519-d594-5d7f-95e9-ae82fe02da1a | note | Any defects have been recorded; and
66366ac1-4a3e-532f-be32-6b433daf903b | button | Have Certificates and warranty periods been submitted? | Yes, No
d765cf86-a050-53c3-9a97-1540faeffe1f | note | Add Photo
1ccc5462-c198-4898-9a02-4d3d2fabb9fb | checkpoint-no-value | GM Fire Sign Off
2f176571-d03c-4992-acf0-ffc8727708db | signoff | GM Fire Sign Off
d2dcbf75-ff29-4a6f-bd97-032b8d4574ff | checkpoint-no-value | Principal Contractor Sign Off
994684c2-bcf8-410d-80e1-6655e7697ef7 | signoff | Principal Contractor Sign Off
dc16a54e-ead8-4c46-9535-7b63d359ff92 | checkpoint-no-value | Consultant Sign Off
9d71f682-3b5a-4a0b-87c2-82949ee4b186 | signoff | Consultant Sign Off
8354ae5f-90f5-4c7b-a0a2-42e8938ff141 | checklist | ITPS-112 Deluge Rough In and Fit Off |  | ITPS-112 Deluge Rough In and Fit Off
124ca26b-6e8e-48c8-a69e-02df44cee828 | section | Details
a958a823-31d5-45b1-a58d-ac003e078971 | checkpoint | 1. LOCATION - VALVESETS
6443b598-6b3c-5bbc-a589-ccbd94cd836d | note | CIBSE W5.2 State of the System
345ffbae-d453-5f65-bd7f-2fc163f625a3 | note | AS2118.3
17e714dd-7bb5-5ea4-bb3a-c51be072af48 | textbox | Drawing Reference and Revision Number:
95ecea19-4767-546a-8192-2ad606f52929 | note | CHECK:
c31f62f0-1a7f-5af2-9dfd-86e5b99a1d09 | note | Valves located outside building shall be considered protected if the external wall has a FLR of 60/60/60 or be situated at a minimum distance of 10 m from the wall.
8b20e0bf-0e01-5d60-bd0e-e51d2bcf4104 | note | Valves located inside the building shall be situated at a minimum distance of 10mfrom the perimeter of the protected area.
0c2b6a25-6e19-5a91-ab2f-4359d3e750a7 | note | TRANSIT TIME:
9db55765-4a87-5088-b3ca-ac5468e3ecdc | note | Deluge valves shall be located as close as practicable to the system they are controlling. This will help ensure that the transit time to the most remote zone is no more than 30 s.
b10f4011-0223-5122-b5fc-e44927144eec | note | Add Photo
20729ebd-0c8b-448d-b9fd-6a0240be8004 | checkpoint | 2. LOCATION- DELUGE HEADS
51e3cdcb-8427-5d70-a955-586916b1e1af | note | CIBSE W5.2 State of the System
3bf1b6d6-7225-5f42-928e-9be6a3377023 | textbox | Drawing Reference and Revision Number:
bbb75322-1289-5cca-b24f-b667fb7d0394 | note | Are Deluge heads located as per dimensioned reflected ceiling plan / install plan?
b9067f60-be70-5740-8df4-b6e23e6e7483 | note | Confirm sprinkler temperature and finish are appropriate for environment; and
582370c0-4101-5bc9-b30d-96e070489e17 | note | Maximum spacing from walls has not been exceeded; and
6aeb92a9-f3e9-500d-97a1-df671f8ee856 | note | Maximum spacing between sprinklers has not been exceeded; and
c365758c-c1bd-55a5-8899-1c743ebdbec0 | button | All is as per manufacturers detail and FER? | Yes, No
d77a0073-3939-5d1a-81cc-991f25124b72 | note | Add Photo
f5073a28-38b7-49b5-a400-de6aa425c4ea | checkpoint | 3. DELUGE HEADS & PIPEWORK
4c2fff74-fbdd-5a57-8c25-68ab77855668 | note | CIBSE W5.2 State of the System
311152fc-620f-5f1e-bb79-deb3fe367e06 | note | AS2118.3
1c22b47b-6201-53ee-acca-34b357632579 | note | Open sprinklers are be nominally 15 mm or 20 mm diameter, and either upright spray (SSU) or pendent spray (SSP) pattern only.
50627edf-f4b8-5ac9-a3ee-b747833a99bc | note | Deluge system pipe and fittings not normally filled with water or foam solution shall be hot-dipped galvanized.
770a65a9-2fc4-5dec-a9f3-c7462175d261 | textbox | Deluge Sprinkler Head Type:
e884840a-5bb5-5ac7-8a5c-713ee3d87322 | note | Add Photo
7bb3f0f1-ca75-478e-a888-816bda5baf0b | checkpoint | 4. WHERE SPRINKLERS ARE USED AS DETECTORS - SYSTEM PARAMETRES CHECK
eadaedf9-da50-5e02-95e1-1d8282a73650 | note | CIBSE W5.2 State of the System
b107ccdc-9d80-5641-ad39-9c26d345d79f | note | AS2118.3 Section 2.9
056ef724-b0b2-5869-be22-cfcda3f0af05 | note | Where sprinklers are used as detectors, ensure the piping layout shall be designed to ensure a response time of no more than 20sec after the operation of the most remote sprinkler or manual operation.
db50d9e9-9715-5a0c-82f3-4f970f090b75 | note | Manual control shall be located at each deluge valve and at a strategic point/s within each zone.
e9733212-0d92-5451-9451-08495cf84b02 | note | Deluge valve trim shall be in accordance with figures 2 &3 in AS2118.3.
973a12c2-83b3-5eb5-b060-ccefd4f8c353 | button | Ensure a remote test drain line is installed (close piping deluge systems) | Yes, No
a2c53019-fe48-51d3-b133-5f35c57cb9fd | note | Add Photo
a4c4d25e-0366-4b62-931a-8769bfa99a67 | checkpoint | 5. SOLID SPRINKLER DROPPERS
8cef6dfc-7e7e-5029-95fc-eef358b1fc9f | note | CIBSE W5.2 State of the System
8246ab0b-e10b-56ae-8643-421e532d6473 | note | Is arm piece supported by hangers?
f83c910c-600b-5d2f-b63a-98c9426283be | note | Is the dropper square?
3c6d6c61-9852-586c-a06e-461c6c5703cf | button | Is the finished sprinkler height compliant? | Yes, No
57d4d028-74df-54bf-af7d-345ca8c0016c | note | Add Photo
a8ea6986-f208-42a0-bd58-d83c4b54df87 | checkpoint | 6. OBSTRUCTIONS
790a4ff4-eac6-5591-9f88-4ac60c91ca70 | note | CIBSE W5.2 State of the System
c3b2d9bb-10e4-5328-a6a8-41c340c8f317 | note | Has minimum clearance been maintained for "On Ceiling" Obstructions?
720645f7-ed96-5792-994e-b9e2a666c860 | button | Has minimum clearance from the Sprinkler been maintained for "Below Ceiling" Obstructions? | Yes, No
7c9ff08a-a4a8-4354-a75f-9a910714df65 | checkpoint-no-value | GM Fire Sign Off
154a3065-d9df-4b03-bc59-41bccdfa7885 | signoff | GM Fire Sign Off
9c0300f9-8f2a-44d7-9767-26cca5400106 | checkpoint-no-value | Principal Contractor Sign Off
f3ac7e46-2802-4581-9b53-e9e28d541a6f | signoff | Principal Contractor Sign Off
640c0d10-91aa-48eb-9482-1ac534b41fe0 | checkpoint-no-value | Consultant Sign Off
214d4b32-c4d1-47a0-9fa0-02c3edb8dd49 | signoff | Consultant Sign Off
d894f2d3-05c5-4a44-b567-91bfd8032595 | checklist | ITPS-113 In Slab Sprinkler Sleeves |  | ITPS-113 In Slab Sprinkler Sleeves
f5954829-995f-4483-91b6-2907d3c33bef | section | Details
6f06e21e-31f3-4d7f-b722-2284326f91e5 | checkpoint | 1. TYPE, SIZE, QUANTITY - CHECK
243c7b35-72b1-594c-9975-a1b8819542cb | note | CIBSE W5.2 State of the System
d6110972-f068-5004-bb5f-e96d8aca3a17 | note | AS2118.1-2017
d2085b64-15d6-55d5-8afa-223fd0bf97a9 | button | Are sleeves the correct size, type and quantity to criteria and specified drawings? | Yes, No
02219e56-25d6-575f-900f-77ab6c8ec0bf | note | Section 9.5.2
42855e17-6826-5c92-af8f-135a01b47464 | note | Has pipe with a minumum DN 25 been used;
fe65682c-acde-58f8-8c8c-66331158aa08 | button | Or where a pipe supplies a single sprinkler protecting an external balcony, canopy or carport, or supplies a single exposure sprinkler, a minimum of DN 20? | Yes, No
37db351f-6407-5fcb-873e-32523f0078a8 | note | Add Photo
bf749157-a4a9-4d2c-a013-425eb044d202 | checkpoint | 2. LOCATION - CHECK
f6e45a7b-4149-5a88-b0e2-484fa1f8e139 | note | CIBSE W5.2 State of the System
a3673a20-e1d5-5bd4-a679-e1ae94b1b1e2 | button | Have sleeves been installed as per specified layout and design criteria? | Yes, No
21a3f283-52bb-5360-9e3d-ac9fed248b9f | note | Add Photo
bc49f1bf-f7ea-4077-835a-95f1aa598495 | checkpoint | 3. INSTALLATION - CHECK
415d5f40-a9d9-5edd-b371-79295ae9ad53 | note | CIBSE W5.2 State of the System
82aebf64-d971-5d3e-99b6-cc7f76bfddd2 | note | Are sleeves joined correctly and tied in?
0e7563db-47e9-5a53-b21c-cdf0a229078e | note | Have sleeves been checked for damaged?
cb617901-26a7-5e6f-84e4-a297b3a451de | button | Have you ensured sleeves are not resting on form work? | Yes, No
f3f12c5f-7393-5bb2-aaff-c785478370b7 | note | Add Photo
73a229a2-72f0-4fde-afd0-9bbc00a07d24 | checkpoint-no-value | GM Fire Sign Off
2da2d42a-2859-4478-9fa2-2cdea754fa0a | signoff | GM Fire Sign Off
28630a3a-b974-442a-a5a3-91440deca5de | checkpoint-no-value | Principal Contractor Sign Off
a51109a5-5c3c-4533-855c-5f83b952786c | signoff | Principal Contractor Sign Off
f2302eb3-eb2b-48f9-b42d-ebd1972d4ac3 | checkpoint-no-value | Consultant Sign Off
dffaadb7-7ae0-41ff-b114-7dc1313602c3 | signoff | Consultant Sign Off
b3f8d876-8d04-4bfb-b6f8-3ece6a42b64b | checklist | ITPS-114 ASD Rough In |  | ITPS-114 ASD Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e1badfc5-20a2-4292-a246-9d666e35e406 | checkpoint | 1. LOCATION
96293bcd-601f-5099-b179-7820df387ace | note | C5.2.2 Set Points
240e0b02-f2a5-512d-aeed-719b5cd82ed8 | note | AS1670.1
b62f054f-5540-536b-88fe-a8415db829b9 | note | Have you check that the ASD device does not cover an area great than 2000m2?
5b85fbc1-b37a-50e6-a8d4-940785a47ec9 | note | Is the ASD unit in an accessible location with no obstructions?
5e7a188a-3045-521f-8ef3-0d3f8816ce98 | button | Is the ASD unit free from damage? | Yes, No
3f7ea496-93a4-543b-8b3e-d37d8c3a8b09 | note | Add Photo
ad64b55a-cf13-43ac-aba4-9f58259422ac | checkpoint | 2. SAMPLING POINTS
fcc33f1d-526c-5bfc-b000-6a4366a357d5 | note | C5.6.0 Sensors/Detectors
adbff3c1-42cf-58af-8cf6-dd82cc0e6742 | note | AS1670.1
4cadb447-b577-5140-8754-9d7f6b736702 | note | Are ASD points unobstructed, unpainted and free of burrs?
dc23a4f0-66bb-5cfe-90aa-97bbc9aae596 | note | Have ASD points been labelled and identified as required?
5c79e75c-fd3e-5d46-96ec-9bfdfd151303 | note | Are ASD points installed in accordance with spacings of point type detectors?
9b5f6c52-6cb8-5a2d-84a4-6ed5db315d40 | button | Have you confirmed ASD points are no more than 600mm below ceiling? | Yes, No
290c4bdb-cb51-5c14-8846-914bf82522ae | note | Add Photo
8c6d0b77-f05d-4fa8-9c95-90954f1746d0 | checkpoint | 3. EXHAUST
cb7ec973-cf4c-5bd2-8f09-979aa610d46a | note | C5.6.0 Sensors/Detectors
32f14e7b-8123-5059-95d2-1c90cadcb074 | note | AS1670.1
6051106a-90dd-5c74-af2d-2d65acbd5c78 | note | If the ASD is mounted outside the protected area and the potential for pressure differentials can occur between the sampled and exhausted air:
3373095d-cdd2-5c79-8724-a94d454f2995 | button | Are the exhaust outlets returning back to the protected area, or as per system design? | Yes, No, N/A
185a80af-8c3b-54d8-b243-91aed6eb2a93 | note | Add Photo
df4b5b8f-93a3-428f-aaf7-8296f036eab6 | checkpoint | 4. OTHER INSTALLATION REQUIREMENTS
75ed72bf-cb90-5541-96ae-3e9fb9ae3398 | note | C5.2.2 Set Points
119b683b-f5e4-5930-9446-195cb62a5a3e | note | AS3000, AS1670.1, AS3013, AS/CA S009
ce595a9d-bc0d-5c76-8e6d-3b709fe1df16 | note | Are all sampling points AND capillaries red in colour OR have visible red stripes at least 2mm wide at intervals no more than 2m?
97f983e6-c6ad-532e-8bb2-5446adaf5aa1 | button | Is the pipe orientated to ensure identification of markings is visible? | Yes, No
4dae3a81-87cc-5ff6-870d-a6031ccc8d4c | note | Add Photo
84079130-cdcd-42d3-a75d-a84f7ab8ce81 | checkpoint | 5. CABLING
d0a85cce-91ab-5ced-9f3b-991e046c2dbc | note | C5.4.0 Wiring
9dedadb0-a6e6-5bbb-aa8d-d208b97aa461 | note | AS1670.1, AS3000
f333eef3-5e93-5cfb-978a-a062fd6eaf29 | note | Is the cable installed the correct size & type?
f8bac317-5d3f-5214-80cb-79578f3a410f | note | Has cable been secured at regular intervals?
dc92242a-512d-50d7-98ef-385db6220f02 | note | Has 24v cabling been installed where required?
62c822b9-5521-5eb2-bc9f-7aa9fc1e4e1e | button | Is the power supply in accordance with AS1670.1 Cl 3.15? | Yes, No
4294a81c-0832-584f-9031-39385436e2c7 | note | Add Photo
0c0fdea1-6819-4f40-83c8-c18f4aba8ce3 | checkpoint | 6. PIPE LAYOUT
d6517f60-2ee6-5758-ab2e-ba7829cfeb93 | note | C5.2.2 Set Points
16c88fe1-7d9b-5ad3-b971-ffd3a7c3233a | note | AS1670.1
69b3b6da-bf03-5344-9c71-67827eaf5c66 | textbox | Drawing Reference and Revision Number:
7e4c7c94-6620-54e3-8a28-fa6f8388d1b5 | note | Is the ASD pipework as per Aspires or Calculations?
406ba4fd-52e1-52c1-8ec7-bf1b740005f1 | button | Have you confirmed the pipework layout with measurements? | Yes, No
5d2f76a6-4e6f-567c-8b93-cdf557823b12 | textbox | PROVIDE measurements:
de9c195d-de70-5bcc-ba65-9b63b3eb8667 | note | Add Photo
7e245dda-2071-485d-8baa-eb4850b86c6c | checkpoint-no-value | GM Fire Sign Off
d6123e00-354e-40e3-9ae2-62cc2c5a7c10 | signoff | GM Fire Sign Off
36b1e456-9474-4dea-8058-6733839500fd | checkpoint-no-value | Principal Contractor Sign Off
85a43da9-7f85-41a2-b8fb-be35b90387a8 | signoff | Principal Contractor Sign Off
247268db-51d1-4153-8ead-9733ce32d594 | checkpoint-no-value | Consultant Sign Off
1c98bd4b-776e-4a91-a732-dceccb429f1a | signoff | Consultant Sign Off
a50ad4c1-f0ab-431e-9a2f-af34ffec3bb6 | checklist | ITPS-200 Fire Detection and Alarm Commissioning |  | ITPS-200 Fire Detection and Alarm Commissioning
d5be8718-4b5f-4949-8d4a-576b3fefb091 | section | Details
7e987ae1-59aa-48fc-8364-41d9a60aa606 | checkpoint | 1. CONDUCT 100% TESTING OF ZONING
9df221f5-f375-5630-894b-c99b4ce2e7f2 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
07d2a0bf-cc87-57b5-aac0-6eeea43f91b3 | note | CIBSE C5.2.9 Alarm Functions
5e7551a6-dd19-55ae-a839-7b6f4ebe9e6d | note | CIBSE C5.6.0 Sensors/Detectors
0a185605-bf24-5dfc-aa32-c776aabecc76 | note | AS1670.1-2018
8440cdb6-6fbe-5621-b3a1-ceed66f0b5bd | note | Are Detectors activated when tested?
fbd7262c-e4e3-52b3-9ba5-8bf3b9415113 | note | Do indicators function correctly on Detectors and FDCI?
443781d7-6aab-5d36-a060-9f7b597177f3 | button | Has "GMF-COMRPT-001 Fire Detection Zone Commissioning" been completed? | Yes, No
dc7d26dc-155d-525c-98e3-61fca876b6ff | note | Attach relevant photos and a copy of GMF-COMRPT-001 below:
43aab04e-7d22-470c-8aaa-56445c3a5ff7 | checkpoint | 2. CONDUCT 100% TESTING OF SMOKE AND THERMALS
9e4a3b2c-2ae9-5811-8fa6-af2248fd6ac2 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
964d8c07-3531-524f-81e4-1e2d3bf1aaf0 | note | CIBSE C5.2.9 Alarm Functions
966d93b8-4191-531e-999c-6829b3ce3e97 | note | CIBSE C5.6.0 Sensors/Detectors
ffa1f9ed-82e5-5c6c-8ee2-74c64f2ce3b1 | note | AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCI
97b94d3f-69d1-5e60-a7b6-0f5821d913de | note | Are Detectors activated when tested?
ecceab86-5688-5b36-b8f4-f9e031f15cb5 | note | Have all dust covers have been removed from detectors?
9da37cf4-d594-5baf-bd74-f6b45ecfa6c9 | note | Do indicators function correctly on Detectors and FDCI?
f7b58a58-67b9-5cec-9002-081aa764dc11 | button | Has "GMF-COMRPT-002 Fire Detection and Alarms (Smokes, Thermals, Duct Probes)" been completed? | Yes, No
55477679-a485-5831-bd49-f7f6c2183524 | note | Attach relevant photos and a copy of GMF-COMRPT-002 below:
94118bf7-79f8-4e81-8fa7-0bd94bfdd1a4 | checkpoint | 3. CONDUCT 100% TESTING OF MCPS
6ce7a4b6-2074-5cf5-96ad-21eba159a5cc | note | C5.2 Dry Fire Commissioning – Automatic Controls
6e54440b-5f1a-5429-b630-621af3916fac | note | C5.2.9 Alarm Functions
44a770d8-76ee-5e81-9e2b-9e794c976539 | note | C5.10.0 Manual Call Points
1de403a4-8277-5514-8177-97686f5ecc32 | note | AS1670.1-2018
0b770fc0-8e62-5834-8914-d27f92c23db6 | note | Have you checked:
d8329420-5c2f-576b-b608-17f11cbef590 | note | The correct operation of each manual call point; and
d427bd67-a2f7-5a0b-88c7-f54639721f12 | note | That the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and
5e6468c3-63e4-5640-9d8e-348fda441303 | note | That manual call points are not subjected to alarm dependency; and
eb9ebd0c-0359-5377-98e6-24e103abc5de | button | Has "GMF-COMRPT-003 Manual Call Points" been completed? | Yes, No
2170bd19-c01a-5923-a5e2-2b76c5e53d2e | note | Attach relevant photos and a copy of GMF-COMRPT-003 below:
7c9af603-de38-4bae-a6be-639616422b77 | checkpoint | 4. CONDUCT 100% TESTING OF DOOR DEVICES
4d879a5b-cf8f-5435-95d1-63e5d3f094f4 | note | C5.2 Dry Fire Commissioning – Automatic Controls
ada6e55a-ffe3-5e32-adee-a088040f10de | note | C5.2.9 Alarm Functions
7d7fabd4-4a2a-5be2-97ed-542199c29973 | note | C5.8.0 Modules Input/Output
236e619f-0f90-5454-b433-8e7aa302dcfc | note | AS1670.1-2018
e5bbb706-c6d0-5e00-a49c-4940f4e0a824 | note | Has the operation of each device/door release been checked after install?
b01d60ca-5a9b-5916-aa29-ad1ae1e37daf | button | Has "GMF-COMRPT-004 M.D.H / Auto Door Commissioning" been completed? | Yes, No
95319be4-4c89-5a91-b3f8-2ba5c7fc8fea | note | Attach relevant photos and a copy of GMF-COMRPT-004 below:
0d6635f3-0a76-4df4-9e3a-6b4356d6ad6c | checkpoint | 5. CONDUCT 100% TESTING SPEAKERS AND ZONES
a2722f5c-7355-5a15-9243-0df0908a0fa0 | note | C5.2 Dry Fire Commissioning – Automatic Controls
32478eb2-6c8e-5091-91e1-2adfb0bf45c8 | note | C5.2.9 Alarm Functions
b8d0b42f-81fa-5e42-8f70-f36cba4288be | note | AS1670.4-2018
b4fc7428-4910-5520-9ce5-fd16083e970a | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
8443e3bb-98a6-529c-accd-89d13621a5b1 | button | Has "GMF-COMRPT-006 Emergency Warning Commissioning" been completed? | Yes, No
cc4fd777-79d6-502a-b763-6576e9d89f42 | note | Attach relevant photos and a copy of GMF-COMRPT-006 below:
9773768c-27d7-4584-b7c9-321597f3cc29 | checkpoint | 6. CONDUCT 100% TESTING WARDEN INTERCOM PHONES
aaef1534-1ad1-5110-8f85-82515a52dcb7 | note | C5.2 Dry Fire Commissioning – Automatic Controls
52b6569e-2e7b-5b62-b22e-ff7b37413a24 | note | C6.2.8 Warden Intercom Phones
9a3abe2b-8eb9-578b-a4bb-f771fad4546b | note | AS1670.4-2018
60e3156e-7459-5552-a68d-d6543a8e1191 | note | The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP.
d45160d4-5b37-550f-b9c0-533b82f5fb64 | note | The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
87e38406-57ec-5fe5-b11d-0cec5889d32c | button | Has "GMF-COMRPT-007 Warden Intercom Point" been completed? | Yes, No
638238b0-9e15-5a38-8f83-f6a6e885e280 | note | Attach relevant photos and a copy of GMF-COMRPT-007 below:
8b363c2d-8cb5-47f8-a7c5-c8e87ff4ea76 | checkpoint | 7. CONDUCT 100% TESTING CASCADE AND EWIS ZONING
fa85aafc-729b-5ed4-a973-83ec25945df7 | note | C5.2 Dry Fire Commissioning – Automatic Controls
ef6c3fca-20b2-5347-9353-6e94d59c1fc9 | note | C6.2.5 Cascade Sequence
c6c04046-ad0f-5f25-91df-d3e36cb4027c | note | AS1670.4-2018
5de44ae9-3a58-5185-b3fd-7a4926ed8e6c | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
ac117643-e105-5437-862f-0fe25536da6d | button | Has "GMF-COMRPT-005 Emergency Warning Cascade and Matrix" been completed? | Yes, No
14e67293-59c1-5524-918d-34adcee453c1 | note | Attach relevant photos and a copy of GMF-COMRPT-005 below:
37b747d5-76ad-4ab6-9158-d25f0ea75dcf | checkpoint | 8. CONDUCT 100% SPEECH INTELLIGABILITY TESTING
53df6158-258e-5679-9425-333066322ed1 | note | C5.2 Dry Fire Commissioning – Automatic Controls
8efd56a0-b09f-5a9b-b6d7-50c1af45709a | note | C6.2.5 Cascade Sequence
587f7b43-b38e-5711-980a-f6c94835b9ec | note | AS1670.4-2018
e6a7d241-1166-5d3f-895e-0a8064b2a3a2 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
9e6fc990-ee17-533f-858d-439ba05049c4 | button | Has "GMF-COMRPT-008 Speech Intellegability Readings" been completed? | Yes, No
05388431-83a7-5cac-8ce5-c33fcbcbc134 | note | Attach relevant photos and a copy of GMF-COMRPT-008 below:
55d3645f-9e9a-40fe-9bf6-c56865edfccd | checkpoint-no-value | GM Fire Sign Off
e0cd6e80-68e7-4a84-8c56-c0be6f5b4485 | signoff | GM Fire Sign Off
13a1730b-b0db-4ef7-b93e-ed8f53c203ba | checkpoint-no-value | Principal Contractor Sign Off
9b09c128-f01c-4e8c-b5b9-c27cb5831a6e | signoff | Principal Contractor Sign Off
d98abd36-c752-4cc2-a43d-d6ad9af3c983 | checkpoint-no-value | Consultant Sign Off
481abe9d-57fa-4a91-a129-960c40e9b501 | signoff | Consultant Sign Off
e75e1e06-0621-4c68-ade1-c9ce8f937961 | checklist | ITPS-201 Interface Commissioning | itp | ITPS-201 Interface Commissioning
1b6b519e-fede-49cf-9de7-1af65ccff442 | section | Details
d28b2e50-4746-4778-92f2-b4aee0564141 | checkpoint | 1. CONDUCT FIRE MATRIX TESTING
8b648699-c46d-56f5-b74b-c026b220e5c0 | note | CIBSE C6.2.4 Fire Matrix
611ab4e7-e9d3-54cd-9106-44a5ee832e10 | note | AS1670.1-2018
3be41a90-b3aa-55bb-946b-94ddea0bf3df | note | The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
e1ab07e6-4200-5ac0-873c-14de63bd3ec9 | button | Has "GMF-COMRPT-009 Systems Interface Matrix" been completed? | Yes, No
824b8680-4bdb-51a1-bb5d-93e51255bbc5 | note | Attach a copy of GMF-COMRPT-009 below:
a2517eb5-a439-4740-b56b-1ddc5c2cd5d6 | checkpoint | 2. CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING
54d32fba-5bf1-54e8-b5d3-b16bcdde0a03 | note | CIBSE C6.6.0 Brigade Interface – FFCP
22dac2ab-bca8-559b-84a3-1c5f1dedf02b | note | AS1670.1-2018 Appendix A
e6f8656d-0f26-51ef-a760-f0d39c44ca13 | note | Check Fan Control Operation as per Matrix.
e94f3a56-bc06-5f2b-86dd-3d758bfce56c | button | Has "GMF-COMRPT-010 Fan Control Matrix Testing" been completed? | Yes, No
a2cc2f6d-e9c2-5070-8580-6a787ec0df50 | button | Has "GMF-COMRPT-011 Fan Control Overrride Controls" been completed? | Yes, No
1fce2452-911d-5695-ab22-dbac2faa17e0 | note | Attach a copy of GMF-COMRPT-010 and GMF-COMRPT-011 below:
bd80b770-d5ed-44b7-a41c-8a68d567eef7 | checkpoint | 3. SPRINKLER INTERFACES FITTED OFF
1955382a-44e8-546e-a396-138dd3f5c031 | note | CIBSE C5.8.0 Modules Input/Output
6bd517e3-4be1-551e-aca9-a3a83bb4f015 | note | CIBSE C5.2.9 Alarm Functions
36a04f0a-830a-57b0-a01f-e66573853d7a | note | AS1670.1-2015
96881d8f-df83-54c4-ac1f-ceb28535c05c | note | Prior to any interface testing, have you checked all systems listed in the system interface schedule are complete and operable?
91374b35-4b48-55f3-9e23-90a7ee642202 | note | Have you checked all systems interfaces to the FDAS?
d4b477c5-f9c7-5dd3-8b64-9388a49b68ad | note | Has "GMF-COMRPT-020 Sprinkler Zone Commissioning" been completed?
7a219af6-7173-5d73-86ef-bdb4c0e7d2a0 | button | Has "GMF-COMRPT-021 Pump and Tank Indication" been completed? | Yes, No
f40f327e-f2ab-5a27-b794-29ab6d7c6ce9 | note | Attach a copy of GMF-COMRPT-020 and GMF-COMRPT-021 below:
98046924-708b-48fb-8bc4-0df59f65c7a3 | checkpoint-no-value | GM Fire Sign Off
e2b1a071-e5d0-47ca-ad75-2256294e30fb | signoff | GM Fire Sign Off
75cb3889-3b13-492c-873f-f5bb3496e251 | checkpoint-no-value | Principal Contractor Sign Off
4216c640-8c6e-4163-aa50-ba3fa336a94d | signoff | Principal Contractor Sign Off
1b2fa36f-4ab6-4b33-9263-0a0da27a9e45 | checkpoint-no-value | Consultant Sign Off
ab76a830-f73e-4a68-8e5a-3e46647256ac | signoff | Consultant Sign Off
0f2ff25f-e1e6-46b2-920f-b4ab2d53e783 | checklist | ITPS-202 ASDS Commissioning |  | ITPS-202 ASDS Commissioning
7b0385b8-0426-45a6-a167-e28fd877bbbf | section | Details
49342fea-a277-40f6-86f4-9e868b52e93e | checkpoint | 1. VISUAL INSPECTION
52ed3247-fd8c-5be2-9cb3-0303d636df0f | note | CIBSE C5.6.0 Sensors/Detectors
3b151d66-61b6-5e7b-ac6a-2757f6afa137 | note | AS1670.1-2018 Appendix A
ac3d67c2-4ec1-5a69-83e7-7a001b694f52 | button | Have you visually inspected every sampling point to ensure it is not obstructed? | Yes, No
44b06533-2dec-51c9-92f7-72a5bb131277 | note | Add Photo
819fb0a0-039a-4a49-ba28-25cf7e1031b8 | checkpoint | 2. ALARM TESTING AND TRANSPORT TIMES
7c4db494-e22d-5754-b445-b1fe5f7ed85d | note | CIBSE C5.6.0 Sensors/Detectors
82243d3c-121d-5c3e-99b1-ffe613755f4a | note | AS1670.1-2018 Appendix A
ec61e35a-d737-599f-a8c5-1c36313a2afa | note | CHECK AND RECORD
92b20542-7bdf-558b-8b16-51e498da88ea | textbox | The response of all capillary sampling points using a test medium placed at each sampling point:
0a2f6a91-ab24-50c3-9ce1-13c2e6a274ff | textbox | Measure and record transport time (TT) from the EACH sampling point:
35075a62-61db-5066-830e-8691de03b4a7 | button | Has "GMF-COMRPT-012-ASD Commissioning" been completed? | Yes, No
2f22ad6f-6883-5daf-9579-0badd0c8c180 | note | Attach a copy of GMF-COMRPT-012 below:
8c6d230a-b0f9-4bba-9f5a-4f55e15c35b6 | checkpoint | 3. OPERATION - ALARM, FAULT AND ISOLATE
d8e54049-4601-58e2-a929-d0a3f71c8627 | note | CIBSE C5.2.9 Alarm Functions
a97deed1-0984-5e8c-8a1a-01dffaae25a4 | note | AS1670.1-2018 Appendix A
00c087dd-d6f9-55b3-979e-5f0cc4d54388 | note | Have you checked:
f5973181-c5ba-50bd-954c-dd48be61cba2 | note | The operation of remote indication of alarm and fault signalst; and
24650c5b-ca34-5140-986a-d0218861649e | note | The operation of airflow failure indicators; and
42e7fa9a-c273-59f4-a4ca-991ea4f22fb5 | note | The operation of the system failure indicators; and
2c0b9784-94ec-55de-a8fa-711e390b7b4d | note | The isolate and reset functions; and
aa328df9-a3f9-501a-8178-2563e01c483f | button | The fault and alarm test facilities (where provided)? | Yes, No
66c4f792-b061-412e-965d-b0cb059a9c33 | checkpoint | 4. ASD MATRIX (If Applicable) - Including Thershold Testing
fb696193-874d-53fd-9f5e-f01a963a1b97 | note | CIBSE C5.2.9 Alarm Functions
11cd5f37-2448-50c4-83f2-4f509bf64125 | note | AS1670.1-2018 Appendix A
6ff33fc9-5f45-5c0b-be34-a28984830f7e | button | Has "GMF-COMRPT-013 Double Knock Testing" been completed? | Yes, No
a7ea4cf6-df32-5fcc-bf8b-3cf639d7537b | note | Attach a copy of GMF-COMRPT-013 below:
1de1dd2d-4c26-401c-b4ac-ccf51452bb21 | checkpoint-no-value | GM Fire Sign Off
9200e9a4-a253-43d0-a70a-de5498dd6586 | signoff | GM Fire Sign Off
0e45c8d1-491c-446b-9d36-859eb573384d | checkpoint-no-value | Principal Contractor Sign Off
1bf088d4-d5b2-477c-9a63-7b085808925a | signoff | Principal Contractor Sign Off
1ac1321c-c925-4522-905e-f2e63257844a | checkpoint-no-value | Consultant Sign Off
1048259b-dcd8-4932-b041-0e0c60b642e7 | signoff | Consultant Sign Off
5eb13912-7700-4622-ac37-90e0d0f7bcbc | checklist | ITPS-203 Pipework Pressure Testing |  | ITPS-203 Pipework Pressure Testing
ac8b9634-2bb7-4a9b-80d7-2c0e5a05a21c | section | Details
93ad5f7f-b978-4aab-8ad2-9a3b32047bb9 | checkpoint | 1. SCHEDULED TEST IS APPROVED - CONFIRM
0f68bacd-e275-582e-a635-63be24be1c1b | note | CIBSE W5.5 Pre - Commissioning
7187bc02-aa79-5298-8327-8d18ae56316e | note | Have you received Approval for test time and location?
ea2fab81-db50-57ce-8f92-8d447794e9e7 | button | Has the site been notified? | Yes, No
fa137254-58b7-5cb9-a6f2-1fc650f6397d | note | Add Photo
5c1321e9-60b3-46f4-98e8-ad68a8b759ac | checkpoint | 2. EXCLUSION ZONE - CHECK
1c501a15-c247-504e-896c-39bf373d4533 | note | CIBSE W5.6 System Checks
b1444967-4b44-550a-99d7-06927f89c653 | note | Has an Exclusion zone been set-up?
f2c18f91-2a5d-5473-85d0-ba23b1efd1c4 | note | Have you erected appropriate barriers and signage?
8e26b6f6-a121-501d-be37-7ffd6b0cfb82 | button | Have all workers/occupants been notified and have they exited the area? | Yes, No
df2c31e2-803b-5d75-85b3-c22a3a47e6e4 | note | Add Photo
89d24679-8559-4180-ba8a-9c2535871d88 | checkpoint | 3. VISUAL INSPECTION - CHECK
3e891c9f-673e-55ca-a45c-1230ae2a3390 | note | CIBSE W5.3 Check before Filling
67a39f51-ced3-594d-a13e-a8be7509469d | textbox | Drawing Reference and Revision number:
4a30ede4-74ec-51f7-ac7a-8af6923ce5c1 | note | Is Installation complete?
83a83350-dc90-55f0-93a7-f48c66979b7d | note | Have End Caps been fitted with lockable ball valves? (BLANK END CAPS MUST NOT BE USED)
828aa2e7-9a1d-54c3-aa31-44e692097b79 | button | Are all outlets sealed? | Yes, No
28844cd5-7bb2-5044-9228-e391953758a2 | note | Add Photo
896bb9d7-47ca-4b83-bfed-025437fae65f | checkpoint | 4. FIT TEST PUMP AND CALIBRATED GAUGE - INSTALL
43dea330-0f8e-53d2-9543-92ccc9aa66c8 | note | CIBSE W5.3 Check before Filling
edca68c3-dd7f-569d-ba3e-a14283b0ab00 | note | AS2118.1-2017
30a7597b-cba5-5a6b-b316-3713d5beaa21 | note | Is the Pump installed in a safe location?
d469de34-4bfe-5517-9350-19bc2f2126dc | note | Is the Callibrated gauge in visible location, and accessible to photograph?
773f26e5-d38d-581c-a1ac-b992ff31f841 | button | Have the Pump and Callibrated gauge been tested? | Yes, No
b448746f-76ed-578c-95d1-d41fc039c1c6 | note | Add Photo
904d99d7-b05c-4c3e-bec5-12d12a1abd27 | checkpoint | 5. CONDUCT BREATH / LUNG TEST
e32a4e09-5a88-510a-8bd1-82ecb8fd6c33 | note | CIBSE W5.3 Check before Filling
4d2947af-5d18-56f5-837f-d0280308ffdc | note | AS2118.1-2017
d82979f5-f43e-5782-953e-93cf03819985 | note | Perform Lung/Breath test where possible;
271edda7-401c-5fcd-a2a5-e29d27987dce | button | Is the system sealed? | Yes, No
93c52820-6f57-51d9-aa5f-1839d2d81df0 | note | Add Photo
340688de-c95a-4c27-b480-6b45d548be83 | checkpoint | 6. FILL SYSTEM - STATIC PRESSURE ONLY (OR AIR PRESSURE)
683f1662-c2d9-5985-b3e9-f268fc06045d | note | CIBSE W5.4 System Filling and Venting
ca80e624-321d-5f4d-9dd1-27946900637d | note | Prime system to towns main pressure OR 300kPa (depending on test);
71b91231-8be6-5965-b92e-9a18f04796f9 | button | Are there any leaks in the test area? | Yes, No
6af862fa-418c-5db1-b328-30be93b916ef | note | Add Photo
9956a627-5c94-4df9-918e-70a640674e03 | checkpoint | 7. START PRESSURE TEST - CHECK
f380db9f-848f-5ef7-bcce-7a41064c0926 | note | CIBSE W5.4.1 Pressure Testing
765d4194-9898-58fb-8b6e-2465713fa2a8 | note | Increased pressure to 600kpa start pressure;
c81590b2-6cc8-50af-8334-6b25f51e4f2f | button | Are there any leaks in the test area? | Yes, No
49f5b437-9ec6-5419-8ab1-6f3db8322a2a | note | Add Photo
1c7b13b1-0fc3-4baa-89ab-3d8a269028f1 | checkpoint | 8. INCREASE PRESSURE
ed52eead-bcde-5de3-945d-6963eda01535 | note | CIBSE W5.4.1 Pressure Testing
04823a6a-faee-546a-a2f9-b2e79e228ef3 | note | Progressively increase pressure in 100kPa incraments; and
0e4d98eb-a5a7-598d-ab8b-74f3ea20019d | note | Inpect test area for leaks at each increase; and
eb9a0f90-6316-51aa-8c07-192e83bdfd20 | note | Repeat until pressure reaches 1600kPa;
ad61eabc-bed2-56b2-a558-3e4e9604cdb7 | button | Were there any leaks in the test area? | Yes, No
470f3cb3-2c83-5e0d-bf19-1144bb4d9e6f | note | Add Photo
9e642aec-2821-4fd2-a52a-c5f60676a7c4 | checkpoint | 9. HOLD PRESSURE
8daf97cf-456c-537d-98cf-3b7728c446ea | note | CIBSE W5.4.1 Pressure Testing
210ab424-b09d-5af5-916b-76d3b49823cd | textbox | Record Start Time and Photograph Guage:
20d8b17f-d789-5bba-8e63-6979929ca402 | note | Hold pressure for 120 minutes.
8d3768cd-9c36-54f1-8b78-946db3a8f957 | button | Was there any pressure loss? | Yes, No
d31d7871-f6ec-5670-97e8-6c768de2a228 | textbox | Record Finish Time and Photograph Guage:
35423f18-087f-508a-a9cf-3370d7ce55a9 | note | Add Photos
153e2c08-aeed-4e75-b101-08b3291acef3 | checkpoint | 10. DE-PRESSURIZE SYSTEM
728475f4-a092-5ff3-b26b-b4f5e312b8f8 | note | W5.4.1 Pressure Testing
0bfe795b-2866-5df0-aee4-53b1bc72e956 | note | Release test pressure from system.
4c9dbac4-b448-5548-bca1-c3e4bb5737f0 | note | System remains primed with towns main pressure.
77980b9c-f504-5657-aa0a-cc3f38440e9c | note | Add Photo
ef8cabe5-04e4-44a0-84dc-0d3f2e818123 | checkpoint-no-value | GM Fire Sign Off
621278fb-429e-432e-9ce7-85237f97ab2d | signoff | GM Fire Sign Off
1e9d431c-15c4-4d1c-92de-bc4ffe9dfe14 | checkpoint-no-value | Principal Contractor Sign Off
3a6f8ff2-ecaf-4c23-9ade-a1f005b33b8e | signoff | Principal Contractor Sign Off
f9f9eeff-ac8a-4546-87bd-92c7124a18a5 | checkpoint-no-value | Consultant Sign Off
5284b9a9-9b10-4442-87a2-8f206c0ed7c6 | signoff | Consultant Sign Off
6cdbf793-9a66-4608-8879-fa8a335d4393 | checklist | ITPS-204 Electric Fire Pumpset Installation and Commissioning |  | ITPS-204 Electric Fire Pumpset Installation and Commissioning
fa54a2bb-ace9-4aae-bb94-f7d4fabfa8b2 | section | Details
938ce357-71a2-4923-985e-abb45eb0488b | checkpoint | 1. CHECK AND CONFIRM - LOCATION
c1a5ee86-3252-5e40-83b0-6d48c361ed7a | note | CIBSE W5.2 State of the System
cac6605f-9ffd-5bb5-bf9a-51e6a98d3d48 | note | AS2941.1-2013 – Section 11
5d5d6d01-e5c4-5ea0-8f2b-9705c2e82ba9 | button | Has the Installation Pump been installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
12e9dc68-48e3-5068-9428-8b755684d798 | note | Add Photo
edde4329-e807-491d-aad5-96561fee443d | checkpoint | 2. CHECK AND CONFIRM - CLEARANCE
5d52c4d2-d740-56bf-b2ac-ac61db8efe75 | note | CIBSE W5.2 State of the System
c6eccb5f-1e6f-5e46-870b-6d72527956ea | note | AS2941.1-2013 – Section 11
4d147fca-6e30-55f7-8467-cccc7cec12ae | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
03c1c00d-a3b7-57c3-b8ad-599273aa3455 | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
899eaf06-f187-5112-96f0-9874124a79fe | note | Add Photo
da39b911-3435-40c8-97df-26d048df04d6 | checkpoint | 3. CHECK AND CONFIRM - ELEVATIONS
0642f9c8-fdd3-5a6e-86af-20a15269b3e9 | note | CIBSE W5.2 State of the System
badaa32c-faf5-5800-8719-38558738adc7 | note | AS2941.1-2013 – Section 11
629413e7-ae7d-5e2a-a6d9-91532c85ff15 | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
4558ba55-9738-535b-860a-6eeb364a2126 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
4b89944e-1b16-5971-b96b-ca9593e96ed7 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
0ddc46c4-e9db-561d-9d15-76314c629a9f | note | Add Photo
3256df10-30d6-411a-9026-8268a50071d1 | checkpoint | 4. CHECK AND CONFIRM - PLINTH
42686af4-440f-5146-b547-ca8d829006a0 | note | CIBSE W5.2 State of the System
b0185eed-abdf-5c61-b8d5-fcb7b1398968 | note | CIBSE W5.6 System Checks
a5fefd75-26f8-5350-8cf0-dc8ef947abf3 | note | AS2941.1-2013 – Section 11
7f788a93-8c17-57eb-a747-17b5f7f7f1c3 | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
61f349e6-72a0-5381-b792-c2e8aaf4f49f | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
6f55530d-ddf5-5d28-8d16-e71da6964abf | note | Add Photo
9e00fd51-eb17-4aeb-8dea-5b86f590b1d9 | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
bb7fbc89-9654-539e-94d7-d185e00ddb73 | note | CIBSE W5.5 Pre - Commissioning
cd58ce82-b2eb-5aa5-9f7e-ccac810f6a06 | note | CIBSE W5.4 System Filling and Venting
739f7847-2293-5e7b-aae5-b01303ec3a7a | note | AS2941.1-2013 – Section 12
a28aa1d4-59ea-5f77-8100-72e1abb6b4d2 | note | Have you checked the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance?
d14a4b98-e884-59eb-a868-62fced2a5c25 | note | Have you confirmed the direction of rotation?
ec8abc51-c03e-5e22-b76c-3d3ca0e440d4 | button | Has the battery electrolyte level, and the battery leads and connections been checked? | Yes, No
5017ea8c-cf49-54a0-97d1-237392edccc3 | note | Add Photo
ac13d5b9-5a55-4803-ba52-23f0e74e68b3 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
899ffff5-8ef6-591f-bfc4-e0d6ccac6b53 | note | CIBSE W5.5 Pre - Commissioning
036c07e3-d65d-5e5f-8224-ddd3107127ae | note | CIBSE W5.4 System Filling and Venting
6ec89e36-f1ca-5063-9a7f-02e10ef99f28 | note | Is the delivery from the pump under test the only supply to the measuring device?
7ce6e543-c725-5d07-ad04-c817a8daaccf | note | Does all flow from the pump passes through the device?
34fa0527-9d79-595d-a1a2-528963ea7a08 | note | Is the pump primed and lines are clear; and
5deb9520-43c2-5bd8-a10c-1645d072ba7e | note | valves are correctly set (open, closed or adjusted to required pressure); and
b9a63136-c661-5808-b3af-0b97a8c8e56e | button | is water available? | Yes, No
ef54afdc-78fa-5a06-b532-f0c086c4cc5f | note | Add Photo
4f05b3f9-236b-46c0-ab81-1468d43a97f6 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
f8e86c7f-cc79-55bc-8c13-6622e3e93c21 | note | CIBSE W5.3 Check before Filling
1d362990-c53a-56ad-bfee-164eca0af046 | note | CIBSE W5.4 System Filling and Venting
290dc729-f246-5546-bd80-37987001d8fb | note | AS2941.1-2013 – Section 12
446208f0-5a79-56c3-8120-aa3a61086c0e | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
2e88a324-7a78-53bf-b49d-03f8c74a19d5 | note | Add Photo
d3a1083e-e751-444c-8832-5d6b7c8a6485 | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
83338fc1-241f-544a-a6bb-c7d49233eec9 | note | CIBSE W5.5 Pre - Commissioning
0dbcbf74-2951-532f-bd46-adcd123ae44f | note | AS2941.1-2013 – Section 12
336810c1-67c2-592d-89b0-38cd82c4063a | textbox | Pump plate details:
dc3ac70b-ab05-5bbe-b316-c02929232112 | note | Add Photo
49934b42-7a5c-4889-a945-ff76f05ddf2d | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
67811bb9-13bd-56ab-9d26-389a52647af1 | note | CIBSE W7.10 Commissioning Certification
95c63f8c-27fc-5f66-8395-67ca4d669063 | note | CIBSE W7.2 Flow Rate Measurement Tolerances
54eb350e-f28d-57d6-9ce5-adc9bd3c7a5c | note | AS2941.1-2013 – Section 12
8d180499-b7d4-5098-8c80-e66810335aa8 | textbox | What is the pressure in the system at which the pump starts automatically?
33f8eb15-02d2-546b-9c8b-5bb81c3c01fc | textbox | Pump shutoff pressure:
36d81544-0f02-527f-95a8-f018d3a2de5d | textbox | Motor shut off pressure:
05c73a58-df1b-5c7d-bfa2-544b95181f31 | textbox | Delivery pressure at maximum flow:
ac08f29f-080b-5a5a-a96c-fad5d064bef8 | note | Add Photo
95e62bfc-6b92-4966-8bc6-16ac2048f106 | checkpoint | 10. COMMISSIONING CHECKLIST - RECORD
12830729-4809-5341-b0db-5c3f2d78e3e4 | note | CIBSE W7.10 Commissioning Certification
19e9793e-f110-5076-bd0c-37e15f51c3da | note | CIBSE W7.5 Preliminary Flow Rate Check
79884ff6-ad1f-5223-87e4-86abf6d8c388 | note | AS2941.1-2013 – Section 12
91663b33-0021-5a50-b7c2-8a907b0e662d | textbox | Record the pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate:
9258c3e6-6db0-57f5-9b8e-7780e6b17b28 | note | Add Photo
d8c99ffb-13f8-4168-bebe-d89268c87282 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
55627e41-ec5b-5262-b786-ff6b7a3aca63 | note | CIBSE W7.10 Commissioning Certification
e0a7401c-2d74-59a9-a4d8-7f0451d9c4fa | note | CIBSE W5.7 Static Completion Records
2972d8ce-3e4a-5489-b6a9-d6b66c690701 | note | AS2941.1-2013 – Section 12
2b8e198a-5f36-5691-8cf1-5aa13a096fb4 | note | DURING OPERATION:
33a9d9ff-08b9-5a2a-9d70-acf99c94f840 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
536f71e8-e727-556c-aab3-def5e53f4a02 | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
62969157-70fc-5478-bfc6-f2042ce159df | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
216ab9da-7d76-5cfc-80e0-7e56cf2b1804 | note | Add Photo
4b72444a-813b-4778-a9a3-636b355d26f5 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND REPORT
9ca55f12-0315-59d3-b00d-1c4bc3bdb5ef | note | CIBSE W7.10 Commissioning Certification
a9a9eed0-db76-5d6a-a423-da9589ccc8c5 | note | AS2941.1-2013 – Section 12
2a7012e6-a05c-59b7-b16a-168373fcf93f | note | RUN AND REPORT:
f50c0b32-cdc8-5f7b-a3d8-f1b35cb55a59 | note | Is the electric pumpset, together with its associated control gear and ancillary equipment, functioning correctly?
0018940d-64d6-52cc-a503-2cfafd07bbc0 | button | Does the pumpset satisfy the intended performance conditions? | Yes, No
2c454577-6981-594f-939f-3b76a447b8d8 | button | Are there any operational abnormalities? If Yes, detail below. | Yes, No
3514ca0f-cb37-579d-be72-ed204d98f783 | note | Add Photo
2f12021c-377a-4730-955c-206aea4a4d27 | checkpoint-no-value | GM Fire Sign Off
d5a50687-80a6-4595-854e-950a01a957c6 | signoff | GM Fire Sign Off
518408f7-2557-41c3-ab05-9de3abb5f71e | checkpoint-no-value | Principal Contractor Sign Off
14891808-52ea-4e0c-b4ec-8551b1ebe1d3 | signoff | Principal Contractor Sign Off
99a9bf6c-0559-49d7-9cf6-ca4a8110365f | checkpoint-no-value | Consultant Sign Off
517866f4-60f2-41e6-9b37-f0cce63128bb | signoff | Consultant Sign Off
b8dd211e-2a7a-4050-9abd-f979578ac23a | checklist | ITPS-205 Diesel Fire Pumpset Installation and Commissioning |  | ITPS-205 Diesel Fire Pumpset Installation and Commissioning
a9a383a5-ecad-4094-9555-ffe8cf5dc23b | section | Details
521b6f34-e3d9-486b-a9e0-2ee9e97976ef | checkpoint | 1. LOCATION
09fb3120-f1fa-5d0d-bb3b-ae6a44d86035 | note | CIBSE W5.2 State of the System
ebf57cea-8540-582a-aaed-b7533cc6b1e9 | note | AS2941.1-2013 – Section 11
b83c5e9f-75cb-5208-8219-62c0f8994a59 | button | Is the Installation Pump installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
e6f63111-1d05-5fb7-90a0-d23fb7dc9c1c | note | Add Photo
15a0992b-fba2-443c-b79c-f465eb5fb2d3 | checkpoint | 2. CLEARANCE
62a957ce-0caf-50bc-a7f2-28a4f76de53a | note | CIBSE W5.2 State of the System
87c246a6-e2b4-5d6d-acda-ca819d9148e4 | note | AS2941.1-2013 – Section 11
eb818b67-2c62-5755-84c8-f3d2881bd6a2 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
19bb6fa7-ff25-52a1-bb1c-d1fa4668688b | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
78661e0d-64a1-52ed-9fc6-bbbc760a0a57 | note | Add Photo
6491f772-a870-4e5f-ae23-b34a859f1fbe | checkpoint | 3. ELEVATIONS
05135e7f-6144-5650-98e8-7cf5409d7065 | note | CIBSE W5.2 State of the System
49940923-2950-57fe-ad0c-aa58748e94d2 | note | AS2941.1-2013 – Section 11
cb431193-338a-5898-a376-e97d1e1fdb9e | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
602c9f82-79b8-5e4c-8622-4224c3a27761 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
ce2fef9a-5937-56b4-b7bc-d49747c3a710 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
bdc41ef9-9217-5f5f-b835-3fe987807489 | note | Add Photo
bc47bc40-e44b-436c-8d26-c4ba483a368b | checkpoint | 4. PLINTH
6a3c4228-0d07-5743-93b2-5833f679c84e | note | CIBSE W5.2 State of the System
3fd88276-57c2-514f-8ec2-04f630fb460b | note | AS2941.1-2013 – Section 11
7c00c025-c47d-597d-bf34-30711fc4bdf1 | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
64fa1d61-90a9-5a4a-bb35-e81dd4b25d5d | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
f60b7cef-36f4-5717-8e0b-34565f39fbcb | note | Add Photo
4aa319f4-c301-4937-b497-fe3857cc8784 | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
ea7f7d16-afaa-50a6-ab62-d9abd2663223 | note | CIBSE W5.5 Pre - Commissioning
92b78f3b-b4a2-51ef-90e1-f1923962241c | note | CIBSE W5.6 System Checks
22bcedb9-0dc4-5253-921b-0b31ebaa8b25 | note | AS2941.1-2013 – Section 12
13e252ca-d819-5806-8589-ad700d9ac103 | note | Have you checked;
6c14f12e-1ce1-5e20-b227-b79eaf93cc34 | note | The cooling supply system; and
7b7876ec-5f31-524f-bb44-ed7a6378bf7a | note | Engine fuel supply; and
1221ef53-abf9-5e0b-ad17-81639b70dd8f | note | The coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance; and
c1635620-67bd-5275-a941-7318774abd8c | note | The direction of rotation; and
6bdf9eb5-f8b7-5514-83ed-59b75e0abc41 | note | That the engine lubricating oil is at the correct level; and
0a2ecd9a-faed-54db-ba21-cb7fc9b94636 | note | The battery electrolyte level and the battery leads and connections; and
d9911a34-6b85-5a39-8775-4257aabce4d5 | button | That the exhaust system is intact? | Yes, No
04904b13-b3f1-5fbb-98b3-700d28101488 | note | Add Photo
3b9c9338-671f-4356-aee7-9d57911e2482 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
2362acd4-aa4f-5b94-a0a0-dd4c28b7efe0 | note | CIBSE W5.5 Pre - Commissioning
74454116-8f35-5152-b72c-1613dd911f08 | note | CIBSE W5.4 System Filling and Venting
789937e6-bf15-5a61-9525-8d387834df08 | note | AS2941.1-2013 – Section 12
ab4cbaa9-987a-59a2-a1bb-19e6cbbf99e2 | note | Is the pump primed and lines are clear; and
dd8e468d-11cc-58fc-bcb2-6c2a4d7187f4 | note | valves are correctly set (open, closed or adjusted to required pressure); and
06063c2e-d367-58e7-ac14-9485065fefeb | button | is water available? | Yes, No
0e8c46af-af98-54ed-87d0-5b7f60ff55d5 | note | Add Photo
effca2f5-b9ad-425f-a762-54cc5d5514f6 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
f9fc041f-88b2-577d-9767-1ae7543ab324 | note | CIBSE W5.3 Check before Filling
29b3f024-d220-5ff4-b330-4df91342d249 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
57ad3b5e-f79b-5841-be72-81c7c8fa4140 | note | AS2941.1-2013 – Section 12
16a4e77d-2052-5aa7-bb8b-5561efef550b | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
5790504b-6c5f-54ac-a108-6b7007f9396e | note | Add Photo
38ade6c6-eedb-4c63-8992-149b4a0bb1fe | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
4a1f9c8f-38cc-538a-a3fb-9f91822df947 | note | CIBSE W5.5 Pre - Commissioning
38f00d74-cb1d-5152-a17e-e9c837276a24 | note | AS2941.1-2013 – Section 12
da2df4d8-6b1f-532b-86ab-94aa82eb8d0e | textbox | Pump plate details:
d62086d3-062e-529e-902e-1c64ce6846bc | note | Add Photo
bcf67cac-a48f-4ec5-b14d-d060fb563352 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
b6528cfb-9a73-5c8c-ae5d-d3377feb6eaf | note | CIBSE W7.10 Commissioning Certification
81c87016-6679-5090-b1c4-df8b616bef89 | note | CIBSE W7.2 W5.7 Static Completion Records
b2410441-284d-556b-897f-6738158577ca | note | AS2941.1-2013 – Section 12
a25b4509-63a5-5ae5-9192-42c226e565d5 | textbox | What is the pressure in the system at which the pump starts automatically?
5c41296b-4736-5979-8218-f01b524fe0b2 | textbox | Engine oil pressure:
faf1bbe3-aa04-575b-9f97-ef2d747cc4d2 | textbox | Pump shutoff pressure:
5f84de41-f58f-54e4-a049-d76de45d2b2c | note | Is the Coolant flow correct; and
a9335233-c174-563f-b86c-0c30d20b9930 | button | Are the fan belts rotating and intact? | Yes, No
8f94f0eb-917e-5385-83af-d4bb5074bbe5 | note | Add Photo
c4da90c5-2386-4057-9251-7368bc510233 | checkpoint | 10. COMMISSIONING CHECKLIST - ISOLATE
be261dcb-8639-53e3-922d-f5ff06a13424 | note | CIBSE W7.10 Commissioning Certification
98e1fec1-7faf-5058-bdfb-601db70e1bd0 | note | AS2941.1-2013 – Section 12
400e5d2f-259d-54c8-b338-ed28d751fef2 | note | ISOLATE the flow meter, partially open the test valve, and flush to remove any debris or foreign matter;
71928dea-3b49-5ece-9014-d28fd085959d | textbox | open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter:
6605463e-e094-5995-b5bc-d7ffc9a246b9 | note | Add Photo
0e16aabf-698d-4e42-81ae-9b9b75502bd0 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
18aeded5-9c51-5954-8dca-61d787cca7e0 | note | CIBSE W7.10 Commissioning Certification
f2b7c09f-84f5-5eea-aab1-fa929ee53279 | note | CIBSE W5.7 Static Completion Records
082a0262-c414-5aa8-b246-f231bf1324b8 | note | AS2941.1-2013 – Section 12
bcc0d088-4b74-5209-b53e-e3bdf6d4f142 | note | RUN the pump for 30 min at maximum flow and record.
5757c3bd-0ad7-55f2-b31f-61c1b0f8a9e1 | textbox | Suction and delivery pressures:
db64d411-9912-5466-ae0b-7cb5412ab9be | textbox | Engine running temperature:
7fefdf41-5b78-5186-b749-d79ec462c15b | textbox | Engine oil pressure (within the engine manufacturer’s limits):
ab19173f-3475-558a-9e0f-ee0cd24ddc56 | textbox | Air temperature at pumpset:
b4b2dff3-24c9-5b9b-9f9b-de3517fc42cd | note | Hold the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles.
2ec9b9ab-6340-5639-9905-5c759c718103 | button | On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position. Does the engine start immediately? (Clause 9.3.6.2) | Yes, No
3b0bcfee-a758-501b-81e2-f70ab89a8396 | note | Add Photo
4232860e-5c63-4443-9089-de31d91b28ab | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND RECORD
cb00a427-ab04-5ed2-b988-2481ff354dc1 | note | CIBSE W7.5 Preliminary Flow Rate Check
84c1fadf-85d9-5805-9989-9d579d22d674 | note | CIBSE W7.2 Flow Rate Measurement Tolerances
dcbbf070-fca7-583c-bbae-3ced97dc7112 | note | AS2941.1-2013 – Section 12
ce31c1b6-8b1f-5519-9244-d648c9ffbe15 | note | RUN the pump for 30 min at maximum flow; then
3ab0048f-2b5b-58ab-882d-c92abaae0cf0 | textbox | Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate:
b892f087-de36-5f59-a588-6310bd389e1c | note | Add Photo
4e1c58b5-e8e8-46e2-a73b-349611a20015 | checkpoint | 13. COMMISSIONING CHECKLIST - RUN AND RECORD
1a4fe90a-d17e-5c75-8fbe-661b6a462c39 | note | CIBSE W7.10 Commissioning Certification
aadf2a39-f7c2-5094-b770-f2e6be76f9bb | note | CIBSE W5.7 Static Completion Records
f2c1b89b-fe4b-5244-9330-455b4560cb49 | note | AS2941.1-2013 – Section 12
1e766622-6c36-5dce-8b79-86f67f093186 | note | DURING OPERATION:
20999bd3-4a19-5427-803b-71de9ee45053 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
c4144976-a09d-553b-845f-afde548811db | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
08d927b4-e4a5-562e-8c0c-7949c710e9c1 | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
11bdbc2e-6ac5-5690-bea0-d405f5f92440 | note | Add Photo
41ce4ef4-4873-4632-8e89-05386d67544b | checkpoint-no-value | GM Fire Sign Off
48057cb9-55c1-4316-8fbd-2c6973c70a37 | signoff | GM Fire Sign Off
d79e7b6d-45c7-44b5-8914-2b9f40b49cdd | checkpoint-no-value | Principal Contractor Sign Off
4d5a8572-9d1c-4e29-827c-f79a4c320235 | signoff | Principal Contractor Sign Off
a6065656-5e92-4bb4-b258-10dfb38340a4 | checkpoint-no-value | Consultant Sign Off
73c933f3-7d6b-4b14-9445-b36924ced033 | signoff | Consultant Sign Off
ba48df17-09cb-4755-b312-c4d548f19fc9 | checklist | ITPS-206 Sprinkler Commissioning |  | ITPS-206 Sprinkler Commissioning
7a36d191-75ee-4a51-9397-11b59b44f9c7 | section | Details
f1ac6a00-22ff-42e8-97f6-85e4632f2345 | checkpoint | 1. CONFIRM WATER SUPPLY & PUMPS PREVIOUSLY COMMISSIONED
8c958e0f-3685-5426-a670-52f084dece5b | note | CIBSE W5.2 State of the System
65307e11-d797-51db-a520-68c060ce4a73 | note | AS2118.1-2017 - Section 14.9
5530fe3e-862f-5447-bdf2-7cef4d583373 | note | Water Supply & Booster Pumps have been commissioned
5d1dffb2-08e4-51b6-bcd6-198d12030a8d | button | Are all Valves in the correct position? | Yes, No
780b2926-4f41-42cc-ac2b-56e7d2d94825 | checkpoint | HOLD POINT
90b8d787-f930-5a81-b7c0-d412cf6929d0 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
81d74ead-c98b-4eb0-8b33-d411098c82e3 | signoff | GM Fire Sign Off
a3689f6f-424a-4351-bfac-ec91277a77ee | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
f4a91461-966d-5c5b-8d99-9f091cda4158 | note | CIBSE W7.5 Preliminary Flow Rate Check
99105eca-a399-5cb1-86b8-56d171c6546d | note | AS2118.1-2017 - section 4.2.2.
17e8ce5e-94e8-5560-bfe1-6df8454cee1d | note | Test
2317b1d0-bb15-5a6d-a402-314ebdfad4f9 | note | 1) Confirm flow & pressure requirement
30af0af0-4a54-58d7-9536-a550481d42bf | note | 2) Secure flow meter to annubar test line
4dea89eb-0749-5ea5-838b-9e7e0745139e | note | 3) Manually start booster pump 1
506d6005-27ec-5fc2-8825-7a9dc993ec52 | note | 4) Incrementally open annubar test valve
794456bf-5911-5345-920e-5a5f33c5ad12 | textbox | 5) Record test flow & pressure at each stage:
c5b4bc8c-8ceb-55b6-8739-78a7157f5b72 | textbox | 6) Record pump data at each stage:
79f5319c-fd59-5f09-bf68-814970ac5a42 | note | 7) Confirm system achieves pass result
d910b407-7546-5859-a628-8d5a37fe2a6f | note | 8) Close annubar test valve
108bbbde-da83-56e6-a743-7d6c88368e55 | note | 9) Stop pump
270ccab9-9d46-5969-a115-ed335dc3daf0 | note
be2c8169-c680-5b88-be3e-eca919e06364 | note | Has the Sprinkler Block Plan been completed?
6c1a67eb-493e-5e8e-87a1-77fc4ba2c187 | button | Have you recorded this on the Pressure Gauge Schedule? | Yes, No
fc463fcc-63e5-5292-9918-62dde44d69a7 | note | Add Photos
41b28026-feae-4af0-a3a5-1e6d49566d06 | checkpoint | 3. CHECK OPERATION OF DBA PRESSURE SWITCHES
e97128c5-cc25-55df-9495-a777bca359d2 | note | CIBSE W5.6 System Checks
622d05ff-3773-5fc9-a5a0-6625cc8c41c6 | note | AS2118.1-2017 - Appendix H4
7efa2419-a384-5920-8b22-c4cf05c5b529 | button | Does the pressure switch change state when system is activated (Rise in pressure switch)? | Yes, No
cfd648e2-c1b9-5a6a-bc9e-ff0261a37a64 | note | Add Photo
a965fba0-144f-441c-af4c-5bf983886955 | checkpoint | 4. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
d3dfc851-22aa-5c97-8817-56543d38e5f5 | note | CIBSE W5.6 System Checks
95fcfad9-4697-5309-b5c4-03da14b1dc76 | note | AS2118.1-2017 - Appendix H5.4
62281e55-b964-5d0d-a01e-287c48fdb338 | note | Are the pump start pressure switch settings in accordance with pressure gauge schedule?
6cccd6b1-7c88-59b9-875c-a751eee04d9f | button | Have you checked the operation of All pressure switches individually? | Yes, No
b87dbb03-194e-5fee-9413-4e3b9ca270bc | note | Add Photo of Pressure Gauge Schedule
50b29b40-b0c2-4c4b-a93c-60f35f111f11 | checkpoint | 5. CHECK OPERATION OF DRY FIRE INTERFACES
73f5e577-7251-5416-a06f-261cc117213f | note | CIBSE W5.6 System Checks
ad4313bf-7a66-536b-a276-db4f46fd32f2 | note | AS2118.1-2017 - Appendix H6
6f2de47d-87c9-5cae-82d0-0d8f9999dda3 | note | Activation of ancillary Pressure Switch (Rise in pressure switch) registers at FIP
45e5adb5-004f-57b6-82d3-102667447de4 | note | Activation of flow switches register at FIP | Yes, No
cddaf41c-ed47-5a73-bb3d-7e1c5ebd99a3 | note | Change in valve state/position register at FIP
de8a9951-d6c3-5a33-acec-9b44f2336e3e | note | Attach the valve list
c53ddb51-38bb-4c57-ae97-e3d60ec1cd97 | checkpoint | 6. COMPLETE FORM 71 & ALL TEST RECORDS
a9d15e0b-1373-5fd2-abd4-9b5047904526 | note | W7.10 Commissioning Certification
e1b6a950-3dc2-5663-8412-28d35603072e | note | NCC 2019, AS2118
bb9fc478-c44f-56f8-a52e-156e11546a45 | note | Flow test pass result on Form 71*
6c8393cc-e8e2-5ad1-86e8-84bcda54d42a | note | Record the pump start pressure switch set points:
b763b4f3-af38-5eda-bf49-bce8c1b3db97 | button | Record the dry fire interface test results: | Yes, No
063e43f5-26d1-543a-bd9a-dc2e0305e49b | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
68bd7cc8-1745-539c-9c7c-6dd0572482fb | note | Add Photo
7e1a7416-8568-42d6-97a3-f534a7e65f6f | checkpoint-no-value | GM Fire Sign Off
895b52f6-cd85-4d54-bc7d-c39029067f92 | signoff | GM Fire Sign Off
404095f6-a115-4043-bdcb-09baf1586005 | checkpoint-no-value | Principal Contractor Sign Off
9d7114be-0d20-42b3-b54c-51ac1260a7f2 | signoff | Principal Contractor Sign Off
dcbd06aa-7c0b-456f-82aa-c763fe6fc9ea | checkpoint-no-value | Consultant Sign Off
922e7652-b4db-4168-89a5-ea7c3fb56d85 | signoff | Consultant Sign Off
485dc581-71f9-4a63-9adc-cb08ec9f0382 | checklist | ITPS-207 Hydrant Commissioning |  | ITPS-207 Hydrant Commissioning
9094b089-026c-46f1-93e2-ce226cf7a973 | section | Details
6ac56350-969b-469e-a253-49c040222b73 | checkpoint | 1. CONFIRM WATER SUPPLY AND PUMPS PREVIOUSLY COMMISSIONED
1cfd29bd-34c6-5dd8-9220-547c299f4db3 | note | CIBSE W5.2 State of the System
9aaf8391-8f5b-53f3-982e-f5a7b44c8ef0 | note | AS2419.1-2005 - Section 4 - To comply with Part 4.2
75a6f51c-2c2f-57fa-bfbb-53e866d9875d | note | Have the Water Supply and Booster Pumps been commissioned?
4257dd25-f232-5445-8d69-edeac5deb5a8 | button | Are ALL Valves in the correct position? | Yes, No
3cdd12cd-22f2-45e1-8ffc-a20b77d16f37 | checkpoint | HOLD POINT
ef5d0bfb-7a76-5268-b110-000405ca26c7 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
f201c07e-6dbd-48e2-a87f-b4d145eb7b38 | signoff | GM Fire Sign Off
a36e9b93-7fd4-4601-ac4c-2aec08440c94 | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
dc96c5d1-1aca-5482-9213-9fd14b8a7766 | note | CIBSE W5.2 W7.5 Preliminary Flow Rate Check
ae587419-99a6-5b2d-ab4a-ddd46558abba | note | AS2419.1-2005 - Section 2
b740efe4-f5b3-58df-bab3-abd369ac2c94 | note | 1) Confirm flow and pressure requirement
7f07ef71-ebdb-5b36-a348-d9eb0324d168 | note | 2) Secure micrometre and calibrated gauge to hydrant outlet
fdba4800-98df-5c42-8716-7b803ca56788 | note | 3) Manually start booster pump 1
5985a334-a03c-5a23-a120-45b7e286a216 | note | 4) Open hydrant valve to required flow rate
9eb3fd9f-28a4-5f3e-9724-a19985170c5a | textbox | 5) Record residual pressure at required flow rate:
11b90e8a-3f2c-5c74-896f-9290056a51f1 | textbox | 6) Record pump data:
12b5296e-dbff-586d-90b7-428aad5d5bc1 | note | 7) Confirm system achieves pass result
2045c2de-9b53-5323-80f5-c7cd588daafa | note | 8) Close hydrant
4e743c35-3144-568a-9d63-e6a9838533d9 | note | 9) Stop pump
2955f843-ded4-5d78-9d6a-759b0efcbba9 | note | Attach Hydrant Block Plan and Pressure Guage Schedule
1f11a85c-6fb0-4f9c-8054-cd09293d0cc4 | checkpoint | 3. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
e8ff651f-d276-5dde-be4f-e8557dcf2dde | note | CIBSE W5.6 System Checks
930cf289-f932-52f1-846f-c1635636a389 | note | AS2118.1-2017 – Appendix H5.4
28fcc483-a3f6-5302-b241-4300971ecb8f | note | Is the pump start pressure switch settings in accordance with pressure gauge schedule?
4c976b73-198a-5e6a-ab77-d0e215b4bbc5 | button | Have you checked the operation of all switches individually? | Yes, No
35cb8447-3a17-570c-9f58-9af161643b8f | note | Attach Pressure Guage Schedule
7f855dfc-c0f0-424b-898e-088f265e0b88 | checkpoint | 4. CHECK OPERATION OF DRY FIRE INTERFACES
859dcbbf-5f68-5e2e-88a2-83e3dee01b85 | note | CIBSE W5.6 System Checks
a4c75d4e-ee0d-5a75-8b7f-e7a994362bdd | note | AS2118.1-2017 Appendix H6
1145fcad-3626-57dc-9481-5d739050bcca | button | Change in valve state/position register at FIP | Yes, No
83680ba9-6c3e-500e-bca5-a254c7f66956 | note | Attach Valve List
8bf9fb52-aa15-4d78-9b55-726828e3c1c0 | checkpoint | 5. COMPLETE FORM 71 & ALL TEST RECORDS
1b67b9e0-b4a3-56c7-986d-9110ab562dc7 | note | W7.10 Commissioning Certification
b4609a97-e369-5029-80ff-7d5991b61402 | note | NCC 2019, AS2118
7cc26841-b2bc-5157-a43b-0dd5a792a214 | note | Flow test pass result on Form 71*
293233a9-86c3-5a05-a1f7-56aa2103e779 | note | Record the pump start pressure switch set points:
34532fdc-188b-530e-8e7b-b7e3bb1e5d98 | button | Record the dry fire interface test results: | Yes, No
dc3e024c-7f4b-502c-aac4-0b601e352ac6 | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
a53a3eee-7cb2-56c6-8be7-24bf3ae21ea6 | note | Add Photo
47df2b1f-18a3-4498-89cc-ef9de274c0f0 | checkpoint-no-value | GM Fire Sign Off
239d215a-72a3-4c52-b1a7-271c4dfa0c33 | signoff | GM Fire Sign Off
215ff1cc-536c-4d46-8454-949e85a78a7f | checkpoint-no-value | Principal Contractor Sign Off
8da68ccb-3c5a-403f-9e34-ae82cc59c848 | signoff | Principal Contractor Sign Off
fe524a92-a4f4-449d-b888-9aa991083739 | checkpoint-no-value | Consultant Sign Off
8140caba-eac3-40d6-b1e8-0d359afd9c7a | signoff | Consultant Sign Off
87dbf723-3c96-462d-bf66-e455fedf5f06 | checklist | ITPS-209 Deluge Commissioning |  | ITPS-209 Deluge Commissioning
8eea13d2-6902-4b58-986a-3c9ed55875f7 | section | Details
7817e386-1f03-4300-b563-044adf24669d | checkpoint | 1. AREAS PROTECTED
0f26962a-7b53-515d-b6b3-22f5c1ae0bbc | note | CIBSE W5.2 State of the System
f6c8df84-0587-588f-a3c6-5fb3d4f3a162 | note | AS2118.3
579b67c5-1d15-5b2f-bfaa-4893198ed8bd | button | Have you ensured areas protected do not exceed 300m/sq per valveset? | Yes, No
69a0a452-eee7-5400-b4c3-1d18d8f626f5 | note | Add Photo
e13b2f41-965d-47fe-b293-b669ac827608 | checkpoint | 2. PRESSURE TEST
b77b8a3d-9734-5cad-b586-4c6c8f11065c | note | CIBSE W5.4.1 Pressure Testing
b5dd3634-0e61-5e2b-a53d-78f9fd902b38 | note | AS2118.1
088ba1e8-65f5-5bab-b519-e8d61450a0f6 | button | Have you completed a pressure test as per ITPS-203 for each deluge system? Note: Where open sprinklers are used ensure all heads are plugged prior to pressure testing. | Yes, No
b4e01887-62fb-5ccb-9378-5e7c57b095e0 | note | Add Photo
1ae11dd8-82e8-4a6a-9c03-a5c7b3ce35dc | checkpoint | 3. EQUIPMENT TESTS - SYSTEM FLUSH
728f2aca-b05d-5e3e-89ac-d818871303ea | note | CIBSE W5.5.2 Flushing Procedure
0851b159-f1c6-5973-977a-cb3586eb9363 | note | AS2118.1
543b63ae-49e1-55ad-b2ff-593c4e0fb7af | note | Complete the following PER valveset and open sprinkler head:
ec26301e-47b5-50d4-972e-b4d24505bd78 | note | 1) Flushing of each open sprinkler head to ensure debris is removed.
9c12745e-e70d-59ce-abb7-ac762de00e99 | note | 2) Setup filtration mesh and water bin at each open head off each system (is there are a large number of heads then separate system by plugging each head).
1903c679-9e94-5e4a-8788-0686e90ca55f | note | 3) Let water flow through pipework onto filtration mesh
29b7d2ca-0540-5357-b85d-d2214726c8f2 | note | 4) Once water is clear from debris shut off water and return system to normal.
79de03cd-4a66-53e9-a70f-2b83859bb91b | note | Take photo per deluge head and record deluge head/s location:
c62db6fb-5360-49e9-b201-c73c7170ea52 | checkpoint | 4. TRANSIT TIME TESTING
c61592c5-2057-5eaf-873e-fdc3c8791cd9 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
655f698f-f7f9-5633-8f34-22bd130f6610 | note | AS2118.3 Cl 2.9.1
dca9d2ad-e275-576e-b1fe-5f22044bf59a | note | Complete transit time testing
24da5ecf-6c2c-59bf-886c-e935fd082ba3 | note | Test of the deluge valve to ensure the transit time does not exceed 30s from the valveset to the remote deluge head.
ca7a5928-1b84-55d6-9e89-7a1559ca7660 | note | Add photo of results of transit time.
3a04b841-ac9a-4574-b21d-5e715db680a8 | checkpoint | 5. RETURN TO NORMAL OPERATION
0a93862e-2b51-5279-931c-3b3f60087f9c | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
83d068c2-f166-5a5a-950f-7dba0ba9b53f | note | Are all open sprinkler heads re-installed where previously plugged?
eb006e7b-ed6a-56f8-8e5a-e7b3b4e19414 | note | Have system valvesets been returned to normal condition (or approved condition where construction still occurring)?
b0c22b87-45d6-5de6-a6c7-d46ea7ff4bc3 | button | Have water filled bins been emptied as per principle contractors requirements? | Yes, No
e3e5c507-051b-5c83-9f98-b95a7e82ef8d | note | Add Photo
f4e4ad9b-dd6e-4b4c-9955-2e35567b6483 | checkpoint-no-value | GM Fire Sign Off
8b042243-f6a4-4082-8826-804c333eb1ce | signoff | GM Fire Sign Off
44ef14c4-0907-4701-b770-28081a0f23f3 | checkpoint-no-value | Principal Contractor Sign Off
85d7a163-ece4-4347-b7b8-2cd6e059e22b | signoff | Principal Contractor Sign Off
287159ad-2b09-44b6-9445-76962cf3474e | checkpoint-no-value | Consultant Sign Off
0531c335-d3e4-4752-a6dc-20e7e02a75ed | signoff | Consultant Sign Off
5e9d9c1f-bf36-4d91-a093-17be7eb069ae | checklist | ITPS-400 Temporary Fire Strategy |  | ITPS-400 Temporary Fire Strategy
4c2da7c2-7922-4194-99d1-6bf09e6f941d | section | Details
58cb70d7-d8f0-4242-aa40-44c3f57ace13 | checkpoint | 1. INSTALL AND CHECK PORTABLE FIRE EXITINGUISHERS INSTALLED AT FIRE EXITS
c1b756fb-d294-4e20-81c2-a4b9420d17cb | checkpoint | 2. INSTALL AND CHECK HYDRANT BOOSTER INSTALLED, BLOCK PLANS, LABELS
c92ed5b5-e25b-439a-9dda-196cd5e20dcd | checkpoint | 3. CHECK EXTERNAL ATTACK HYDRANT IS WITHIN 20M OF BOOSTER
5d418db6-1d37-43e6-a87e-e94d397b1b66 | checkpoint | 4. INSTALL AND CHECK SYSTEM IS PRIMED WITH WATER (TOWNS MAINS)
a05bd693-4636-4d25-9cbc-ab8d24cd9d5f | checkpoint | 5. INSTALL AND CHECK HYDRANTS INSTALLED PRIOR TO JUMP
d43fd54d-bdeb-4b72-8a44-17fc3f7aeed2 | checkpoint | 6. CONDUCT WATER PRESSURE TEST OF HYDRANTS
4dcf8017-de22-4a72-96b2-0bdb9a0b5b85 | checkpoint | 7. HOLD POINT DETAILS
412b3e48-4653-5f2e-ba46-f3cf3b78c198 | button | Hold Point Required: | Yes, No
bdb36023-1202-48ca-ae18-caca2f3b2977 | checkpoint-no-value | GM Fire Sign Off
0ac42a97-9b40-47ff-8e66-deebeba3af7d | signoff | GM Fire Sign Off
853f83f2-4ebd-4486-b35a-cd4fbf688154 | checkpoint-no-value | Principal Contractor Sign Off
3193779e-6fa7-429a-8567-f4aac6a7e45e | signoff | Principal Contractor Sign Off
5ae4f12a-942d-4704-9c3d-6e5d3866443d | checkpoint-no-value | Consultant Sign Off
53378368-2b8b-483e-b884-cb11d33a0100 | signoff | Consultant Sign Off
77e7ea8a-86b5-4db4-a8f4-96b77540061e | checklist | ITPS-401 Site Temp Asset Lists Extinguishers |  | ITPS-401 Site Temp Asset Lists Extinguishers
5be128e0-a8b1-411a-a35d-d57fa1bd9b7b | section | Details
5e04fa86-4c2c-4825-bd7f-280cb712d4c4 | checkpoint | 1. ASSETS 1 TO 10
9e37df3e-d351-5fad-9ec6-a98b2f5be662 | note | Add Photos and Numbers Below:
6b64456e-f6d7-409b-b1cf-9ed53fba1e19 | checkpoint | 2. ASSETS 11 TO 20
b1b79cbf-be76-51e7-a586-5d7b95e5f503 | note | Add Photos and Numbers Below:
fd4aae07-ac57-4558-9f3d-c48703b9b1e1 | checkpoint | 3. ASSETS 21 TO 30
d239232d-9d24-5f1f-a9f7-5fadd7c46cf6 | note | Add Photos and Numbers Below:
c30082e6-4d5f-4960-beef-ee1548f7c7b6 | checkpoint | 4. ASSETS 31 TO 40
58035038-7f23-568f-ae63-a8f42985b47a | note | Add Photos and Numbers Below:
a968fc18-4023-47b6-a70d-4c06f5b0a08a | checkpoint | 5. ASSETS 41 TO 50
ce1cbbb9-cae5-507b-aac5-768cd37b4580 | note | Add Photos and Numbers Below:
edf5f2be-6f31-4b4e-8725-c8da2524bc02 | checkpoint | 6. ASSETS 51 TO 60
151f6e20-e37f-5ea9-b4dd-61a4793fc856 | note | Add Photos and Numbers Below:
bb0b7bf5-5e04-4bd8-9603-bc8ccbf7a3ee | checkpoint-no-value | GM Fire Sign Off
36550151-92cf-4fab-9e32-33017e2c3287 | signoff | GM Fire Sign Off
3f1e3117-2449-47d9-ac65-e306a4e7f37c | checkpoint-no-value | Principal Contractor Sign Off
a1690d51-460c-441e-9acc-794fbe95b3a7 | signoff | Principal Contractor Sign Off
f9f3a853-7a02-4d31-b58b-b48158dd3acd | checkpoint-no-value | Consultant Sign Off
f2e2334d-c5bc-4fcc-90c6-7a1c111db749 | signoff | Consultant Sign Off
1e70382a-cd84-5ae1-8862-c1c058edde43 | checklist | Lendlease Contractor Schedule H Checklist |  | Lendlease Contractor Schedule H Checklist
7a748d55-533f-527b-b0f9-60e8fa293f5f | section | Incident Reporting
a6cd5443-3e7d-4bef-9a2c-82b1a72e25a9 | checkpoint | Incident Reporting
b5b35a37-7382-54ba-8bfb-811dbf4572bf | button | Any incidents were immediately verbally communicated to Lendlease | Yes,No
6801e20c-e2f1-5a7f-a0d5-fe47c4fd717b | button | A copy of Incident Notification Form was submitted within 4 hours | Yes,No
66e9a4c6-0421-5ef0-8732-cd78bca8e3a8 | note | Detail any incidents from the past month below and attach relevant forms below.
826609b4-fc54-5a39-ad75-e1293f234680 | section | Workers compensation first, progress and final medical certificates and Return to Work Plans
0c9492a0-811a-544b-b5bc-2fc846063034 | checkpoint | Injuries and Illnesses
e20f96b2-5ee3-56b2-b5c5-912388171f1b | note | The following have been provided;
5492c177-794d-5136-81c9-8f8430e1d1c8 | button | First Medical | Yes,No
823e0dc6-15b2-594f-962a-261c0a26bf92 | button | Progress Medical | Yes,No
09fd6dbb-22b0-55d9-bec1-c657d23b526c | button | Final Medical Certificate | Yes,No
d36edd68-abcb-576d-b8fc-6978886ed6b8 | button | Return to Work Plans | Yes,No
a20041b8-0ee5-5f04-a4e5-2f9b0b26598b | button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes,No
b9e71c13-fb0c-5796-9a4d-1f3ce13a3ae0 | section | Reporting
e2cefbe1-7b4c-58cb-9296-52013acd2aff | checkpoint | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator.
4094ba7a-5738-5658-93bd-78c5dff3acda | checkpoint | Daily Pre-Starts have been delivered to the office by 9am each morning.
4fb06383-4684-5418-9d3a-cc9f4daa39dd | checkpoint | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance.
67b6449c-0fcb-586a-8ebf-2addf988ee69 | checkpoint | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted.
2c6854ff-7dce-52fd-90e9-e611023a913b | checkpoint | Labour Statistics and Man Hours
c45fef96-b2bf-597b-b3ce-585cf62a4bdb | note | Contractor Labour Statistics:
3961a981-e885-5a9c-877f-050b8d38419c | button | Has been completed weekly? | Yes,No
2fcfc2ff-fc1b-5978-9631-1633f919466f | button | Has been submitted before the 26th day of each month? | Yes,No
506b1288-bedf-5659-a27b-52efdb96cd11 | button | Is attached below? | Yes,No
c5929b96-f03b-5652-94b3-156328f9754d | checkpoint | SWMS
1bfaab1b-8e49-53ee-9e9e-873030346dbc | button | Copies of updated SWMS have been submitted to Lendlease | Yes,No
e4104c40-5765-5a71-b723-f81d0bcfb590 | button | Contractor SWMS review register has been submitted to Lendlease | Yes,No
1adcbe56-3cdc-5f92-af30-4e947fc6e60f | button | Updated copies of signed SWMS have been submitted after onboarding each worker | Yes,No
d064d5c0-d0e0-5fe2-a4de-7727e0a3ff4a | checkpoint | Workers are trained and competent
973bcb55-6152-5f6d-a2b0-4d5902cff6f6 | button | Copy of current training register has been submitted | Yes,No
58d3b39a-17b8-56a7-9770-52ce522e2ef8 | button | Copies of licences, qualifications, training records for any courses attended during the month | Yes,No
3495576f-5639-59ab-a767-a607784a3cf2 | button | VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes,No
aef74d7b-d587-5e34-9266-884de37191d4 | checkpoint | I have submitted copies of daily pre-start inspection records for the month
d77f5e32-8a3c-5a96-97b8-96e1ee4e803b | checkpoint | I have attached a copy of the up-to-date Plant & Equipment Register
863d56e4-a279-57b2-a68e-d4b15f9c5577 | checkpoint | Copy of current and up to date Electrical Register has been submitted ( 3 monthly unless new tools added)
1c11da09-d5b8-50be-807f-7a10f77c3645 | checkpoint | I have attached a copy of the Fall Prevention Register
f73063a9-6e9f-572b-981e-bc4461355341 | checkpoint | Lifting gear to be inspected, tested and tagged
e9a421ee-a73c-5e73-8691-a5ecb3c66c99 | button | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register | Yes,No
92bd2845-9677-5a10-9f62-2f292143cd1c | button | I have submitted annual inspection certificates to Lendlease | Yes,No
d8e7b937-09da-531f-a96c-18f76041589f | button | Monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes,No
ae92f7c6-9451-56f7-ae90-9960f5122f4b | checkpoint | I have attached copy of Hazardous Substances Register highlighting any chemicals brought on site this reporting period.
a02a0ab0-ff4d-53ee-8a92-1c3a98928fa7 | note | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
ba1f906f-1a0c-5a9f-a883-1abf31d17b82 | checkpoint | A copy of the Ladder register has been submitted this month
3d903859-b52d-52dd-aabf-1957c83c9f42 | checkpoint | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
23484093-b5c0-5552-a60d-8d92e054fe12 | checkpoint | Temporary Works Design Register
75720ec4-cb43-5a56-a617-c22bb12e8de3 | note | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
fcd4c867-242a-5081-80f1-6d415a64ea0b | button | I have attached the updated Temporary Works Design Register | Yes,No
5d21287a-0bce-5c38-a159-cd6673bf2998 | button | I have attached Evidence of Engineering Certification | Yes,No
d80834eb-8560-5715-b772-28441493f097 | button | I have attached Evidence of 3rd Party review of engineering | Yes,No
92ddcd9e-8e9b-5040-844d-c86a13562740 | signoff | Signatures
6b425fde-3f4a-5270-aaee-4f741cfad8e2 | checklist | POLICY-005 Safe Work Procedure |  | POLICY-005 Safe Work Procedure
90e555f1-b7db-5342-8f6e-ab9bb0160482 | checkpoint | Task Details
6b8a15e8-1814-51de-b2fc-d7b36581e4ef | note | Use this form to record your safe work procedure after analysing a particular task in your workplace.
5f804626-2bf6-583d-b32c-3696a13b82f2 | textbox | Work Area:
4dfdb759-c64d-5e60-9066-dec37953d1a3 | textbox | Task:
8eaacf96-78df-51c3-a7e0-6d71022c5318 | textbox | Safety Risk: e.g. electricity, moving parts, noise
73bf96f4-9e1e-51a1-a557-4789936e6b2d | checkpoint | Personal Protective Equipment (PPE)
5034254c-49bc-523e-83d0-0b50696bada9 | note | The following PPE must be worn, and precautions taken, when doing this task:
cdecb107-8736-5cb7-b25f-52e301bc9c21 | tickbox | Work Gloves
6e006040-d637-51e0-91cc-4eeb1aa0a9f3 | tickbox | Safety Glasses
592e9b78-6a41-5096-a30a-282fb1e747da | tickbox | Steel Cap Boots
8cb5e136-c1b3-50f1-b5e6-ff562f09928d | tickbox | Ear Protection
840d696c-24fa-5198-8b53-9a564cb797c1 | tickbox | High Visibility Vest
3758635a-12ae-5a58-b054-3c6662f95579 | tickbox | Head Protection
cc98135d-18b4-52fb-9b0e-46fe68f2e071 | tickbox | Respiratory Mask
600ce93e-46c2-5018-afe5-a56decd65ec8 | tickbox | Face Mask
5afc56d6-b302-5a92-9797-bf2035abfd20 | tickbox | Protective Clothing
231ce415-f23a-56bd-bc16-9320b236ae58 | tickbox | Wash your Hands
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
4570fb2e-7310-5ac1-a58f-8ade9076d7c2 | signoff | BY SIGNING I CONFIRM I HAVE APPROVED THIS SAFE WORK PROCEDURE
e4a0efb6-0717-517c-b470-f52e30057f5e | checklist | REPORT-002 Hazard |  | REPORT-002 Hazard
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7016619e-d9e9-575d-a598-04fc8176f882 | checkpoint | Hazard Report
93e32352-041d-5e23-98d1-7c55ac68d30b | note | GM Fire employees shall complete a Hazard Report in the event they identify a hazard that may result in injury or incidents to person(s), property/plant, the public or the environment.
f95be724-d906-56a8-956e-4dbe1f4f3e23 | note | The principal contractor will be informed immediately and provided with a copy of this report.
423d5ed9-def2-5985-8cad-6c2afa7e0d08 | checkpoint | Hazard
2e2ba252-2b94-5726-957d-a9246c48bbd6 | textbox | What is the hazard?
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
871fff26-a68f-55e5-8332-45fe293ad849 | note | What are the contributing factors?
be7b97e3-98ec-5cb4-a09e-91cbc0697ea8 | tickbox | Environment such as noise, slip or trip
fa2b71ed-c42c-510b-87da-c9a4855d0b62 | tickbox | Equipment/ materials i.e. wrong or inadequate
8ade3482-199d-5f41-aecb-ba13517e4467 | tickbox | Work Systems i.e. inadequate training
4e60d88d-b879-5601-b937-736cd5c38b81 | tickbox | People i.e. production pressures, lack of communication, lack of procedures
84900e88-f611-5971-9011-3e679a876450 | tickbox | Other
3eb7311a-c940-5e36-95de-9eb6156356e4 | textbox | If 'Other' please specify:
5b8936dd-da50-5d1e-a2b4-e9a5b6b57cc3 | checkpoint | Corrective Action
db9683a6-2b79-5bf1-a0b1-6b4951e6a24f | textbox | What are we going to do to fix the problem?
0018ab99-bb90-598e-8304-d5aa874defc3 | textbox | Who
e869e1a2-deb0-522b-9389-e4013dc120fc | textbox | When
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
740b84cc-5645-5345-b613-707237dd7084 | checklist | REPORT-003 Chemicals Review |  | REPORT-003 Chemicals Review
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
62855fc8-1db7-4c9b-b4fe-c7ba6c14917c | checkpoint | Details
bfb7c958-cad7-53c6-8490-c1343b02d9eb | date | Date:
feac56dc-90cc-5231-b009-3c9291cea59a | textbox | Time:
eefd7d21-c3a8-5249-9155-dcea38b4b61b | checkpoint | Existing Register
8d55c9dd-04db-5648-a8a5-4c154ced93c4 | date | Last Revised on (date):
f2ef9a2e-52c8-55f5-b2ad-c4e6a815856f | note | Upload a photo of the "Register-006 Hazardous Chemicals" as it is on site today.
586de132-0677-5158-8fb0-c38150ef6201 | checkpoint | Chemicals on Site
1d27b382-af67-5a7b-bc9e-2d6b492aece1 | textbox | Location where Chemicals are being stored:
29f17690-ddcd-5f65-98a4-57c83c29296e | note | Upload a photo of each Chemical on site
8cbd2a0e-3c28-53bd-b9da-5a65540b2443 | checkpoint | SDS
2ada76e1-7ea6-5c44-ba68-a5551931dec6 | button | Have any of the SDS sheets expired? | Yes, No
a343ec4e-5118-557d-8266-3b5174cca6be | note | If 'yes', cease use of Chemical and contact GM Fire Management immediately.
dca38367-5449-5dee-ab5a-05d11f7596ee | note | Upload a photo of ALL Safety Data Sheets (SDS) on site.
58bfb4fd-b3d4-5f94-a67a-e067a225bcd0 | checkpoint | Declaration
c5d0e4e0-7604-548c-8ceb-62179bf0dbe6 | button | All Chemicals on site have been approved for use by the Principal Contractor | Yes, No
808cfcdb-5f69-515e-8f7e-58a089f4e815 | button | All Chemicals are stored securely | Yes, No
f1a7e5b3-8da7-555b-8e79-165c7cfc9ba1 | button | Any Chemicals that are no longer required on site have been removed and or disposed of as per WHSE guidelines | Yes, No
0da0ee29-0ac0-5051-ad4a-3e439a9e4b19 | signoff | BY SIGNING I CONFIRM I AM THE REPSONSIBLE PERSON FOR HAZARDOUS CHEMICALS ON THIS SITE, AND THAT ALL INFORMATION I HAVE PROVIDED IN THIS REPORT IS CURRENT AND TRUE.
42c7df9a-ccb8-5d7f-9abf-a956b1f84163 | checklist | REPORT-006 Incident Investigation |  | REPORT-006 Incident Investigation
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
6412ac75-35b3-555b-a89e-87d89553cfa8 | checkpoint-no-value | Incident Investigation Report
26c7a877-82ff-5d4d-9964-4e831bec896a | note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
c7009061-5139-5526-a062-83adc69dbabf | note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
0bb42031-c4a8-5bcf-80ff-6fc5304ee4f4 | checkpoint | Class of Incident
319b1c6b-9f44-55ea-b16c-b1a07631b0a3 | tickbox | Injury
0adde8bb-4f35-5400-993c-c7d0180c2af2 | tickbox | Property/Plant Damage
621668cf-7542-5404-a731-45e940e7d4ee | tickbox | Near Miss
95d75d3d-669b-5354-b3b0-96b4a129a1c0 | tickbox | Environmental
67776edd-303c-58ed-b6a4-4c93c3ad56de | tickbox | Other
c5515547-5acf-5223-adaf-ff810432bbba | textbox | If Other - Please explain
e433ee97-85b5-52fa-97a9-25ca60ea13bc | button | Reported to Princpal Contractor | Yes,No
857bb4fc-18cf-5306-a76e-802c247b752f | textbox | Details:
e1d07f73-ecd2-514f-8842-5a2e0effd57f | button | Further Action Required | Report to Authorities,Other
820f14d5-50a0-5c15-96c5-71e6e32d06c6 | textbox | If Other - Please explain
bc36afa9-00da-5f53-99b5-0b99d61a7935 | checkpoint | Details of Incident
92284681-efd2-53d4-8e0b-d46de0d7e437 | date | Date of Incident
673f8d24-ff72-5e07-b453-93880d52a9f4 | textbox | Time of Incident
325ed646-43a2-5fc3-9425-0bef6e03fe7f | button | am/pm | am,pm
4b70799d-acc0-5966-a907-0ef28ba3f126 | textbox | Witness Name
541505a5-4428-5a09-a1c7-efa380a6cf43 | textbox | Witness Contact
fdfff4a4-8f76-588d-97bd-e1944521b0f4 | textbox | Nature of Incident
725a55af-18c7-57c8-afe2-bfa092de1b6a | textbox | Location of Incident
3f3be10a-9abd-53e3-82f0-2667d7e71aa8 | textbox | Description of Incident
b482344c-2e6d-577b-9ddb-70e3d053f88b | textbox | Details of damage to equipment/property?
5acc9a29-5ef8-55dc-93ab-9320efe0254e | checkpoint | Injured Person/s (if applicable)
24e6a102-3cb8-5740-9562-2f6fcc5871ca | textbox | Name
c68b8d90-60e8-5111-8e35-d7857559c628 | textbox | Address
e678a59a-6b1f-5756-b6cf-2d17da084cb1 | date | Date of Birth
66d64f8b-744b-59a5-8649-41a77a1b3902 | textbox | Occupation
f3631539-86a5-543a-ad2e-dad8be5e4b52 | textbox | Employer
df6586a3-039d-5599-8263-333b90fa2c9b | textbox | Referred/transferred to
2653d5b4-f6f4-5d10-b061-5710923ec319 | section | What factors contributed to the incident?
673b3686-24cc-52e8-a200-da491c74d4d4 | checkpoint | Environment:
5bebb027-96f0-5460-890a-132a143a47e3 | tickbox | Noise
5e04e3c6-c511-54d9-855b-61b79ba33d83 | tickbox | Layout / design
be7367f6-b65c-5e31-9806-b57e064484b1 | tickbox | Lighting
b344a257-3875-58bf-9242-ae1b70d9c52a | tickbox | Dust / fume
c1b98094-8764-57ae-8d8f-23524f9f5e83 | tickbox | Vibration
c6079cb7-cfed-539d-a3de-4ffe5242c1a5 | tickbox | Slip / trip hazard
85c76db0-7b13-5e0b-b320-9a0f6543aa2d | tickbox | Damaged / unstable floor
1e95cef6-f5ed-5510-89c5-ba7214c48c16 | tickbox | Other
7af769cf-fdc6-5763-a34f-36b7668432b1 | textbox | Other (if applicable):
da263eea-7753-5dda-9253-36aae5136ab1 | checkpoint | Equipment/materials:
fe1e78dd-509e-5b53-8078-3c13e8d0020a | tickbox | Wrong equipment for the job
48449b5b-94f5-56fd-aa68-28179f2a1234 | tickbox | Equipment failure
34dbaa91-66eb-5b35-86e6-12b7080c0add | tickbox | Inadequate maintenance
340c7cf0-23ea-5aaf-be3e-08341656325a | tickbox | Material / equipment too heavy / awkward
d44177e4-2535-597e-9309-931a3a8d12ee | tickbox | Inadequate guarding
3d7d49b4-0c2b-5d53-bfdc-aa67787549d7 | tickbox | Inadequate training provided
000690e7-a449-5a80-a869-a79c71c27c48 | tickbox | Other
e2a3d872-b06f-56d7-868a-7dfc157a60c7 | textbox | Other (if applicable):
29bb93fe-1a56-5a6a-a4d8-caafbdc08848 | checkpoint | Work systems:
5dd9bf85-df05-50a5-9d39-ba8c92524aee | tickbox | Hazard not identified
2fbf68fc-22c1-530f-9cb2-b87b25344ca7 | tickbox | No / inadequate risk assessment conducted
0387a054-0cba-5d62-97d1-4479ebe8b41d | tickbox | No / inadequate safe work procedure
d37a698b-994a-54ae-81f2-b04aa7a1df63 | tickbox | No / inadequate controls implemented
c6ba7810-1a06-5766-8b22-30f4fdc6cfd1 | tickbox | Hazard not reported
8f15171b-ea63-518f-a1d3-40a0cdb8bb86 | tickbox | Inadequate training / supervision
22ddaef3-e684-5031-82f2-eabc39055e20 | tickbox | Other
df7a8e40-28bc-528b-b28a-0b6efe49c3d3 | textbox | Other (if applicable):
13eb0e36-06f7-5153-ba71-5b36d7104644 | checkpoint | People:
68c29607-73a8-59a9-918a-e8a1a7758f3b | tickbox | Procedure not followed / no procedure exists
f49a9eb6-f469-5486-a041-424512d20bb0 | tickbox | Drugs / alcohol
315224a4-528b-59d0-b752-048abb08d4dc | tickbox | Fatigue
2ed0f27c-86d8-5e84-a4f2-361debecd863 | tickbox | Time / production pressures
1cf8af67-af67-5409-bca2-d1a6cdab08ea | tickbox | Change of routine
91dc8070-c2b8-5f0c-bd24-be694c6f87a7 | tickbox | Distraction / personal issues / stress
06712e9c-8051-58f7-8676-16be7955cabe | tickbox | Lack of communication
feefc030-bfe5-5354-a12e-104f9508da2b | tickbox | Other
c3685b47-7234-5973-bc9c-d337e162b8f6 | textbox | Other (if applicable):
1c21ef12-b1aa-5192-a53b-a50ba28212cd | section | Corrective actions:
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
34fb92e3-cc81-5b39-9cc4-3570d31ea806 | textbox | (from above list)
73874509-bac9-555d-8853-d738436ac006 | textbox | What are we going to do to fix the problem?
da26fb44-6d60-52fb-870e-90b8c5ffd716 | textbox | Who
f5d8b083-01e8-5841-aea1-53e16258b921 | textbox | When
585d5a57-d317-5a2c-8c86-399f10c406d3 | date | Completion date
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
11f31f0b-4a44-5a8b-8133-2e07b430d536 | textbox | Name
9346513a-1500-5fae-b25b-d6e769dd31d7 | textbox | Position
40b6d092-dcdd-58fd-840d-c4a54e7f5c2d | date | Date
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
dbc03ac1-9ace-5f3e-8ff3-c49e802ff36e | checklist | REPORT-010 Request Corrective Action |  | REPORT-010 Request Corrective Action
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
a80c9dcc-a214-5e89-b5b4-bc2fa96fed3e | date | Date:
e76a599a-23af-5a4e-8106-9a96464e03c5 | textbox | Time:
2b7e31b1-c0ee-5d8c-a2b3-29bd72e55776 | textbox | Location:
ffa5d3f7-9abb-563a-ac4b-c0b159105ead | textbox | Supervisor Name:
d5aaa5eb-093f-5332-af20-a8b65033877e | checkpoint | Corrective Action Report
3596ee3e-b9a0-5fcc-a227-768c414bcebd | textbox | Principal Investigator
5a633b70-af3c-5569-ac46-19f4c906da41 | note | Non-Conformance is:
b2cef70c-f3ea-503d-b193-7e79f6e2f2f4 | tickbox | Minor
dccffc19-66f5-555d-827c-0821c540dab0 | tickbox | Major
bedbccce-bba7-57bf-b16e-63635aab07ee | tickbox | Critical
d3ef1ad9-5725-527b-aaf0-0f70fd0cc44d | textbox | Details of Non-Conformity Identified
e7d8de0c-474e-5908-bf1a-8efb1e852aa9 | button | What is the likelihood of Fatality? | Very likely, Likely, Unlikely, Highly Unlikely
756837a2-45bb-5671-93b4-f5d336f5aec3 | button | What is the likelihood of Major Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
f48f6abd-d3a0-5dab-8eab-ec0f9d354219 | button | What is the likelihood of Minor Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
55bb8c18-a30a-5382-829e-f9d63b69417e | button | What is the likelihood of Negligble Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
bdb68e70-6b9b-5a48-aa3f-1fae2f96008a | note | Add photo evidence if applicable.
5d294295-86ae-51e1-92b2-e35eee764d2a | checkpoint | Corrective Action Plan
e6ad6c61-d952-5a29-9fb7-b1627fe81371 | textbox | Describe corrective action
4a03bc21-fb92-58c6-ac2a-1c7526618563 | textbox | Is this plan permanent or temporary? | Pernament, Temporary
1b741756-ac92-5cc9-8728-ee6e9933086e | date | What is the proposed completion date?
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
2923664c-ab55-5c48-87d4-1901f7c5ef27 | signoff | BY SIGNING I CONFIRM I HAVE COMPLETED THIS REPORT TO THE BEST OF MY KNOWLEDGE

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
8b3b509a-75aa-5bb4-bf99-8e6b8d8e597b | checklist | 010SAF_08 SWMS - AIDP Ripley |  | 010SAF_08 SWMS - AIDP Ripley
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
e10de068-098a-54e4-9ca5-367664a0021d | note | GM FIRE 001 Working with Elevated Work Platforms
15671497-ad54-5d32-afa4-04d3f3c4b7b8 | note | GM FIRE 007 Manual Handling
520f9407-d01a-5995-b868-f3de1b60147e | note | GM FIRE 008 Working at Heights
fd6856ce-5fcf-5581-a5f9-83f42ae44906 | note | GM FIRE 051 Using Platform Ladders
98e081c0-c0f2-5647-a6e5-e314220d57ab | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
12aa4e47-69ce-583a-99b5-9ec6063e0430 | note | GM FIRE 009 Pressure Testing of Pipework
68ec500e-a59b-5b0b-b97e-769b3dde3619 | note | GM FIRE 031 Sprinkler System and Associated Pump Test
f9b74e32-e4b3-583e-91f9-e7b3e7f28716 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
96e187af-4508-5796-814d-edf71d430753 | note | GM FIRE 002 Wiring Rough In Minor
edf53965-a075-57b6-9e59-ee1f53c5eea8 | note | GM FIRE 003 Fit Off Fire Alarm System
6d09c463-be7a-5e4e-bf48-f312657a39db | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.