## Master List Templates
Id | Type | Name | Values | Prompting Name
65334946-7ad1-40ae-94fa-2e6946071ac2 | checklist | Upload Attachments |  | Upload Attachments
6da6f498-e18e-4121-84fe-5cd5ddfb8d03 | section | Details
abd1894c-f4ca-4bd7-adb7-c536eb29dab6 | checkpoint-no-value | Upload Attachments

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
6facfb0c-5759-4ec3-b23c-d8d68dc48160 | checklist | C - 7051 ITC-ITR - Mechanical ITC | itp | Mechanical ITC
8f39aa89-f948-4076-9ba1-ddca8d5476d0 | section | Location Details
1aebb473-fd27-4387-bc62-09681d46aefe | checkpoint | Details
e36ce310-9d7b-5b6c-951f-48fa79e9af20 | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
77124a0c-1d70-54ea-ba20-acbcf7960a08 | textbox | Row Number
1ad1c1c0-4bda-5cae-bbdd-e2e68e938950 | textbox | Table Number
9b22b676-50f5-4c89-b9e8-52889d22f11b | section | Construction
71c22888-0d21-40d8-bba3-d16ae90c69a4 | checkpoint | Mounting of Girders
f1586f09-024f-595c-8246-2bbeb5a2ded1 | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
800c92c6-bd42-546a-a5ec-89d17ccce8ef | note | ITC Mechanical Installation
94001e3e-ef88-527e-a228-1e1ed27bdeed | note | Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut
02915e6f-5b1b-5d30-932b-36f277ec8b1e | note | Torqued to value of +/- 5% of 53.2 - 58.8 Nm
3f3228ba-ccd9-560a-ac24-348323cc83bf | note | Each bolted connection shall be marked after torquing
9b8c4c53-26ca-4f54-bc41-dfa40c63f9c5 | checkpoint | Girder to Foundation Post Step Check
690c8009-69a9-5224-b363-b563a5591351 | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 9.0
09ae7102-fdef-5892-8a7a-2561b534bcf4 | note | ITC Mechanical Installation
76351a79-1260-5ce2-986a-4be4795ac3db | note | Angle of the Girder to the horizontal to be an angle of 23° +/- 1°
4292ae4a-3064-46d1-be9f-f8e2bf523170 | checkpoint | Purlin Connector Installation
12bdf820-8113-5509-8b3c-24b41ada5f72 | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
960b36ea-b8fa-57de-96fd-c802dc07a254 | note | ITC Mechanical Installation
fc55cb3e-eae8-59c7-9711-3f9f4bff11f0 | note | Purlin Connector placed under purlin
26bb3e8f-6735-54f2-a245-e7ba28541157 | note | Screwed together with Four x M10x25 bolts for LC/LT Purlins
85e1e245-e983-5605-a05c-e4d4d06f77c0 | note | Tightened to a torqued value of +/- 5% of 32Nm
9652dcff-c18f-586a-9eee-6c630c3aebee | note | Each bolted connection shall be marked after torquing
31c498ab-227f-43f9-b14b-ce5f62163dea | checkpoint | Purlin Mounting Checks
30490f0a-73fc-5cc4-846f-3977d09763ff | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
d169c3a3-a0c5-50a9-a7ef-93793e281bd2 | note | Purlin placed on top of the girder in correct direction
4446e3b4-dce5-52ae-8d11-e8e8fa868026 | note | FS Gen3 Girder Purlin connector bottom part attached
650c67c2-85e0-5c26-9c42-385321a08d0c | note | FS Flex Claw Installed
e6d1d163-ac27-52d9-a773-f1ce4d17f90c | note | Purlin Connector Attached
53bbf837-b92c-5297-8487-0893b38e03f1 | note | 3x Lengths as per IFC Design
94ef7cb8-612b-5dca-adb5-567f05dfc591 | note | East/West 4320mm-5310mm-4320mm
cf4fa027-2e4c-4b61-95c3-2d49993699eb | checkpoint | Connection of Girder and Purlin
d383810c-7ab6-5526-a238-e0046145473e | note | Schletter FS Duo - Fixed Tilt Instalation Procedure - Item 10
369f821f-69fd-538b-bb4f-3044878d99e2 | note | ITC Mechanical Installation
6cae3466-f3a5-510a-bbb2-906bb91d91bb | note | Girder
8648c22b-9079-558f-b11d-5953797010c7 | note | FS Flex Claw
e6e3017e-7922-51de-b198-89522870c55c | note | M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm
6fef94e0-bbbc-570c-88b0-1e77fba5f6f8 | note | M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm
4e8aa4e6-6548-446d-8c44-4046b5a3905f | section | Close-Out
018ab7cd-5595-4eac-be85-521add1dd73d | checkpoint | Non-Conformance-Reports
b775f3bf-6772-58f4-9d02-88951b664dec | note | Each Non-Conformance Reported, Rectified & Closed Out
ce391511-d7b3-47d6-bb30-e8c2c7b5b0ee | checkpoint | Table Mechanical Work Completed
5899f4ac-fc8f-5f40-bc7f-e3eca6318238 | note | Works completed for the table and checked
fd5a576f-473b-4b7b-943e-ff2e0d9cb9a3 | signoff | SIGN HERE
b76b7a9b-318b-437d-bc18-a7ec03f51c99 | checklist | C - 7051 ITC-ITR - Panel Installation ITC | itp | Panel Installation ITC
84b004a2-9be3-449c-84d3-a7f33d0e9858 | section | Location Details
ca5eb87c-25ca-4860-99f0-9ae8037cadc8 | checkpoint | Details
a04f617c-9da7-56bc-bbfe-047c3387deff | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
8ea7f151-935c-5fc4-a5ae-9d73eed7ece8 | textbox | Row Number
a1311ff6-e0d0-5db5-ac45-99d5819d74df | textbox | Table Number
f2437099-edd1-4cf9-a2dc-e7c63076bb7b | section | Construction
8bfcf3c2-6a6c-493d-9ad2-ab9a97a157a5 | checkpoint | Placing Module Clamps on Purlins
48325882-3a42-59f5-ae10-906d1c653181 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
ee113c3c-48a5-50e2-b699-ca93148c228d | note | ITC Panelling
5fac6022-3747-4a71-be7b-a24718b157c3 | checkpoint | Align Module and Tighten Clamps
384f7a8f-11c9-5d83-b6fc-b867efe10f48 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
5930a196-55f5-56b7-a105-99968bdc8ade | note | ITC Panelling
23094c85-32c3-4d73-be19-1f07a67074f4 | checkpoint | Align Module and gap between panels as per IFC Drawings
5c399d65-97cc-58c9-b7ae-46c65ee8f07b | note | Schletter FS DUO - Fixed-tilt Installation Procedure
89965199-47b8-57cf-b127-ffb948a55f49 | note | ITC Panelling
11c9f901-9046-5a3a-80d6-d6079014a285 | note | Top Panel to Bottom Panel: 5-10mm
db11b132-62ac-58e1-9b66-aa53d5b99334 | note | Panel with Module Clamps: 22mm
fc17cff4-59b3-4dc3-ad8c-a1dea40cf119 | checkpoint | Ensure Panels are dry, clean of dust/mud and no visible damage
ff5892ce-07d4-5bd4-8bcb-032cfd6dfe06 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
3838f2e4-8cdf-5302-976c-fbbc28ac9ce7 | note | ITC Panelling
aa149fe5-58c8-4cab-8f43-a4aef239d07e | checkpoint | Ensure Panels Start and Finish at even distances of the Purlin
6960ed9e-33f5-55c2-8fae-bf347f714e6e | note | 01_Maungaturoto_FS2V-23°-12_DUO_EX
489c585b-42c5-5805-9e3f-bcda49c6964e | note | 02_Maungaturoto_FS2V-23°-12_DUO_EX
7701ec70-6dbe-586a-932f-145ecf772af1 | note | ITC Panelling
9f55b68f-a9fd-5f8a-9587-c6567dcd7bf1 | note | Panels shall be 50mm from the ends of the purlins
0cee966a-21b2-445f-b2e8-3a6ce4ced673 | checkpoint | Ensure correct number of panels are installed for each table
88ed8e54-fc55-5a66-a265-07efff007add | note | Issued For Construction Drawings:
5c1cc5e4-3160-55f1-b91f-aa767f5b5577 | note | 01_Maungaturoto_FS2V-23*-12_DUO_EX
e60d08b7-0697-571e-afbb-8c65ffc9e6e6 | note | 02_Maungaturoto_FS2V-23*-12_DUO_EX
2bab54c3-46c1-5875-8f3a-2ec2bf6bd96f | note | Schletter Electronic Design Data
b4f102ef-a2d2-5e0b-a58e-ea804572c3f0 | note | ITC Panelling
e7f7feb7-db97-4581-ab25-380707bef90e | checkpoint | Ensure Panels are properly secured
1baed857-9c30-5ba5-bae5-6746787c0f57 | note | Schletter FS DUO - Fixed-tilt Installation Procedure
f9046feb-5654-5031-a0eb-f3aac28bb331 | note | ITC Panelling
044b050e-46c4-42fc-97b6-0ac1274e34a8 | section | Close-Out
379095e5-d8e3-4f18-a346-c93e7860af2d | checkpoint | Non-Conformance-Reports
46bc79cc-3690-50f0-904c-566dc82c778a | note | Each Non-Conformance Reported, Rectified & Closed Out
2eaa3569-3fe7-4b3f-981e-3e3cfc0cfa5d | checkpoint | Table Panel Installation Completed
9540b1ae-06aa-5aa8-aebf-392ec4bc838e | note | Works completed for the table and checked
c60af4fb-fb03-4d10-90b3-6192a63fdc7c | signoff | SIGN HERE
9f49e27c-2056-407f-a303-67f99efe0e7f | checklist | C - 7051 ITC-ITR - Pile Predrilling & Filling ITC | itp | Pile Predrilling & Filling ITC
5738c08d-86b4-4b6a-aee8-5fa146c5b879 | section | Location Details
6bda0d81-77cb-4baf-a585-016e28bbad72 | checkpoint | Details
1f596568-9c9d-507f-8dfa-9148345c32e3 | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
66ad2c96-597f-5b8b-801e-4a4ad0ddb2be | textbox | Row Number
91a37380-a01f-5a03-b483-721e8c68ab86 | textbox | Table Number
70f7f60f-fc23-5a06-8c42-02366c104d8f | dropdown | Number of Piles | 8 Pile,16 Pile,Other
0360103b-28b5-5317-9919-255653afb097 | textbox | If other, please specify
e3e599ae-f55f-4332-8ef2-4fee6b7066a6 | section | Drilling
508c71b4-a95c-4f7f-85e4-a8ec8c1e6a25 | checkpoint | Drilling
d4c7ded7-3d17-504f-bc36-ddb4cd2b53d9 | date | Date
32a8bf2a-60c0-5fc2-83f8-d7746a1a43ae | dropdown | Drill Depth | 1.8m,Other
9e74df0d-62f5-5017-abf3-3376daa16e42 | textbox | If other, please specify
e7ad25dd-3d6d-5c45-a3cd-4b0337653a13 | dropdown | Drill Width | 300mm,Other
785ca52e-e1c9-5697-a6b7-6ce38cd7cc47 | textbox | If other, please specify
580325e1-ec8e-4ebe-8b42-1ddd964442ca | checkpoint | Verticality +/- 3deg in each direction
6b0be5bf-672c-427e-8508-ce8b7e30a93d | section | Fill
86af1137-75f5-4602-b8d4-a643a6ccc8d5 | checkpoint | Fill
a319c738-9a0b-5371-94d4-fcd294c63e29 | dropdown | Predrill Fill Mix | 2MPa Flowable Fill from Atlas Concrete,Other
ecee9879-2951-57c4-9cec-0a6851849d83 | textbox | If other, please specify
dd6b58a0-8c65-41a2-ab77-af337dd4ff94 | section | Closeout
bbed9555-0561-4c05-b15d-4bb6e7387509 | checkpoint | Non-Conformances Closed Out
60dfc178-4415-52f2-9e08-50d4227ea150 | note | P,F,Attachment
f66a321b-e6e7-4aae-b3b0-8c6903328278 | checkpoint | Works checked & completed
c7e82b73-561e-4f34-8ad1-5c8aae3e0c77 | signoff | SIGN HERE
d4d49fb6-a788-4d67-84f9-aaa64d7adb28 | checklist | C - 7051 ITC-ITR - Piling ITC | itp | Piling ITC
2c59cffa-f77b-4d48-b2d7-2e806a3e03bf | section | Location Details
9c43fd9e-4ab9-4d18-ac64-e1cb29eb2f0b | checkpoint | Details
3b82aae6-5a76-572f-95c6-1cc5e99ffd5d | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
f85f1388-86a3-5eb1-a74a-76626ec0c47f | textbox | Row Number
9369a1e5-1e49-5c9e-802d-6220f2b28de8 | textbox | Table Number
4225b7ab-74b6-53ba-921d-b496e0bb45e8 | note | Number of Piles
ad779398-5f71-5d89-8baa-a2dca8f399c0 | tickbox | 8 Pile
b715c811-2158-5a46-9b66-f3651cf0aa6e | tickbox | 16 Pile
a6bb2bd2-2ac6-5deb-803c-5138e91c4ef5 | tickbox | Other
1c7c3fc3-5164-5713-a8ca-5365030f5d27 | textbox | If other, please specify
244f7754-8063-4499-b3fb-d7609a4b84fd | section | Preconstruction
f921aff3-73fa-4411-9681-aeb8f23c42a3 | checkpoint | Design
a0ea1765-f33c-556c-8db1-2c02a751306c | note | Issued For Construction Drawings:
4ce14052-82ce-503b-b87b-04a347a716b7 | note | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
ae7911c9-e560-52ec-9e53-55e1e43160a9 | note | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
e2cd379e-5ed3-5361-9912-6b12a9e306ce | note | ○ Schletter Electronic Design Data
3a1fb47c-814c-5a95-a3f6-2cfb62fee010 | note | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
25a4f4df-d6df-4c04-bf5f-17a621e964d2 | section | Construction
8b8bf062-7a28-4692-ba3f-4b4c092bd04b | checkpoint | Pile Distribution to respective blocks
99963f40-6f90-5d52-b019-199abc31f7cd | note | Survey Data
a75bdad7-8e4a-5cc5-9a53-4c9f91cece91 | note | ○ Schletter pile location data
4be5c9e6-a222-525d-abcc-cb7b13150a77 | note | Visual Inspection
79a1c68b-91d3-5d2c-a55f-6fc85947f830 | note | ○ Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length
706c3ff7-9c79-41c3-ad35-c70246f52a52 | checkpoint | Pile Refusal
ed7bec2c-cf94-52d5-9c4f-e94704de5660 | note | Drive piles to depth until they reach the point of refusal
42d03e63-fa10-5f0b-b531-44ac68aa0f5d | note | Record Pile location and mark on the drawing
eb386e04-e1ec-5c21-9af0-e5e1b8545979 | note | Record Actual Pile embedment Depth
785d5259-a18f-5421-8df7-56fb9ca58ef2 | note | Pile refusal in accordance with pile refusal procedure
1e2057e4-f9bc-550e-a882-22319dcd9b14 | note | Piles cut and holes drilled as per Schletter documentation
f61bee56-07eb-51c8-99cb-4b5088f2adb3 | note | Survey Record
2aa8946a-5fd5-52be-92cd-7d545f13c7f7 | note | ITC Data Tracker Excel Pile Monitoring Sheet
c8bebe9d-7286-5f44-9d65-69d4e85140e4 | note | – Embedment Depth
a3a44430-0007-51d0-98fc-4bcf23375d54 | note | – Reveal Height
12a3de77-aa35-572b-920c-8a58256807d2 | note | Pile Test Result documentation
c35cc98a-b980-4715-b484-7646e490d23f | checkpoint | Pile Predrill to minimum embedment
aa630883-4e45-5105-b929-ebcda616487c | note | For Each Pile
fab0c7ac-56ec-599b-ad2f-fda482e425e1 | note | Pile Predrill ITC
101bea9a-b9dc-5b72-a672-8583eb411b24 | note | Piles are minimum of 1.8m deep
0d78926f-396b-5c21-865a-292b968ca48c | note | Predrill holes are minimum of 300mm dia
b933a6ba-11b0-5cfe-977b-a2eac0a422bc | note | Backfilled with approved mix as per Schletters Installation Procedure
9141426a-a547-4da5-969c-a4c85c66f271 | checkpoint | Pile Installation
bd89ef17-f188-50d5-a6f8-7ff6c731360e | note | Schletter FS Duo Fixed-tilt Installation Procedure
d6824b71-5bbb-53eb-a05d-8df04b9dfc97 | note | Install Pile on the correct location as per Schletter drawing
d1764b30-9533-5467-88ae-a507148d6e37 | note | Install pile within the design tolerances
21c79310-7a83-573b-b074-5fe76a1ce81a | note | Piles should have no damage or deformation and in correct orientation
4c9d0a4f-3882-5498-a68e-074e5cb7d634 | note | North/South +/- 3°
4370ace4-7833-5bf9-afa6-060ad484673a | note | East/West +/- 3°
ff9adf8c-6d55-5325-9955-703518748c9b | note | Pile Twisting from axis +/- 5°
dbd6eb9d-569e-55ca-b90d-d3312337a4bc | note | Distance E/W +/- 100mm
9296f22c-88b5-5338-9934-e08f5cbc6238 | note | N/S +/- 50mm
19845f46-16ec-5fa4-a8fd-bc5253e4f5a2 | note | Reveal Height +/- 100mm
e1e10c35-b30c-58be-ae80-8957743454fc | note | Height difference foundation posts within one row +/- 50mm
6a234024-ceba-5e06-9188-4e4ca330d310 | note | Piles have no damage deformation and in correct orientation
5f1aa039-e75e-4689-af9e-c8fd46a3505a | checkpoint | Cold Galvanising Repair, if required
4f5df91c-934a-5069-99ac-af64d836d7ba | note | Schletter FS Duo Fixed-tilt Installation Procedure
31998d24-1d0d-538d-82ff-7b27df951c2a | note | Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer
8ede4410-24f4-48e9-921c-cff85c54e3b1 | section | Close-Out
afb5eeb7-147e-47f3-8534-0a4a2fa23912 | checkpoint | Non-Conformance-Reports
c125d2fd-915a-5415-8300-09a008f2e125 | note | Non-Conformances Closed Out
c842c45b-15c3-4a61-a52e-ae8a6ffa7425 | checkpoint | Table Piling Completed
fd61497a-e171-51a2-ad5a-0444e1fca77b | note | Table Piling Works checked & completed
aa03b4be-9620-4ec8-99bf-fe15e653eebb | signoff | SIGN HERE
53b42571-4ad7-4ef9-9303-2a304d708f37 | checklist | ITP - Module Installation | itp | ITP - Module Installation
5b7ae7d5-11ab-4874-bdff-013ff11e63f7 | section | Location Details
cb657d1b-d737-4621-ad61-528a95651e69 | checkpoint-no-value | Site Reference - Block
fba294e1-b473-51a1-95c6-d7cb0c4722ec | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19
0f17062d-ec77-42bf-ad7f-cad660bd256a | section | Preconstruction
a92a15a9-d562-4d97-8648-b43447929d49 | checkpoint | Design Review
a49a7296-f31c-55a7-8432-f90ca4cf3f28 | note | Verification of Module layout and mounting details
1710415f-6f1d-5a2d-adf2-fb38e98e8c46 | note | Compliance with approved drawings and structural analysis
c395b5d7-0358-5c12-9b7f-b4d82a9f3226 | note | Design Approval Documentation
0b552bc8-39a4-5c55-bc2c-4c0ee7beaaf0 | note | Schletter FS Duo - Fixed Tilt Installation Procedure
c3c11045-ddb7-59fb-9283-6b13e3b18536 | note | 01_Maungaturoto_FS2V-23°-12_DUO_EX
239d2bc1-a553-543f-820b-58fd12e3de8e | note | 02_Maungaturoto_FS2V-23°-12_DUO_EX
d32d3c85-0a5e-4f92-9df6-3c0456a29f25 | signoff | CHINT Hold Point
e64e356f-677e-4c24-987a-008dbd51b9c5 | checkpoint | Material Approval
647ed8c9-85a9-5946-8fbc-c7ab026b0402 | note | Approval of Solar Module components and hardware
53d3eeb7-0b35-51f7-8f9a-131d2d18dbba | note | Compliance with material specifications (e.g. certifications & warranties)
ff96a0ab-6d7c-5fbc-8842-0c5fbd125b42 | note | Material Test Certificates
2db7d6b1-b16d-410a-a795-3e2bfe3c2c0f | signoff | CHINT Hold Point
88c01fc0-ad57-497c-a58e-97b5b86be8a0 | checkpoint | Racking Inspection
af5b0e3a-350a-53fe-99d1-df00e8240696 | note | Verify racking system readiness for module installation
34ee68f9-1181-5f82-99d9-7bd0d15d858d | note | Properly installed and inspected as per Racking Installation ITP
cc3859df-e009-5873-90c3-d4972742ca4e | note | Inspection of all tables
0532fbe5-4153-4d46-af37-c341d0b44a7c | signoff | CHINT / United Civil Hold Point
a4b168b6-1063-4b7b-837c-7becf1682e91 | checkpoint | Equipment Verification
af4fd6cd-a930-59bf-b729-1c040a57e8bc | note | Inspect equipment and tools for installation
2bcb9175-ed55-5929-9ef3-373ea3e6e064 | note | Equipment is functional and calibrated
b5399334-73dc-5feb-9e76-75cbdb36fdd7 | note | Equipment Records where applicable
ea272fb9-dfae-42f6-a416-d626b9bdf8e9 | section | Construction
ace267a1-4448-4a82-8802-1c3e28900b3c | checkpoint | Module Handling
5324f0f5-699d-5431-a475-24d705962826 | note | Visual inspection of modules for damage during unloading
880fc288-85bb-517c-98f8-7168406e2cf8 | note | No visible cracks, chips, or scratches
7c3ba0a5-5fe6-4aa9-aca3-b488ecfdd2c5 | checkpoint | Mounting Hardware
b0565234-9b75-51b2-9b87-dd8effbc36e2 | note | Verify assembly ITCs as per Schletter FS Duo - Fixed Tilt Installation Procedure and secure mounting of hardware
5c9f2226-e31c-5f64-ae83-adc951761ee9 | note | As per manufacturer’s specifications within Schletter FS Duo Installation Manual
3b6f05a5-eb1f-5b21-8243-b5583b113129 | note | Visual Inspection
f6ed70c5-3879-4df3-8bd2-4932574e9861 | checkpoint | Module Mounting
e9083e42-5d10-59e2-8c1c-3fd968943d50 | note | Check alignment, tilt angle, and secure attachment
f4c101a5-ebfa-5c73-bbd3-d22d8a44f774 | note | Compliance with approved layout and tolerances within Schletter FS Duo Installation Procedure
649a452d-bdfe-4b4f-86a8-053b754c5781 | checkpoint | Align Modules and Tighten Clamps
c4e90e38-47cf-522a-9b86-bac06b1d6bb2 | note | Check alignment and verticality of installed frames and modules
4c1e9beb-59fa-5667-aff9-efa42378176d | note | Top panel to bottom panel to be between 5-10mm
a39fcc0b-4455-56a5-91c9-f60b3882179c | note | Horizontally between panels with module clamps: 22mm
d261eda1-29f1-5466-bfcc-e1e889fb4d14 | note | Panel clamps torqued to 15Nm and recorded as pass/fail in ITC's
c5b5ca8d-d20c-573f-ba5b-4820101f7e75 | note | K&T to check 100%, United Civil to check 15%, CHINT to check 5%
c6f998dd-dbc1-4ce1-89a8-bee736eb6467 | section | Post Construction and Handover
e3375f67-fb57-49fe-9060-3773d143bc8e | checkpoint | Final Walkthrough & Inspection
a867b1fa-8f11-5a06-af7f-662750ee76d0 | note | Comprehensive Visual Inspection of installed modules
4ce6746f-4f2c-53cb-9ba3-187012387012 | note | Inspect modules for alignment and cleanliness
00e42694-2394-598c-b90e-fc0e4a38a515 | note | No misalignment, defects, or debris
7d6fec9d-b0ca-5f12-bccd-6a209d06e6c0 | note | ITC's Completed for each table
3a03824c-c7fd-43fe-aede-f1b19830288e | signoff | CHINT / United Civil Hold Point
bd0a2294-55a0-4716-8a53-cd0c9f8b79c7 | checkpoint | Non-Conformance-Reports
acb91851-e3ac-5874-8b11-900b14cc1c6d | note | Each Non-Conformance Reported, Rectified & Closed Out
de6d4584-d889-4a49-ac29-df58b872a49f | checkpoint | Punch List
48e2808d-cc4c-5b0d-a787-047717851d76 | note | Development of Punchlist with Client and Contractor Representative
0d576349-9ac1-5904-a000-69fad4384786 | note | Punch List closed out in a timely manor
828c5655-b562-4700-a3b1-93bc6e3e7c02 | checkpoint | Documentation
1bdcabf9-9efc-57f5-9fad-96a033abd827 | note | On completion of the Module works for this Block
6b7ade3a-cd5d-5f09-ba0a-dbf11553b698 | note | Supply all documentation on completion of the Module works for the block
70b743ff-edf3-5b91-9a73-26878f982bee | note | Submission of all test results, ITC's and any as-built drawings
c539457a-5466-4fc2-a50d-f3f2fd5cf5e5 | signoff | CHINT / United Civil Hold Point
f4dd9af1-1226-476e-880c-52f88f9dfb1f | checklist | ITP - Pile Predrilling | itp | ITP - Pile Predrilling
47a92dcf-72bb-47a7-baa5-d7a11364a262 | section | Location Details
191d110d-3c31-4ba3-a26f-ad8c259c79fa | checkpoint-no-value | Site Reference - Block
2715b1b9-bd3b-57cd-9bc9-3a9790e6f00b | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19
6e61cfd0-677f-4a24-b8bc-bb3fe4e34978 | section | Preconstruction
7138a70b-da81-4777-8ae2-5619edfb808f | checkpoint | Design Review
e7765449-4556-57cf-9940-f213452c1bd8 | note | Verification of Piling Design and Layout
c86d3951-de9a-53c5-aa83-273c60209715 | note | Compliance with approved drawings and geotechnical report
ffc8e3ed-2488-52fa-977a-ba4ee22dfb13 | note | Design Approval Documentation
82256675-65d3-502e-8e75-5753242414fd | note | 01_Maungaturoto_FS2V-23°-12_DUO_EX
fc3af11a-7dfc-57cf-b74e-6d4b3c03413e | note | 02_Maungaturoto_FS2V-23°-12_DUO_EX
223530fc-d4ac-5b76-8923-74fd4f09b1cd | note | Schletter FS DUO - Fixed-tilt Installation Manual
b0413a7c-2460-51a4-bd31-6d870f363656 | note | Schletter Piling Instructions for Maungaturoto Solar Farm
30a889fa-7d5b-4b8e-90d8-9416a13c633f | signoff | CHINT / United Civil Hold Point
20d300c5-6eff-4fe4-8802-d4368f355039 | checkpoint | Material Approval
623bd0ff-c6af-53f8-a7ba-a6b520787e77 | note | Approval of drilling fluids or stabilizers (if applicable)
955cb29a-9e56-5331-b5fe-fd2cc521e907 | note | Compliance with specifications
ddd1c5f8-30f0-522e-a62b-2e6438aae84b | note | Material Test Certificates / Delivery Dockets for each delivery
40914853-3a64-485d-ac9b-e722b297050c | signoff | CHINT / United Civil Hold Point
9a05f42a-302d-44d3-ad72-e4a6eb81ea40 | checkpoint | Survey & Marking
6ea48678-515c-50ca-ab0b-38c74e73c7e7 | note | Visual Inspection of marked drilling points
33a21942-98ae-5a79-8bb8-ef2ca36328f5 | note | Visual Inspection of alignment and marking of pile locations
aba8fc74-c7f3-5ca6-99da-39db5ce6bde1 | note | Alignment with approved layout drawings
8470b2cc-46fc-493f-9d76-b5677daf1785 | signoff | United Civil Hold Point
899a21c6-c191-4477-b2e9-8bd7989e959a | checkpoint | Equipment Verification
5e5ea622-098b-5e90-910b-d17ed3612841 | note | Visual Inspection of drilling equipment functionality and calibration
5f882f34-ecf4-52a3-81b7-4d180eb76553 | note | Drilling equipment in good working condition
4cdb5905-58cb-5a64-a0db-dc7ab7605f71 | note | Visual Inspection of Plant Prestarts
0d981e27-458a-48aa-a4ee-c6e11a027914 | section | Drilling Operations
77979162-888a-4d14-8b1f-44751dceff0e | checkpoint | Drilling Alignment
41d3769e-2b47-5f0c-ac9c-50beb8d4cf60 | note | Check verticality and alignment of drilled holes for every hole
76718e6b-f4fd-5fc4-8a18-1e782d1963b8 | note | Hole should be within 3° of vertical in both North/South and East/West directions
dc265dac-df02-59e0-8b17-3519de7bf703 | note | Visual Inspection and Measurement
9583609a-dfd9-53e6-ad4e-65bd59e3a6f5 | note | ITC Record Updated for every table
d5d53481-370c-47f9-9b06-279eb61c3575 | checkpoint | Rock Penetration
9515115f-e26a-56bb-b21e-17ed3caa4bb3 | note | Confirm penetration into rock (if applicable)
cb05629a-a816-52bb-8897-2d7a5ae95005 | note | Achieves specified embedment depth
51057b76-6578-5121-8026-c0035566aeb7 | note | Drilling Logs
af595064-ee1e-4122-839e-be44e3ab6c95 | checkpoint | Spoil Removal
f6a47c01-f163-5861-bafa-a85fb2881416 | note | Spoil has been removed from each hole
6561bf1e-a7c1-5cb2-a7d5-8aba5a251d69 | note | Hole is clean and ready for pile placement
0dd862a0-16ba-581d-91ca-71002fb35c00 | note | Visual Inspection of the holes drilled
24fbacbd-f254-4cf6-bc60-d7814d542848 | checkpoint | Drilling Depth and Width
e1b76ae3-c594-5a52-b63b-fa8e30ad1e35 | note | The minimum depth for all holes shall be 1.5m
53194536-141a-5eb9-9d48-722c5ed2112c | note | The minimum width for all holes shall be 300mm
f119f456-e3c9-56e2-b092-339144c532cf | note | ITC Record Updated for every table
e18bab55-9172-417d-a7d9-e8872e36f6c8 | checkpoint | Predrill Hole Fill Media
c552a627-38e4-5b84-8a1d-dbed110f9373 | note | Predrill hole media to be Stabilised Sand
1e2b3ced-a554-543c-b95a-530c05905bbd | note | Material Test Certificates/Delivery Dockets Attached
162a377d-7815-4d02-b573-11af6f94e3ee | section | Post-Drilling Activities
166378a0-f1b9-47e9-bdcd-f0701342dfab | checkpoint | Cleaning and Preparation
90ee45fa-6000-51dc-8a16-84f9fdfc5b75 | note | Visual Inspection of cleanliness and condition of drilled holes
06ecbc0e-4f98-5729-b64a-2157b6365d74 | note | Free from debris and loose material
578503ea-1811-4745-a369-936780d9b645 | checkpoint | Stabilization
950c85ac-b602-5493-8c6f-64161c68076e | note | Verify stabilization measures (if required)
55d68ee0-13b0-5a4c-bf98-500df4787a81 | note | Free from debris and loose material
7072d798-09ae-49cc-a476-a515bc6dc817 | checkpoint | Survey Verification
4c9a3d40-69bc-5f08-ad90-df3844a0cac7 | note | Visual Inspection of resurvey alignment and location of drilled holes for piling
b03853c5-5081-5a53-9d56-981bdb75387e | note | Compliance with design tolerances
a8e8c80b-81ad-4739-8079-1a30e33f4a24 | section | Maintenance and Monitoring
75838ed2-aca2-4cd5-ab8d-ebc847a7994e | checkpoint | Equipment Maintenance
99590935-e8fd-5e7d-9625-31968124f0e1 | note | Inspect and maintain drilling equipment Daily
6d4f2f9a-3a7e-5186-bf14-a713d3f04877 | note | Proper functioning and safety compliance
0a0315f0-7420-5146-a120-2385b32b32b4 | note | Visual Inspection of daily maintenance records completed
c91fc784-1f4a-44a2-8ba2-062af38a5d18 | checkpoint | Drilled Holes
2a2ee23f-8812-5848-a969-32d8a5f5b8f8 | note | Monitor for collapse or deformation
b0a84230-ef22-5be0-9837-2ce578ebd04d | note | Holes maintain structural integrity
2d8c2401-b79b-490a-9a4a-af09cb924ba9 | section | Post Construction & Handover
8018ec57-f699-4e26-8acc-42a7c36cc736 | checkpoint | Final Inspection & Walkthrough
d4312288-96e3-5ebe-8de0-a5da523cccaa | note | Comprehensive Visual Inspection of all drilled holes
fbfd9587-9165-54f5-9b09-8ba3d1d0ebb0 | note | Compliance with approved design, function and specification requirements
13a1b9a4-dadf-5cbe-a82f-fdb43df5b551 | note | Verify readiness of drilled holes for piling
58e2fe0e-934e-5249-82a1-0806aeaf1993 | note | Area ready for subsequent construction activities
0dfc4168-6eed-46ba-ab3c-5b9cc533221a | signoff | CHINT / United Civil Hold Point
f5429da2-66d8-41d1-81e0-e2c1e3ec305e | checkpoint | Non-Conformance-Reports
b8d30fbc-18e3-52c7-9f3a-39bb063bd5d5 | note | Each Non-Conformance Reported, Rectified & Closed Out
4cf81f89-7ad5-452a-bb44-32c8116255a0 | checkpoint | Punch List
0d583cd1-8d78-5a12-b5d7-7ecb4d94b865 | note | Development of Punchlist with Client and Contractor Representative
ac79c287-1bf0-5f8c-b260-0c1f8d59d695 | note | Punch List closed out in a timely mannor
92d5ebc7-cf42-4c6f-98cd-00fb419b98f1 | checkpoint | Documentation
1801fdbe-a371-5da0-a0ae-3453933c9c49 | note | On completion of the Predrilling works for this Block
6ad0eb9e-0fe0-53a7-a7e8-f22e54d51c68 | note | Supply all documentation on completion of the Piling works for the block
32ef626f-9f26-5079-80f9-e128b8d89fcd | note | Submission of all test results, ITC's and any as-built drawings
1f70ab48-3435-4b97-b0b6-170285fd9e0c | signoff | CHINT / United Civil Hold Point
a9955f8f-0340-4a47-b054-c440a6ed6f40 | checklist | ITP - Piling | itp | ITP - Piling
417cbe03-c810-42f3-ad25-45e60e8db3b4 | section | Location Details
2bbd324b-0de0-4e25-9713-41b54104f6cc | checkpoint-no-value | Site Reference - Block
d6484470-d1f2-5bcb-966e-c1636eeb28df | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19
afbde610-a64d-4a79-a65a-c9cf5f2ff750 | section | Preconstruction
171e3de1-44c3-499a-91cc-681ea617d13c | checkpoint | Design Review
70a510aa-1195-51f0-a871-3a66864a4c8f | note | Verification of Piling Design and Layout
a9a2c67d-c456-5d6e-bc14-b5927534aed7 | note | Compliance with approved drawings and geotechnical report
d79bb9b5-67e2-5744-8219-55f489707ad9 | note | Design Approval Documentation
9c9f7b0d-8dd4-5627-9ddd-0e624beaef16 | note | 01_Maungaturoto_FS2V-23°-12_DUO_EX
c6986809-6f17-5a0b-8966-d56eff571626 | note | 02_Maungaturoto_FS2V-23°-12_DUO_EX
1b0e7035-0c66-5978-a1c8-a3f4dcc1be1e | note | Schletter FS DUO - Fixed-tilt Installation Manual
03efec73-c1e3-5709-9a53-6ef255af8e88 | note | Schletter Piling Instructions for Maungaturoto Solar Farm
b0645dc7-bb01-5444-bb88-280feb90f72b | note | In terms of the Piling Operation, in the event that early refusal is not observed, the Pile Testing done by Schletter prior to the construction phase is the extent of the Pile Testing done. Please refer to the Pile Testing Report provided for further details.
84d4f191-1aa4-4df3-9c89-329c3972da67 | signoff | CHINT / United Civil Hold Point
3f0463f8-1262-4153-b4c7-7a41931c7987 | checkpoint | Material Approval
099ddbbd-f772-5aff-9e1a-cbb404de770b | note | Approval of Piles and Coating
2d793514-a6a9-5d88-b6a0-035a2e72bff6 | note | Compliance with specifications (e.g., grade, dimensions, corrosion resistance)
f0acb642-7756-5866-9fdf-52b96aa22e5f | note | Material Test Certificates
adaf5dc2-d43e-4520-8b76-95fbfd56e2b1 | signoff | CHINT Hold Point
a37ad80b-bb49-4c31-9db7-3b6973ee894e | checkpoint | Design Verification
284288f6-f138-5987-9c8b-6f040bf670ca | note | Visual Inspection of Design
f9b3361d-1479-5f6f-9a4b-a2adef96fe95 | note | Client Review of ULS Testing and Geotechnical Reports
d7eec359-d204-51a0-bf24-df230e21674b | note | Pile Design Report/Drawings available
87966668-72c4-4797-8948-9301604cc8a8 | signoff | CHINT Hold Point
b09c0e72-e90a-4b9a-b20d-c191827f56b8 | checkpoint | Survey & Marking
315d28bd-1687-53a4-9650-a6bae415c181 | note | Visual Inspection of alignment and marking of pile locations
a6b820ad-5d8d-54ed-8e36-b99d0fd9940a | note | Alignment with approved IFC Drawings
ea4a717f-56e5-47a0-bd09-9c802f96a35d | checkpoint | Ground Preparation
8183135c-42b0-53bf-b67b-be90f2d55493 | note | Visual Inspection of clearing and levelling of the site
05124024-3485-5b54-a601-0ce99a9cbcef | note | Free from debris, vegetation, and obstructions
c1e98152-ca58-4cff-b28d-5a01303b9682 | checkpoint | Equipment Verification
32bc1ffd-58c4-55b2-8e45-f6909a443521 | note | Inspect equipment and tools for installation
b5a12022-812c-5400-bd74-6896ec151c56 | note | Equipment is functional and calibrated
eb7fa69e-398d-53bf-a1be-cf637f7f904a | note | Equipment Records where applicable
86453cd6-bd1c-41fa-87a5-6fa8598b2522 | section | Construction
8df580de-17da-45c1-86b0-d41920c91d53 | checkpoint | Pile Installation
b620027b-c58e-5d74-b864-e49ad62b6c74 | note | Schletter FS Duo Fixed-tilt Installation Manual
d5541111-fb78-5b64-aaca-1956ef3830ab | note | Schletter Piling Instructions for Maungaturoto Solar Farm
361426e6-5f8f-5e39-a5bf-9226a0efb291 | note | Piles installed in the correct locations as per Schletter drawings and electronics Setout data
cdebe89d-6961-5492-86e1-0a8fc7c80cc1 | note | All piles in every table are installed to the designs and every pile is checked for the following tolerances:
f4883c02-24b1-55c4-8ecd-d164b18ade97 | note | North/South +/- 3°
4baddc63-d506-5bdd-8e68-fac431bc8cbf | note | East/West +/- 3°
446d1a1d-f6ff-5c4f-90bc-930f587344d7 | note | Pile Twisting from axis +/- 5°
d2c2e529-ec54-5659-b7e1-22a2bc26f414 | note | Distance E/W +/- 100mm
f964e5dd-945a-5a68-9d01-ca2eac106b9e | note | N/S +/- 50mm
3f5c1a4d-0b7e-570e-a9e1-7725ce2a4798 | note | Reveal Height +/- 100mm
26dc3736-6056-57a0-8100-f97d02b9772f | note | Height difference foundation posts within one row +/- 50mm
e5a6fff7-3e52-50e9-929c-24abd2094f84 | note | Piles have no damage deformation and in correct orientation
12f03beb-812b-5f54-ab6c-8ab1040180a4 | note | Piling ITCs completed for each table
ae117c68-a74c-4d4f-a849-acf9e48697cb | signoff | United Civil Hold Point
6ecf03cc-6518-4141-ab09-047c6fa07688 | checkpoint | Pile Depth
d4b3a70e-70ff-5fa7-98ba-428f12bdd6bb | note | Drive piles to marked embedment depth or until they reach the point of refusal
668c6936-edcd-5bae-8718-22cf5c03a563 | note | Pile locations recorded and marked in Piling Maps
f3e71ae4-4c4c-5485-aad9-fa8de7c9fb66 | note | Record Actual Pile embedment Depth and reveal heights in Data Tracker
833e613d-559e-5239-b7d5-8c77ba295a38 | note | Pile refusal in accordance with Pile Installation Manual
02160caf-2ece-5ef0-9327-024710058f9a | note | Piles cut and holes drilled and cold galvanising applied as per Schletter Installation Instructions
da33221d-056b-5836-b36c-2bf7f64b4300 | note | Piles are installed to a minimum driven depth of 1.8m
09dd2bba-7320-5b65-bc7d-c6e8402eba40 | note | If Pile refusal is found at 1.5-1.7m Perform individual Pile Test with Vertical SLS Load: 11.31kN with a displacement of less than 5mm after resetting to 0kN and Horizontal SLS Load: 5.77kN with a displacement of less than 5mm after resetting to a load of 0kN.
e094a02c-e7a2-5b3d-875d-4d3daf66479a | note | If Pile refusal is found at shallow depth of <1.5m consider predrilling a 300mm diameter hole to a minimum of 1.5m in depth and backfill with stabilised sands and perform one pile test per area to determine foundation strength.
7cb0499b-2166-57f9-8585-dd4b76363151 | note | Piling ITC's completed for each table
4dd188bd-a97d-4251-ad1d-5258a5010be7 | signoff | United Civil Hold Point
e330e791-e213-4c25-ae34-1dee4f81660f | checkpoint | Pile Predrilling
4b8c79be-a1a8-5152-bd1d-83809ecfb102 | note | For every pile predrilled:
c1253d18-b270-53cd-a295-2a78bda8aa17 | note | Predrill pile holes to be drilled and cleaned out to a minimum of 1.5m deep and results recorded
9c82c0c3-06ca-56ed-abeb-851bbf05219e | note | Predrill holes are a minimum of 300mm diameter and results recorded
630305f5-ef31-54bf-aeb8-8602661ee4a0 | note | Pile Predrill holes are backfilled with an approved material
4c7911d9-1917-5ec5-b17b-757e79dfa53f | note | Predrilling ITC's completed for each table
f50ab4b5-8f2a-491f-9563-f774beb00b40 | signoff | United Civil Hold Point
9a6f3d2d-706a-49ba-9ee1-945153b5def9 | checkpoint | Cold Galvanisation Product Application
26765272-d51a-5fce-be45-6bb190cea2c7 | note | Review & approval of galvanisation product
b7a3e052-4572-5029-9cab-1c74dab1482c | note | Top 30mm of each pile must be sealed with an appropriate zinc coating as per Schletter FS Duo Installation Manual
13a7468e-829e-5c9d-a859-6648fbf6f144 | note | Application of zinc protection follow paint manufacturers recommendations
a8e53890-063f-5bad-b6a9-efc002251650 | note | Predrilling ITC's completed for each table
9cd5d5f7-bf04-4344-9fad-8e78e9b90582 | section | Post Installation Testing
1cee4012-5874-4846-900b-ed81e06c7033 | checkpoint | Refusal at depth (1.5-1.7m or less)
d6ed236a-abe2-50a9-a347-e8f665291353 | note | If Pile refusal is found at 1.5-1.7m Perform individual Pile Test with Vertical SLS Load: 11.31kN with a displacement of less than 5mm after resetting to 0kN and Horizontal SLS Load: 5.77kN with a displacement of less than 5mm after resetting to a load of 0kN.
b5ee74e9-5344-58b7-9c34-e0756d171fc0 | note | If Pile refusal is found at shallow depth of <1.5m predrilling a 300mm diameter hole to a minimum of 1.5m in depth and backfill with an approved material and perform one pile test per area to determine foundation strength.
b7022e84-80bb-55d6-88d5-d21f302b7c2f | note | Hold Point for United Civil
83ad09ad-8fe2-440b-8d09-0c6638c7aeda | signoff | United Civil Hold Point
6c5e4d57-ca31-4fa4-9444-aecc5234c742 | section | Post Construction & Handover
2895abb2-9b46-487b-b815-77facb015ef8 | checkpoint | Final Inspection & Walkthrough
32366832-7544-5638-83aa-fc76dfb8a1e6 | note | Comprehensive Visual Inspection of all installed piles
bb5a3fc0-60f7-5889-88ef-0af15794cc21 | note | Compliance with approved design and specifications
8a11eb12-fc9e-5e44-b9f5-649fed1eff3b | note | Verify all piles meet design and functional requirements
17fc5aac-936c-5c20-981a-dd64989b6375 | note | Area ready for subsequent construction activities
8e58dc91-4452-459a-aa83-ba60b9dccfd1 | signoff | CHINT / United Civil Hold Point
8b9651f1-6e97-48a6-b9b3-70db7159dd86 | checkpoint | Non-Conformance-Reports
6d4bcc16-824f-5f0f-95e6-9b010832e79a | note | Each Non-Conformance Reported, Rectified & Closed Out
c49f9713-a560-4a1e-bc16-af85516d230d | checkpoint | Punch List
48aaa1b3-1f3f-509c-8c31-e8336a3666e5 | note | Development of Punchlist with Client and Contractor Representative
e44b0c05-d58e-59c6-9e7f-2c266d132718 | note | Punch List closed out in a timely manor
9bbfbc75-0ddf-43ba-83fe-a4dc6e35c69d | checkpoint | Documentation
908e3ac0-686d-51a3-af28-885e4383541c | note | On completion of the Piling works for this Block
5a2cf4d0-52dc-5d0b-ab7a-1aacebcf1326 | note | Supply all documentation on completion of the Piling works for the block
6140b62f-0121-5f2e-9156-db0d42879a36 | note | Submission of all test results, ITC's and any as-built drawings
21e5d32f-6d5d-4850-a3e0-03329894c559 | signoff | CHINT / United Civil Hold Point
aa34db95-4182-41e6-ab77-bcb5bcbb8e9d | checklist | ITP - Racking Installation | itp | ITP - Racking Installation
284aef29-2bfd-461f-b7c3-ca4132b5c807 | section | Location Details
b2f81882-e54f-4bb8-8bc6-a3116e371087 | checkpoint-no-value | Site Reference - Block
2cf7d399-1aa7-536b-b37e-30b223e26dc6 | dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19
b17cd211-51a6-4933-8bc3-7f0aec9a0e08 | section | Preconstruction
272c4176-d6fc-404b-83b5-54554a7c7e20 | checkpoint | Design Review
cd811b5a-0eb7-5ccd-bde6-5e2eefb747d7 | note | Verification of Racking Design and Layout
5169d2d6-bd58-5b2b-9513-cd7a7c1f5db8 | note | Compliance with approved drawings and structural analysis
d4983793-262b-50d9-a019-c2e120be0c87 | note | Design Approval Documentation
48e3ca41-44c9-59bb-881b-8422afd48446 | note | Schletter FS Duo - Fixed Tilt Installation Procedure
5088cb05-0a75-51b8-a802-dbf17fc22865 | note | 01_Maungaturoto_FS2V-23°-12_DUO_EX
4da20fff-a405-5757-97ac-1bd50822da7d | note | 02_Maungaturoto_FS2V-23°-12_DUO_EX
e0e7c797-9910-45b8-b51a-4b34e71e8c22 | signoff | CHINT Hold Point
46cd5221-845d-46c6-8028-207d9c94f080 | checkpoint | Material Approval
b9482d2d-e7ec-5518-ad9d-5b6381195c4b | note | Approval of Racking components (e.g., frames, bolts etc)
6718eec8-2866-547b-8401-f31e1dee4050 | note | Compliance with material specifications & standards
0bd626f3-1760-5c15-9586-6eacb298166f | note | Material Test Certificates
e76c1d02-413e-4f50-bfb1-8741a907fa9a | signoff | CHINT Hold Point
8654d58f-8515-4be2-aaf6-dcb8f5d58df5 | checkpoint | Equipment Verification
8bb9caaa-6ef3-56b6-8340-5e228d800487 | note | Inspect equipment and tools for installation
087affe1-5e78-5cd9-9c15-e272d9c93ede | note | Equipment is functional and calibrated
e337db23-d937-51ef-8cf9-d361d999a5f7 | note | Equipment Records where applicable
e612d5ed-7431-453e-8f0c-fb61421b413b | checkpoint | Survey and Marking
af9f97b2-3a12-57c9-a6b4-5bfba0709c22 | note | Visually Inspect & Verify alignment and marking of racking locations
4326c08e-f1ad-501b-a299-89100e3016f3 | note | Alignment with approved layout drawings
e85e42c9-3bc0-4500-a747-00fe571bcb06 | checkpoint | Ground Preparation
353cd080-504e-5e1c-9143-9c0be21c749c | note | Visual Inspection of clearing and levelling of the site
d62ed969-9b50-573f-a341-12ff863d5d63 | note | Free from debris, vegetation, and obstructions
5c12277e-20f8-4b62-a74a-9e6d4e1e4a13 | checkpoint | Foundation Verification
880a2079-a72c-527d-8d42-c74151507ac0 | note | Verify foundation conditions and readiness for racking
4d875ab4-e3fb-527f-9f96-3f15a064c77b | note | Foundation integrity meets specifications
b22ad6cf-7588-58d4-b961-aba73aff5ca7 | note | ITC completed for each table with piles installed
b0a5cd1d-196e-423e-a827-f8725b6b8e43 | signoff | CHINT / United Civil Hold Point
006023d5-b88b-4759-965b-6589417e13fd | section | Racking Installation
1be3711c-9076-47b1-82de-0c0e477445e6 | checkpoint | Frame Assembly
6a848ec9-04e9-5a06-b0c6-baa7f99fea6a | note | Inspect assembly of racking frames
e849c9c4-20d2-56d5-9764-09faabe8bdaf | note | Proper assembly as per Schletter FS Duo Installation Manual specifications
c9baf65a-957f-520d-a98d-76874f369e90 | note | Visual Inspection of each frame
16062c84-b6ae-4889-9bc0-e8af2b9040e2 | signoff | United Civil Hold Point
de482ffc-cf6f-4683-9f64-829088fe7bc3 | section | Post Installation Checks
bd4bdd24-4010-49a1-bcd5-2a0b5ff9d557 | checkpoint | Mounting of Girders
b602d241-50ec-5dc1-92d7-d6b12fe0022e | note | Mechanical Installation ITC's are completed for Mounting of Girders
304cbfb0-3fc8-509a-b0cd-352b36b04202 | note | Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut
7e4b1b5e-d844-544b-83c1-e69eb8dc86e2 | note | Torqued to value of +/- 5% of 56Nm and pass/fail recorded
45e88ba9-c889-56fd-99f2-344659548774 | note | Each bolted connection shall be marked after torquing
e59ede91-53dd-5a5f-aed4-b9f5e1ec4080 | note | K&T to check 100%, United Civil to check 15%, CHINT to Check 5%
d0b192f8-3846-4c72-b84b-8989ae842ab2 | checkpoint | Girder to Foundation Post Step Check
f18c7559-fe92-5761-92f1-d1db21d92d91 | note | Mechanical Installation ITC's are completed for Girder to Post Installation
fee5a40f-774d-5022-b455-dd17a718a384 | note | All Angles of the Girders to the horizontal are an angle of 23° +/- 1°
f5400843-9383-521d-8795-c3dc0cf8c1f7 | note | K&T to check 100%, United Civil to check 15%, CHINT to check 5%
73aa7c4f-7527-40e5-b44c-603d90108761 | checkpoint | Purlin Connector Installation
49d89fdb-5b3a-557a-bb40-d0d758f6feb6 | note | Mechanical Installation ITC's completed for purlin connector installations
cf4d8890-f48a-52d3-8c52-861aae55b4f0 | note | Purlin Connector placed under purlin
fa067f89-b9aa-5447-8684-7fa610d6269b | note | Purlin Connectors are screwed together with Four x M10x25 bolts for LC/LT Purlins
b5e18762-cd4d-5306-99fe-aa273757788f | note | Tightened to a torqued value of +/- 5% of 32Nm and pass/fail recorded
3b89aca7-3880-5be7-8728-4ec34644bd8c | note | Each bolted connection shall be marked after torquing
441e8310-79f0-584f-a3b1-5360a9b300bf | note | K&T to check 100%, United Civil to check 15%, CHINT to check 5%
7eb6ef16-1533-43fe-8012-a10acbd14d06 | checkpoint | Purlin Mounting Checks
3a56014d-19b6-5cb0-9c41-ab1760479a3c | note | Purlins have been placed on top of the girders in correct direction
61e4adde-1fb0-5865-b77c-ce251454b78d | note | FS Gen3 Girder Purlin connector bottom attached
394ca061-a24d-563b-ab1d-bb63e13ac9fe | note | FS Flex Claw Installed
125b6e26-0c57-5395-b016-109a044d3e68 | note | K&T to check 100%, United Civil to check 15%, CHINT to check 5%
6cc84f4f-9082-45f0-a323-76680484d3ae | checkpoint | Bolted Connection of Girder and Purlin
8b611640-2c02-51c1-8f65-33c648e94b93 | note | Mechanical Installation ITC's are completed for each bolted connection
8d4018d3-20ed-59b7-adcd-00836fcb82e8 | note | M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm
a6835718-3723-5fb2-80de-1e3aa0eae478 | note | M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm
1b2e29ab-333d-505d-ac4c-a71b9fe58437 | note | K&T to check 100%, United Civil to check 15%, CHINT 5%
39ba529b-f628-45f1-92ba-56ce4261bc83 | section | Post Construction and Handover
71d203dc-f604-4aa4-bb72-acedc89d0df8 | checkpoint | Final Walkthrough & Inspection
3483bbf1-f509-5efa-8719-d93f698d5d14 | note | Comprehensive Visual Inspection of installed racking system
0f954c4b-e236-5b40-a17e-34ad15b0ab0d | note | Compliance with approved design and specifications
c0026596-dc40-4e03-a4fb-106fbb62fa93 | signoff | CHINT / United Civil Hold Point
60197642-4fcf-411e-8e87-3642177f7545 | checkpoint | Non-Conformance-Reports
451a7eaf-014e-5b67-8308-e4e92a7f7467 | note | Each Non-Conformance Reported, Rectified & Closed Out
d44c9eba-36ec-4145-a5c1-9ddd2ece7cbc | checkpoint | Punch List
52557aa5-f85e-5837-bb9c-c784dba8e993 | note | Development of Punchlist with Client and Contractor Representative
23920ac8-c09d-5b10-91b3-83781be3f94b | note | Punch List closed out in a timely manor
c8096065-f177-4366-8406-122e4f0cf438 | checkpoint | Documentation
d2dae3e4-b638-58e4-968c-86ad4eb67263 | note | On completion of the Racking works for this Block
3a8d66aa-3cd6-5df0-b6f0-327e523d0f19 | note | Supply all documentation on completion of the Racking works for the block
b9a03e2d-7b61-5a35-b97a-5bd76eaa5219 | note | Submission of all test results, ITC's and any as-built drawings
95530026-f4da-4595-9f32-bb4753538611 | signoff | CHINT / United Civil Hold Point