## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Combined Services - DCW Pipework Hydrostatic Pressure Test | [5 empty] | Combined Services - DCW Pipework Hydrostatic Pressure Test
section | 1.0 MATERIAL COMPLIANCE
checkpoint | 1.1 - RDM & Consent Approval
note | Resp. - CPB
note | Referenced Documentation - RDM Tracker Consent Tracker
note | Conformance Criteria - RDM approval tracker Consent approval tracker
note | Method - Document Review
note | Frequency - By Building/Site Wide
note | HP - CPB
note | Records - Receipt of Approval by Client
signoff | CPB Signature
checkpoint | 1.2 - General
note | Resp. - SE
note | Referenced Documentation - NZT5007-STE-HSSP-0001
note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
note | • Specifications & QA Documents Approved
note | • Drawings are confirmed
note | • Equipment fit for purpose
note | Method - DR
note | Frequency - Each material
note | HP - CPB
note | Records - Aconex approval
note | • Incoming Inspection Checklists
note | • Drawing Register
signoff | CPB Signature
section | 2.0 CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint | 2.1 - Confirm Flushing & Disinfection of Pipework
note | Resp. - SUP
note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0001
note | Conformance Criteria - 1. Air should be removed at each building prior to the DCW water supply water entry assembly to prevent debris from entering building.
note | 2. Ensure system sterilization completed.
note | 3. Ensure TNK filtration is cleaned/ inspected if not isolated from test.
note | 4. Ensure all screens/ strainers are cleaned/ inspected if not isolated from test.
note | Method - V + DR
note | Frequency - Once
note | WP - AE Smith
note | HP - CPB
note | Records - CMP + Check Sheet
signoff | CPB HP
checkpoint | 2.2 - Accept delivery of pump to site
note | Resp. - SUP
note | Referenced Documentation -
note | Conformance Criteria - 5. Check pump is rated for pressure test
note | 6. Check all supplied attachments are correct and in good order
note | 7. Check fluid levels & fill as necessary
note | Method - V
note | Frequency - Once
note | WP - AE Smith
note | Records - Check sheet
checkpoint | 2.3 - Isolate: Mains water Storage Tanks
note | Resp. - SUP
note | Referenced Documentation - AEC-NZ1005-TNK-DWD- HYD-006
note | Conformance Criteria - 1. Check Mains water is isolated
note | 2. Check Storage Tank is isolated
note | Method - V
note | Frequency - Once
note | WP - AE Smith
note | Records - Check Sheet
checkpoint | 2.4 - Connect pump to DWC ring mains
note | Resp. - SUP
note | Referenced Documentation - NZT5007-STE-HSSP-0001
note | Conformance Criteria - Confirm connections are safe and correct
note | Method - V
note | Frequency - Once
note | WP - AE Smith
note | Records - Check Sheet
checkpoint | 2.5 - Connect calibrated gauges for pressure test
note | Resp. - SUP
note | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
note | Conformance Criteria - Confirm position is correct, gauge is in good order for test & calibrated
note | Method - V + DR
note | Frequency - Each test
note | WP - AE Smith
note | Records - Check Sheet + Document
section | 3.0 HYDROSTATIC TEST
checkpoint | 3.1 - Fill DWC ring mains with domestic water
note | Resp. - SUP
note | Referenced Documentation -
note | Conformance Criteria - Completely fill closed loop system with water releasing all air from the Taps at each Building
note | Method - V
note | Frequency - Every time system is opened
note | WP - AE Smith
note | Records - Check Sheet
checkpoint | 3.2 - Gradually increase system pressure to 1550kPa
note | Resp. - SUP
note | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
note | Conformance Criteria - Slowly raise system pressure to 1550kPa
note | • Checking for any signs of leaks or pressure drops
note | Method - V+M
note | Frequency - Constantly Monitored
note | WP - AE Smith
note | Records - Check sheet
section | 4.0 COMPLETION RECORDS
checkpoint | 4.1 - Testing Results
note | Resp. - SE SUP
note | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
note | Conformance Criteria - All pipework pressure test reports shall be provided
note | Method - DR
note | Frequency - Each lot
note | WP - AE Smith
note | HP - AE Smith / CPB / IR
note | Records - Check Sheet
signoff | CPB Signature & separate IR Signature
checklist | Combined Services - Fire Inground Ring Main Pipework | [5 empty] | Combined Services - Fire Inground Ring Main Pipework
section | 1.0 MATERIAL COMPLIANCE
checkpoint | 1.1 - RDM & Consent Approval
note | Resp. - CPB
note | Referenced Documentation - RDM Tracker Consent Tracker
note | Conformance Criteria - RDM approval tracker Consent approval tracker
note | Method - Document Review
note | Frequency - By Building/Site Wide
note | HP - CPB
note | Records - Receipt of Approval by Client
signoff | CPB Signature
checkpoint | 1.2 - General
note | Resp. - SE
note | Referenced Documentation - NZT5007-STE-FSSP-0001
note | • NZS 4541:2013
note | • AS/NZS 2566.2
note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
note | • Specifications & QA Documents Approved
note | • Drawings are confirmed
note | • Equipment fit for purpose
note | Method - DR
note | Frequency - Each material
note | HP - CPB
note | Records - Aconex approval
note | • Incoming Inspection Checklists
note | • Drawing Register
signoff | CPB Signature
section | 2.0 CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint | 2.1 - Accept delivery of pump to site
note | Resp. - SUP
note | Referenced Documentation -
note | Conformance Criteria - 1. Check pump is rated for pressure test
note | 2. Check all supplied attachments are correct and in good order
note | 3. Check fluid levels & fill as necessary
note | Method - V
note | Frequency - Once
note | WP - AE Smith
note | Records - Check sheet
checkpoint | 2.2 - Connect pump to Fire ring mains
note | Resp. - SUP
note | Referenced Documentation - NZT5007-STE-FSSP-0001
note | Conformance Criteria - Confirm connections are safe and correct
note | Method - V
note | Frequency - Once
note | WP - AE Smith
note | Records - Check Sheet
checkpoint | 2.3 - Connect calibrated gauges for pressure test
note | Resp. - SUP
note | Referenced Documentation - NZT5007-STE-FSSP-0001
note | • AS/NZS 2566.2
note | • Clause 109.2 NZS 4541:2013
note | Conformance Criteria - Confirm position is correct, gauge is in good order for test & calibrated
note | Method - V + DR
note | Frequency - Each test
note | WP - AE Smith
note | Records - Check Sheet + Document
section | 3.0 HYDROSTATIC TEST
checkpoint | 3.1 - Fill Fire ring mains with domestic water
note | Resp. - SUP
note | Referenced Documentation -
note | Conformance Criteria - Completely fill closed loop system with water releasing all air from the Valves at each Building
note | Method - V
note | Frequency - Every time system is opened
note | WP - AE Smith
note | Records - Check Sheet
checkpoint | 3.2 - Gradually increase system pressure to 15.5 Bar
note | Resp. - SUP
note | Referenced Documentation - NZT5007-STE-FSSP-0001
note | • AS/NZS 2566.2
note | • Clause 109.2:NZS 4541:2013
note | Conformance Criteria - Slowly raise system pressure to 15.5 Bar
note | • Checking for any signs of leaks or pressure drops
note | Method - V+M
note | Frequency - Constantly Monitored
note | WP - AE Smith
note | Records - Check sheet
checkpoint | 3.3 - Stabilize 15.5 Bar pressure (START WITNESSED)
note | Resp. - SUP
note | Referenced Documentation - NZT5007-STE-FSSP-0001
note | • AS/NZS 2566.2
note | • Clause 109.2:NZS 4541:2013
note | Conformance Criteria - Record START time & photograph gauge
note | • All relevant parties to witness starting pressure of 15.5 Bar
note | Method - V+M
note | Frequency - Once
note | WP - AE Smith
note | HP - AE Smith / CPB / IR
note | Records - Check Sheet + Photos
signoff | CPB Signature & separate IR Signature
checkpoint | 3.4 - Hold 15.5 Bar pressure for 4Hours (END WITNESSED)
note | Resp. - SUP
note | Referenced Documentation - NZT5007-STE-HSSP-0001
note | • AS/NZS 3500.1:2021
note | • Clause 109.2:NZS 4541:2013
note | Conformance Criteria - Record FINISH time & photograph gauge
note | • All relevant parties to witness pressure of 15.5 Bar
note | Method - V+M
note | Frequency - Once
note | WP - AE Smith
note | HP - AE Smith / CPB / IR
note | Records - Check Sheet + Photos
signoff | CPB Signature & separate IR Signature
checkpoint | 3.5 - Pressure released or reduced for next test
note | Resp. - SUP
note | Referenced Documentation -
note | Conformance Criteria - Supervisor to ensure energy (pressure) is only stored while under test
note | Method - V+M
note | Frequency - Once
note | WP - AE Smith
note | Records - Check Sheet
checkpoint | 3.6 - Discharge pressure leave system in a safe state
note | Resp. - SUP
note | Referenced Documentation -
note | Conformance Criteria - Discharge system pressure, ensure area is left in a safe state meeting site requirement
note | Method - V+M
note | Frequency - Once
note | WP - AE Smith
note | Records - Check Sheet
section | 5.0 COMPLETION RECORDS
checkpoint | 12.1 - Testing Results
note | Resp. - SE SUP
note | Referenced Documentation - NZT5007-STE-FSSP-0001
note | • AS/NZS 2566.2
note | • NZS 4541:2013
note | Conformance Criteria - All pipework pressure test reports shall be provided
note | Method - DR
note | Frequency - Each lot
note | WP - AE Smith
note | HP - AE Smith / CPB / IR
note | Records - Check Sheet
signoff | CPB Signature & separate IR Signature