## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 15776937-588d-4e28-aa96-e959be61871f |  | checklist | A/C Checklist Commissioning [I] |  |  |  |  | Yes | A/C Checklist Commissioning [I] | 0207d080-672e-4f24-ba7c-7fa512b721f9
checkpoint-status | 624ca2e7-0ccb-495b-b967-dc4c17d1cf2c |  | checkpoint | Refrigeration lines have been pressurised and have maintained pressure for more than 24hrs?
checkpoint-status | 4c3de089-80c4-4e2b-97f8-9ca8e04e1cbb |  | checkpoint | Refrigerant lines have been vacuumed to 500 microns and maintained the vacuum?
checkpoint-status | ec2ad6f4-fabe-4da9-b17f-e46bf28cf891 |  | checkpoint | Indoor unit drains have been terminated to the tundish point?
checkpoint-status | 2ac2fc20-5547-4c42-831f-b17915ea4535 |  | checkpoint | Outdoor unit drains have been terminated to the tundish point?
checkpoint-status | 0cea28a5-bba6-43ff-810e-6c5766bf5292 |  | checkpoint | Indoor unit flare connection has been properly insulated with specified insulation?
checkpoint-status | 1c941cd9-212d-4d6e-827e-cd5e6c6786ac |  | checkpoint | Indoor unit drain connection point has been securely fastened and sealed?
checkpoint-status | bcdcec85-f3d1-4467-a9de-e88cf4d724b4 |  | checkpoint | A/C system has been operated for a minimum of 5hrs and no leaks are visible in the drain lines?
checkpoint-status | 632af249-ce54-4e56-a882-ef6d1dffc21b |  | checkpoint | Adequate flow has been achieved in bedroom 1?
checkpoint-status | abfd4ad7-7e18-4d3c-a611-f9eb4f05ba44 |  | checkpoint | Adequate flow has been achieved in bedroom 2?
checkpoint-status | ee747dd8-86c6-4438-890f-8f64efc3c807 |  | checkpoint | Adequate flow has been achieved in bedroom 3/study?
checkpoint-status | 4fd6b0db-f615-4323-a282-f6d3fa60d9a2 |  | checkpoint | Adequate flow has been achieved in living room?
checkpoint-status | 8f6d3c66-fc30-47ba-9c55-8db99b776165 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 3d6a176a-41eb-4156-81e5-d92c425a3b07 |  | checkpoint | Inspection Date
checkpoint-status | 3f37ceb7-9dc3-4560-a3f2-bbd361d848dd |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | 1c3bcb21-5ce2-437e-960b-8cbc2373494c |  | checkpoint | Builder Representative Sign Off
checkpoint-status | c20f6bee-d82a-45b5-a244-36c1364cbc2c |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | ef669986-1281-4211-8b1e-f3cb02f3abe4 |  | checklist | Fire Damper Checklist -IBD-FS-A [K] |  |  |  |  | Yes | Fire Damper Checklist -IBD-FS-A [K] | 0461fd14-da1b-40b0-b7f0-18a2e7506c10
checkpoint-status | 29c739a7-2d1c-4d10-b792-679d33f6bdbf |  | checkpoint | Penetration details have been captured
checkpoint-status | 03467ead-a041-4eba-8890-c2d5e9b1c01f |  | checkpoint | Gaps between the fire damper and wall no greater than 25mm and is filled with Lorient Intumescent Sealant with no cracking visible
checkpoint-status | 58e7e195-2579-41b2-b98b-24acc283411c |  | checkpoint | Appropriate fire rated mastic has been applied to entire perimeter of fire damper cell on both sides. No evidence of cracking.
checkpoint-status | a28c6027-d481-4228-ab3f-09c9c5553997 |  | checkpoint | Casing perimeter is sealed with Appropriate intumescent sealant. No evidence of cracking.
checkpoint-status | f0523493-ab8d-46be-85ea-d1f8b98d47dd |  | checkpoint | Mechanically fix the branch to the vertical riser with steel screws or pop rivets
checkpoint-status | 1fe71261-94c8-45f4-be80-4894da712d46 |  | checkpoint | Sheet metal thickness is 0.7mm or greater.
checkpoint-status | 7ac3c950-32e8-4d56-97b8-1e9417eebcf5 |  | checkpoint | Ductwork is connected to either side of the casing with nylon bolts on the flanges as per the AS1682.2 break away joint method. Bolts do not exceed an 8mm diameter.
checkpoint-status | 8c028e20-fbbd-46cf-b05a-eebe62e57b8d |  | checkpoint | Breakaway Joint is in the allowable distance from the wall (Max 150mm)
checkpoint-status | 2a52ca81-20ba-4f29-b303-822b8eecc666 |  | checkpoint | Access panel is provided to conveniently access fire damper for visual and/or maintenance inspections.
checkpoint-status | ce832925-8f0f-4fe7-a2e9-3649223ce0dc |  | checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
checkpoint-status | e296e7fc-af94-4854-ab59-97af4ce5d6c6 |  | checkpoint | Pictures attached
checkpoint-status | d15a0ff5-dde2-4655-8f85-fdeaa5101192 |  | checkpoint | Signature (Contract/Subcontractor Assessor)
checkpoint-status | 11a8a2d6-bda2-4c50-b2f4-1e83b50e2913 |  | checkpoint | Signature (Builder Representative)
checkpoint-status | c602ae7f-2ea7-432b-a4b1-b2f4d77ee3f9 |  | checkpoint | Pictures/Comments attached below
checkpoint-status | 936d0a1f-dade-4494-9e29-c53d50813412 |  | checkpoint | Notes/Additional Comments
checkpoint-status | 31d6db9b-dd17-476a-abc8-b0ca5f00ed45 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 89580426-ba25-4ff0-a44d-c5de34f98c24 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | f5fad26a-2e79-44a1-bab3-ccfee9ba5884 |  | checkpoint | Builder Representative Sign Off
checkpoint-status | 944448b4-b595-4b69-a81b-699c5f3048db |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 578bc445-5332-44eb-87e7-c5e4492ad45a |  | checklist | Ventilation Checklist 1 Rough In [C] |  |  |  |  | Yes | Ventilation Checklist 1 Rough In [C] | 17b0fb6e-a6f9-40e4-9f53-2d3b1b9e9df3
checkpoint-status | fb770396-4183-4733-b708-f403d78f0665 |  | checkpoint | Plenum Boxes are installed and sealed in the perimeter of the penetration
checkpoint-status | 016f9f7e-ce00-4f51-9227-e8753aa03242 |  | checkpoint | All Flex has been run to correct location
checkpoint-status | 1df88041-5ab6-4869-b581-f48d7ec8ab77 |  | checkpoint | All flex are hung independent of other services and supported by intact load spreaders
checkpoint-status | 2dfa29af-faa6-4a9b-af0a-95e0ac10abb8 |  | checkpoint | PVC sleeves has been installed in wet area walls
checkpoint-status | 65aee4e9-07aa-47e1-8d37-cda688d7110a |  | checkpoint | Fresh Fan and associated ductwork installed as per mechanical drawings
checkpoint-status | ea8481a1-7f38-45ba-816a-a70aef3f9c1a |  | checkpoint | All Flexible duct connection to the Spigots are tightened by Duct tape internally and Draw bans externally
checkpoint-status | cf8171b6-5928-4d8f-b06c-eadb9e858603 |  | checkpoint | Vent boxes are installed in correct location as per RCP and SEALED
checkpoint-status | 9ca30436-b714-45e1-ba97-ece463b25d97 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 9c1cf7f8-fe4b-4fbc-8488-739792272339 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | eee07699-74ec-422c-9936-70afcf0edd56 |  | checkpoint | Builder Representative Sign Off
checkpoint-status | 509d5f51-574d-4ee7-97ea-a416cf40884f |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
text | 50021902-ac89-5f70-af47-44d772fadc2a |  | textbox | Inspection Date:
checklist-flat | 19009887-c347-44d6-b942-ee22d93cf747 |  | checklist | Wall Closure Checklist 1 Rough In [A] |  |  |  |  | Yes | Wall Closure Checklist 1 Rough In [A] | 247140f5-9372-42ce-a5ba-a69cbd684940
checkpoint-status | 60b6e3f6-7661-44d4-94cd-1411b60b2545 |  | checkpoint | Pipe cavities have been sealed
checkpoint-status | bbefea6c-62b8-451e-9f6a-b3c88931d5d5 |  | checkpoint | All wiring including interconnection wiring and power from isolator to the condensers are roughed without defect
checkpoint-status | 758b3837-00b8-4f61-823e-359dc5f10de0 |  | checkpoint | Drains have been run to Tundish
checkpoint-status | f539f6c7-efa7-46ff-87f3-a791005dde8b |  | checkpoint | Refrigeration insulation is not damaged
checkpoint-status | eb131bae-2397-4cc0-953d-2e1a90b2e598 |  | checkpoint | Refrigeration pipes are run through cavity without being kinked or damaged
checkpoint-status | 080e9627-e26c-4b6d-b2a2-10979e7b2736 |  | checkpoint | Drains have been tested and witnessed by Builder Representative
checkpoint-status | 1c965b7d-578d-4a28-86e2-d272158b5a13 |  | checkpoint | Plenum Boxes are installed and sealed in the perimeter of the penetration
checkpoint-status | 1e240636-ae8e-4ccf-bb33-1139f64d735e |  | checkpoint | Unit Model Number and name plate matched the AC schedule
checkpoint-status | ed788934-99b3-4450-b4a2-9122cca4c95d |  | checkpoint | Unit Height is in accordance with the RCP and drain fall requirement
checkpoint-status | c7ed4c94-8ac3-45c2-b5da-38834e855700 |  | checkpoint | Flexible duct runs to ceiling areas are in the correct location as per Mechanical Drawings to connect to Ceiling Fan
checkpoint-status | bc71e692-dce7-4bba-be19-859d484855dc |  | checkpoint | All Flex has been run to correct location
checkpoint-status | 8680d5bf-ee47-4960-ac29-49d97a904fd8 |  | checkpoint | All flex are hung independent of other services and supported by intact load spreaders
checkpoint-status | 60146cbd-808d-4aa5-be59-13c79a81809d |  | checkpoint | PVC sleeves has been installed in wet area walls
checkpoint-status | 9c28b88b-6c02-4813-95b7-f403561875ab |  | checkpoint | Fresh Fan and associated ductwork installed as per mechanical drawings
checkpoint-status | 85c7a740-940b-4b88-9477-7e89ff94402e |  | checkpoint | All Flexible duct connection to the Spigots are tightened by Duct tape internally and Draw bans externally
checkpoint-status | e35bfb41-3a88-4ef2-a7c3-e29fd0726514 |  | checkpoint | Vent boxes are installed in correct location as per RCP and SEALED
checkpoint-status | 38c95a02-b795-44d8-b6b4-26acb9e9b054 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | fdfed1a4-d7e2-47e6-a34c-05df8e9c14c2 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | 2c7fcef0-37b0-45bd-87ed-89a566159f62 |  | checkpoint | Builder Representative Sign Off
checkpoint-status | 3fa67559-aadf-40b7-91f7-4003971f4fd2 |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
checkpoint-status | 052e3a03-4728-4716-836d-c894c38cc8a9 |  | checkpoint | Inspection Date:
checklist-flat | 91e400e4-ff91-4230-91f5-6c2bc6572c48 |  | checklist | Duct Installation Check List [F] |  |  |  |  | Yes | Duct Installation Check List [F] | 36c3e933-31d8-4170-975e-6bb9fa829e70
checkpoint-status | a6a0b18e-6733-4eb6-ad75-e58c560138f3 |  | checkpoint | Are drawings on site the latest issue
checkpoint-status | 2bd8b5d5-506e-4a91-9e3b-d7e07a7eaac0 |  | checkpoint | Are plant and equipment location correct
checkpoint-status | 42e2327e-6c45-4ba4-afa9-18d298dc6ffa |  | checkpoint | Duct size and location correct
checkpoint-status | 866d7160-639a-4242-9612-0155ddc4f071 |  | checkpoint | Material and gauge correct
checkpoint-status | 0bf13a0c-928f-4e0e-a788-41c95488ec9f |  | checkpoint | Is correct support method being used - Risers are supported at each level.
checkpoint-status | 50d9fdb9-1be2-4fa3-a373-06b8185ff73d |  | checkpoint | Is correct jointing method being used
checkpoint-status | 515027d8-e31f-4fd3-bc10-c48bc37e87f7 |  | checkpoint | Are joints completed and cleated installed on flanges
checkpoint-status | 5257c6c6-1a8e-472e-a326-d502daa8d976 |  | checkpoint | Is correct joint sealant being used
checkpoint-status | 6ec1550f-4be8-49ce-8620-a747b7d5b3f4 |  | checkpoint | Are fire dampers installed and break away joint complete
checkpoint-status | b6e1f312-74ec-4147-a92f-b6b075d6d082 |  | checkpoint | Are flexible ducts installed, supported and connected to spigot by approved method using duct tape on internal core and cable tie on outer core
checkpoint-status | 3a8215dc-e9c8-4884-b427-3d915d1aec5d |  | checkpoint | Are flexible connections to equipment sealed and aligned
checkpoint-status | 879c101c-ef39-4303-bc28-538865523368 |  | checkpoint | Is ductwork insulation as per drawings
checkpoint-status | 73e9f116-95e9-4766-9c94-9f690a54e04d |  | checkpoint | Is ductwork fire rating complete
checkpoint-status | 15710fb7-b9ea-4032-968b-5ed2fa55acc4 |  | checkpoint | Are all spigots installed and dampers fully open
checkpoint-status | e52e679b-3083-4043-9bf0-0bed3dcbc06c |  | checkpoint | Are all access panels for fire damper access installed and closed
checkpoint-status | 16d0e54f-76d1-4797-953d-311a94c9e277 |  | checkpoint | Is ductwork installation complete
checklist-flat | 759114e3-c597-4b20-ac42-96469515ac00 |  | checklist | Job Details |  |  |  |  | Yes | Job Details | 4184fb8d-fe60-4374-879d-f6ba7ffc3d96
checkpoint-status | 6aa207eb-5254-4363-9ad6-efcca7d2d478 |  | checkpoint | Site Info
text | 3b648171-c477-5bbe-8ffa-3a6f0c4a5b47 |  | textbox | Site Address
text | 27e1d5fe-2a4a-50a5-b1ed-ffb62ed10cb6 |  | textbox | Builders Details
text | da23b250-c2bc-5f27-9f75-c486988869d8 |  | textbox | Project Managers Details
text | 72fd0e93-972a-5f64-9ce8-4bcfeca941c6 |  | textbox | Site Managers Details
checkpoint-status | e33fb0ad-ce34-430a-90f7-e4d867795da0 |  | checkpoint | latest drawings (attached or referenced)
checkpoint-status | fae211e3-8372-4c37-929d-3f62cc020c87 |  | checkpoint | Scope of Works Attached
checkpoint-status | 5fa57453-e28a-4fb8-a4c0-c5dc360a8475 |  | checkpoint | Additional Pre-Start Docs (attached or referenced)
checklist-flat | 41b47336-a54e-4471-89e1-715eedda3bd8 |  | checklist | Ceiling Closure Checklist 1 Rough In [B] |  |  |  |  | Yes | Ceiling Closure Checklist 1 Rough In [B] | 6167db07-2e43-428f-8648-41e02146ceb3
checkpoint-status | bb1514a5-9f3b-4e51-892e-778415d6895e |  | checkpoint | Units all hung with isolation mounts and with slight fall to drain point
text | e93d182b-2d47-563c-a25b-791cf147bb8d |  | textbox | Inspection Date:
checkpoint-status | 68fe7b13-89f0-4910-b3e6-cdeb7cbc3b62 |  | checkpoint | Other services installed are not impeding access to fan coil
checkpoint-status | 4d3b7a15-1f2b-4144-b920-d366a7685e16 |  | checkpoint | Wiring connected to indoor unit
checkpoint-status | 2d64f4b5-7cdd-46d4-b0bd-dc57a0da4158 |  | checkpoint | Condensate drainage is in correct location
checkpoint-status | 6d15372c-ac00-480b-a7b8-beb98034a535 |  | checkpoint | Fresh Fan and associated ductwork installed as per mechanical drawings
checkpoint-status | de468c8f-4426-4eb8-bc5d-c236fd60149c |  | checkpoint | All flexible ductwork are equipped with load spreader
checkpoint-status | 3a650967-a626-4827-a568-5c47a73d9230 |  | checkpoint | All Flexible duct connection to the Spigots are tightened by Duct tape internally and Draw bans externally
checkpoint-status | 2c865287-9d93-4944-baea-573114a5b324 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | d7f3f999-0c59-4067-bcce-ffb58d175a60 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | fad18e3c-9587-4d89-88b3-18357e955762 |  | checkpoint | Builder Representative Sign Off
checkpoint-status | 2ad7245c-8cc9-46dc-83dc-8f44c3c28b83 |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
text | 1b570f05-7f13-5d48-811c-b2e4c1c029d6 |  | textbox | Inspection Date:
checklist-flat | d291fbcd-e1a1-47f7-a796-8d29c083019d |  | checklist | Prestart OH&S Documents |  |  |  |  | Yes | Prestart OH&S Documents | 96ce13c8-77d2-4c69-8d58-b9774ddebe9a
checkpoint-status | b863da0e-ca27-4bc7-8a6e-abb06c89b77d |  | checkpoint | All Pre-start OH&S Documentation Completed, Reviewed & Attached
label | 13e7b56e-7ba7-5274-b701-c6f14d60a35e |  | note | Public Liability and Work Cover Insurances
label | 7dd33892-5742-560c-a243-cc1aa7260b53 |  | note | Company Safety Plan
label | a1c8a123-0e0b-5041-92fb-7cdceafd0c08 |  | note | SWMS & MSDS (Attached below)
label | 44533c08-1f6b-53ec-be11-85197ba7750a |  | note | Additional Prestart OH&S Documents
checklist-flat | c80833e0-dc8c-4cb5-8551-f1072eb3dd0a |  | checklist | Splt System Fitt off[M] |  |  |  |  | Yes | Splt System Fitt off[M] | 992e69ea-6eaf-4f39-87c2-db37e68f311d
checkpoint-status | 4b5a273a-7471-4478-858d-315fd59fcf4c |  | checkpoint | Wall mounted indoor unit installed
checkpoint-status | 8cf8d3e6-147a-4ab7-bbcd-b2fdb48c45d7 |  | checkpoint | Condenser installed on Vibration pads
checkpoint-status | 9b086d0c-c61e-41eb-89b5-c3cafa37984b |  | checkpoint | Drain from indoor unit is terminated to the tundish point
checkpoint-status | 8bfd6f0f-798e-4b93-ad5a-8fa8cf511563 |  | checkpoint | Drain from outdoor unit is terminated to the tundish point
checkpoint-status | 76e62e1f-2330-4154-a646-12eeb64ba777 |  | checkpoint | AC wall bracket is installed in as per location shown in the drawings/ Agreed with Builder
checkpoint-status | e9b29eb5-430b-4453-b1a5-3ccfe00a62ae |  | checkpoint | Inspection Date
checkpoint-status | 76a0e23b-89c6-4ccf-8424-e003c0595c22 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | b84eedc2-ef7e-4dec-8ef6-dafe56083d1c |  | checkpoint | Builder Representative Sign Off
checkpoint-status | f20edc1b-b125-4c79-b565-d467e51a3f3c |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 86320732-c5ac-401c-9de9-4c0de6fc52b5 |  | checklist | Carpark Fit-Off Checklist [L] |  |  |  |  | Yes | Carpark Fit-Off Checklist [L] | 9e853faa-c669-42cc-9ab6-c233b1f3b902
checkpoint-status | cd9ce8e7-41d3-4db3-923a-e68eb63d0e01 |  | checkpoint | All grilles fitted
checkpoint-status | 5ffa779b-2d1a-4828-bd20-cd091ca7ad7b |  | checkpoint | All ductwork are installed and the joint are sealed with Emer duct sealant
checkpoint-status | 2e4b2fd5-fcf5-445a-97d3-86ccba0624c8 |  | checkpoint | All C clips installed
checkpoint-status | 5fb15a5f-e94b-4701-9d93-15af73d9ba5a |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 199208da-76f6-47a5-a1fc-3d579748a90a |  | checkpoint | Inspection Date
checkpoint-status | a04cf72b-b865-4a39-acd1-5ff3061a6cff |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | 228163ec-9b32-4498-9b7e-4248bc8d976e |  | checkpoint | Builder Representative Sign Off
checkpoint-status | 719cb7d5-e36c-4e6f-8a0d-94886c5cebc8 |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 23112642-a50d-48c1-9871-47040a421b88 |  | checklist | Variation (21/05/2020) |  |  |  |  | Yes | Variation (21/05/2020) | adb4d8a3-a2f0-4da9-a678-e0f5cee8faad
checkpoint-status | b6805669-8e0e-4d1b-8a93-4523de1037d1 |  | checkpoint | Variation Details Complete (Pass once inputted)
text | 520e525b-3b6e-5ec8-9087-4c2a5e584b08 |  | textbox | Variation Name
text | 4eb84de5-2019-5418-a637-65d2609085bb |  | textbox | Variation Description
text | d4631637-dbb3-56d0-b27a-46ea21c327ee |  | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
text | 9b677c71-3464-594a-bad1-c019bd5befc1 |  | textbox | Acknowledgement (Who requested the work to be done)
text | ca5338fe-44c7-507a-88a9-dc658e63eaff |  | textbox | Signature/Reference Mail (Who to send the variation too)
checkpoint-status | 8b58150d-bad8-4c47-b52f-0572c208b6f1 |  | checkpoint | Supporting Documentation (Attached or Referenced)
label | eae45edb-a250-5da9-acb8-c42d456bccd1 |  | note | Add Photos/Comments of variation work below
checkpoint-status | 122670ed-43c9-40ef-9f63-227ecf70b886 |  | checkpoint | Variation Sign-Off - Click to Add signatures below
button | b030c753-62e7-5619-9e5b-5a1af84e742f |  | button | Broad Air Representative Signature Added below | Yes, No
button | 40917a3e-036e-5dd4-9669-ec224af88a14 |  | button | Builder Representative Signature Added below | Yes, No
holdpoint | 3ff223a8-fe01-4fff-a272-a3868a8f35b3 |  | signoff | Click to Add Signatures of Wilson & Builder's Representative
checklist-flat | ac4d31e2-b95d-4e6e-8428-765e2c80c5f8 |  | checklist | Toolbox meeting |  |  |  |  | Yes | Toolbox meeting | cc1271b0-1d70-48e3-9d79-b67c11ae479e
checkpoint-status | db8c1b1b-d875-407f-ade2-ecfce1834bee |  | checkpoint | Toolbox meeting completed & Specific Document(s) attached
text | 6ceaddbb-9d63-5870-a90d-25594497c6ae |  | textbox | Date
text | 921d0275-6c49-57b4-855f-2e0235558e26 |  | textbox | Site Address
text | 7fdc3218-1b84-5cce-82d5-8ba3cbb46870 |  | textbox | Toolbox meeting topic
text | 0f2dbd44-831d-536e-82c5-edb12a7e4e77 |  | textbox | Toolbox Item 1 - (Add any resolutions below item)
text | 2012cced-b447-5cb6-8ef4-db7a40996a08 |  | textbox | Toolbox Item 2 - (Add any resolutions below item)
text | 3f900945-6e8d-5bf5-9233-ab45ca7cb48f |  | textbox | Toolbox Item 3 - (Add any resolutions below item)
text | 3f25c199-fbf0-52ea-81ae-541987689882 |  | textbox | Toolbox Item 4 - (Add any resolutions below item)
checkpoint-status | 06a37bda-1515-45c7-83f6-255a78f48ab5 |  | checkpoint | Toolbox meeting pdf attached (Add below)
label | 0d830e98-0fe6-5e96-8968-acaac1abf33f |  | note | Broad Air takes safety seriously and we encourage all persons representing the company to speak up if something is not right. If you find yourself unsure about something when it comes to safety, ASK! There is no such thing as a stupid question.
checkpoint-status | fcb3a254-79df-431f-9603-351038781c8c |  | checkpoint | Sign Off – By signing this page you acknowledge your attendance of this toolbox meeting and your co-operation with our policies & procedures
holdpoint | 5f6867d5-46f9-48bd-bcfc-976ef003f6a7 |  | signoff | Click to 'Add' signature's of each attendee
checklist-flat | 59e441c0-61e5-4a17-b7a7-9b90706df490 |  | checklist | Ventilation Checklist Commissioning [ J] |  |  |  |  | Yes | Ventilation Checklist Commissioning [ J] | d31e88e6-9503-435e-a4a4-347ba8becb06
checkpoint-status | fbcfbe91-f3c4-4361-a4ed-1604f27513d0 |  | checkpoint | Fan has been tested and is operational?
checkpoint-status | f3f4e4bb-3e3e-447c-9da1-b2d36c4777dd |  | checkpoint | Adequate flow has been achieved in bathroom 1?
checkpoint-status | f789d8d3-1880-4d04-b89b-1a31e1ae7808 |  | checkpoint | Adequate flow has been achieved in ensuite?
checkpoint-status | 39b32c97-0875-4b37-b7e4-4967e8590d11 |  | checkpoint | Adequate flow has been achieved in laundry?
checkpoint-status | 9a05f239-c3e6-433d-a6a8-b0ee220ef611 |  | checkpoint | Range hood has been tested and is operational?
checkpoint-status | 4f0967be-19d4-4db9-8a8c-ab6965b50e42 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 608c5bff-d163-4c1d-9c7d-aa2605d08165 |  | checkpoint | Inspection Date
checkpoint-status | bbd11e09-27fc-4ab8-a2d6-dbf0532e04c8 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | 62cdafb1-8ed5-41fb-8a5d-6fd4321c7651 |  | checkpoint | Builder Representative Sign Off
checkpoint-status | 8082d71a-4b52-4b5d-b733-c3ced543bbca |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | a30166e6-62c5-41f3-b331-6dfe449341f0 |  | checklist | Apartment Fit-Off Checklist [H] |  |  |  |  | Yes | Apartment Fit-Off Checklist [H] | d5052a1f-9247-46f6-8b70-39fb6f8b1bb4
checkpoint-status | 93e23a37-0a46-40eb-bb4f-dc2b09e7dbad |  | checkpoint | AC grille to living room installed with no defect
checkpoint-status | 42f07544-c2a4-443a-aa46-92baa91fab7d |  | checkpoint | Ensuite exhaust Fan installed with no defect
checkpoint-status | e6db795f-11a4-428b-8d3e-78a2a67a8042 |  | checkpoint | Toilet exhaust Fan installed with no defect
checkpoint-status | 297d2c66-5b32-42c7-af3d-7cb82cbe0740 |  | checkpoint | Range hood duct connected and taped to ensure air tight
checkpoint-status | 31a719be-315f-4f9a-8efb-209b99ab521d |  | checkpoint | AC Controller bracket installed as per RCP drawings
checkpoint-status | 5b3df55b-2325-4c1d-856f-b4ac0c9ae2b1 |  | checkpoint | Condensation drain is connected to Tundish point 10 mm air gap is provided at the connection point
checkpoint-status | 1485b7e1-26ec-4611-94ac-e247cd724f8e |  | checkpoint | Laundry exhaust Fan installed with no defect
checkpoint-status | 772c98b7-5c4b-445d-8c6d-2b6c174cac48 |  | checkpoint | Bedroom grilles installed
checkpoint-status | f29f20c3-386a-40b3-9b4e-1206cffc2b89 |  | checkpoint | Access panels placed as per drawings
checkpoint-status | 171de669-9161-469a-8017-6fe28242c0a4 |  | checkpoint | Condenser unit installed, refrigeration pipes are connected , all gaps to insulation is sealed and pipes are not kinked
checkpoint-status | 79ebc3cd-c67e-4f04-a0ca-815489414545 |  | checkpoint | "External louvers installed all gaps sealed between plenum box and wall/ louver flange to wall , photo evidence provided for below 1.Box sealed internally and the gap between the box and wall is sealed 2.Louver flanges sealed to the external box "
checkpoint-status | a1499e01-1c73-45d6-8de9-68e78b31f156 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 4bdeb266-f285-42cb-8912-aa4d5824913c |  | checkpoint | Inspection Date
checkpoint-status | 470a7fd6-d87e-4988-8d81-1da5e4fae879 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | 4dc290aa-96ed-42c1-8fd1-7c2f9a9a3683 |  | checkpoint | Builder Representative Sign Off
checkpoint-status | 0a73e5ab-d725-4455-b8d6-a482aba9de2c |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 9608b6a6-8864-4fd9-bf69-4053cd9d76b0 |  | checklist | Common Area Fit-Off Checklist [G] |  |  |  |  | Yes | Common Area Fit-Off Checklist [G] | d8b1ed11-220e-4b7e-a351-4ef3968d59d3
checkpoint-status | ed11a0b6-49c3-4820-ae21-069cd2897d29 |  | checkpoint | All grilles fitted
checkpoint-status | 31710fea-c397-4ae5-827d-85e315bbe3da |  | checkpoint | All VCD is installed and the motorised actuator is fitted of and wired
checkpoint-status | 22c47ea8-34f6-492e-ac4b-9a1e523eb0c4 |  | checkpoint | All relief grilles fitted (if applicable)
checkpoint-status | ac38b964-8543-4448-8b97-00bba052371f |  | checkpoint | Stair pressurisation grilles in the stair shaft fitted (if applicable)
checkpoint-status | 21fa2979-0f86-4e39-9928-76771bb2480f |  | checkpoint | All fire dampers provided with an access panel as per mechanical drawings (if applicable)
checkpoint-status | f003e336-ec8f-4535-b082-3043d9a2456b |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | 77733413-da90-47a3-888f-20b3cabcba4e |  | checkpoint | Inspection Date
checkpoint-status | 85e9abde-6f09-44d2-a19e-2ef759c189d0 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | c99808cf-941e-4fa0-9916-368c1069c669 |  | checkpoint | Builder Representative Sign Off
checkpoint-status | a443a4c5-2d8d-456e-bd0e-9f044c1704b0 |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist-sectioned | aef8d9ff-b316-473b-ba31-2e0ceef0e68d |  | checklist | Incident Report - Checklist |  |  |  |  | Yes | Incident Report - Checklist | dd7ce894-4d46-48c1-99ef-e989d66d76b7
checkpoint-group | c497c7b8-0bb3-4f14-8e33-ed318dad2c20 |  | section | Injured Workers Details
checkpoint-status | 89142f8a-8a5f-41d0-8317-88d82f80ee56 |  | checkpoint | Injured Worker
text | acad42bb-9c21-593a-b1ff-ae6c3bc80eee |  | textbox | Name of Employer of injured Person(s) (If any):
text | 1b215938-9368-5dde-83b7-e716814bb65d |  | textbox | Business address of Person/Organisation in charge of the equipment:
text | e558d9f9-1243-5ceb-a762-a457bb79067a |  | textbox | Full name of Employee:
text | 19c7c93a-5bdd-55f0-9bf3-345c51329643 |  | textbox | Date of Birth:
select | 9a158fe4-cf28-53e6-9afa-e1856f2a4e7f |  | dropdown | Sex: | Female, Male
text | ca2d8b09-d96f-5eeb-acc3-07cabf55f8cd |  | textbox | Residential address and telephone number (if known):
text | 40850f22-dbeb-5dd9-8db8-f23016c074ac |  | textbox | Occupation of Employee:
checkpoint-group | 253c0248-017a-4217-aecd-9f54acde46e1 |  | section | Incident Details
checkpoint-status | 08d892af-7976-43a2-ba6c-2726119ac302 |  | checkpoint | Incident
text | f2bda1d4-0761-5b6a-9e0f-482eb3dd48ee |  | textbox | Date of Birth:
text | 10ee8fc1-04b2-54db-bd0b-8d27f7b16045 |  | textbox | Place/Location where incident occurred:
text | a46229dd-40e1-5192-b3ad-92e23d370b58 |  | textbox | Work/activity being performed at time of incident and equipment being used:
text | 7683680c-6aab-507f-a3a5-ab763c8c65c5 |  | textbox | Brief description of incident:
text | 11ccf358-ad77-526d-9d59-be1605162fab |  | textbox | Treatment given/action taken at the time of the incident: (Attach Statements below)
text | f452d178-18d9-5b2d-8740-6b10e604a7e0 |  | textbox | Name of Witnesses or Name of Person(s) who first attended the scene: (Attach Statements below)
text | 119f1593-44ee-5308-baaf-db44bf6de5cc |  | textbox | Action taken/intended, if any, to prevent recurrence of the incident:
label | 2bd0d46c-829c-5d31-84c0-731684d6b6ed |  | note | Add diagram or picture of incident below
checkpoint-group | 34823282-53bd-45fe-a93d-ed2c0cf6be03 |  | section | Treatment Details
checkpoint-status | 7b9f20e2-7a9e-4cac-bf96-cfb8f687c6a8 |  | checkpoint | Details
button | 845fa44a-b47e-5bf7-9f61-36349a57e3bc |  | button | Did the injury necessitate loss of time? | No, Yes
label | ecd64058-aa2f-52f0-a894-35083d0e48a2 |  | note | If "Yes" selected
text | 45f8443e-6d68-51eb-840f-fda2161f281f |  | textbox | Name the clinic/medical centre attended:
label | b5cd9fe9-284f-5175-b52f-881cfb048d76 |  | note | Attach WorkCover Certificate of Capacity (Attach below)
button | 0104f33b-f27d-5da6-b530-acac84832a3b |  | button | Was an ambulance required? | No, Yes
button | 6a34c938-1f8b-5363-9e90-b1fd440db76f |  | button | Was the incident reported to WorkSafe Victoria? | No, Yes
label | ad3242c9-12b5-5525-97fe-de138f31e9c4 |  | note | If "Yes" selected
text | 880a90cb-6de4-54e1-b751-a0866cccc062 |  | textbox | WorkSafe Incident notification number is:
checkpoint-group | 9a51c868-8728-477b-9378-ecfec5c1e51b |  | section | Form Details
checkpoint-status | f144a56d-8cc4-4f70-8e38-382e3f4624a2 |  | checkpoint | Details of Person submitting this form
text | d8325cab-7b3f-5126-8bf5-5e26dda314f4 |  | textbox | Name:
text | cd743af7-6219-5a7c-894e-9e23df3295aa |  | textbox | Position/Title:
text | 366363f1-ca07-5dbc-8c95-95d4f8998eee |  | textbox | Date:
select | 89f63078-f98f-5796-8764-73f49f82376a |  | dropdown | Type of Injury (Filled out by OHS Manager): | LTI, MTI, FAI
checklist-flat | 2c25b67e-2134-4299-bfe7-7050db032a02 |  | checklist | Access Panel 1 Rough In [D] |  |  |  |  | Yes | Access Panel 1 Rough In [D] | e7d3c0d6-0d60-41f5-b8f3-1354d4853433
checkpoint-status | e7b9575d-5875-4939-b065-fbf7c264dd74 |  | checkpoint | Access Panel location has been marked on floor as per RCP
checkpoint-status | 1ed010b8-f5d8-4388-befb-166d380213bb |  | checkpoint | Access panel location allows sufficient access equipment
checkpoint-status | 57434c39-84cd-4979-bfe1-5792cc1c6e1a |  | checkpoint | All other other services do not impede access
checkpoint-status | 6c8a5b8a-1259-4d4f-88fd-0b472525806f |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
checkpoint-status | b81864b7-d1d0-45ab-93e6-1d7b656f3716 |  | checkpoint | Contract/Subcontractor Assessor Sign Off
checkpoint-status | 3ba89e91-fde3-40c4-a638-04ecabffdd56 |  | checkpoint | Builder Representative Sign Off
checkpoint-status | 8c9c6e4d-6047-49a8-8f71-f7c0d2fdf9a0 |  | checkpoint | Request Sign-Off(s) + Click to Add Signature(s)
text | 72216b5d-f979-5c77-a7d0-17bce9d7e67f |  | textbox | Inspection Date: