## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | Ventilation Checklist 1 Rough In [C]
checkpoint | Is the installation area unobstructed?
checkpoint | Fans installed within ceiling areas are in the correct location as per Mechanical Drawings
checkpoint | Fans Installed correctly with rubber isolation pads
checkpoint | All Flex has been run to correct location
checkpoint | All flex are hung independent of other services and supported by intact load spreaders
checkpoint | Butterfly dampers are installed on the PODs grille neck and they are in a fully opened position and air tight sealed
checklist-flat | Access Panel 1 Rough In [D]
checkpoint | Access Panel location has been marked on floor as per RCP
checkpoint | Access panel location allows sufficient access equipment
checkpoint | All other other services do not impede access
checklist-flat | Duct Installation Checklist [F]
checkpoint | Is the installation area unobstructed?
checkpoint | Are drawings on site the latest issue
checkpoint | Are plant and equipment location correct
checkpoint | Duct size and location correct
checkpoint | Material and gauge correct
checkpoint | Is correct support method being used - Risers are supported at each level.
checkpoint | Is correct jointing method being used
checkpoint | Are joints completed and cleated installed on flanges
checkpoint | Is correct joint sealant being used
checkpoint | Are fire dampers installed and break away joint complete
checkpoint | Are canvas connections to equipment sealed and aligned
checkpoint | Is ductwork fire rating complete
checkpoint | Are all spigots installed and dampers fully open
checkpoint | Are all access panels for fire damper access installed and closed
checkpoint | Are the correct fixings used for fan installation?
checkpoint | Is the fan secured correctly to hanging equipment?
checkpoint | Is the hanging equipment correctly installed and secured?
checkpoint | Is the ductwork connected to the fan as specified in workshop drawings?
checkpoint | Are the cables connected as per electrical drawings and manufacturer's specifications?
checkpoint | Is ductwork installation complete
checklist-flat | Sign Off
checkpoint | Sign-Off Completed as per below (Pass once complete)
textbox | Inspection Date:
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | Base Building Fit-Off Checklist [G]
checkpoint | Supply grilles fitted
checkpoint | VCD is installed
checkpoint | Exhaust grilles fitted
checkpoint | All fire dampers provided with an access panel as per mechanical drawings
checklist-flat | Apartment Fit-Off Checklist [H]
checkpoint | Ensuite exhaust grilles installed
checkpoint | Toilet exhaust grilles installed
checkpoint | Range hood duct connected and taped to ensure air tight
checkpoint | Access panels placed as per drawings
checkpoint | External louvers installed all gaps sealed between plenum box and wall/ louver flange to wall, photo evidence provided for below
label | 1. Box sealed internally and the gap between the box and wall is sealed
label | 2. Louver flanges sealed to the external box
checklist-flat | Ventilation Checklist Commissioning [J]
checkpoint | Fan has been tested and is operational?
checkpoint | Adequate flow has been achieved in areas the fan is serving to?
checkpoint | Does the fan interlocking working correctly with lights?
checkpoint | Range hood has been tested and is operational?
checkpoint | Provide evidence of airflow reading
checkpoint | Visual Survey
checklist-flat | Fire Damper Checklist - Intumecent FD [K]
checkpoint | Fire damper is mechanically fixed to the casing with min 1 screw per side and min 200mm spacing betwwen screws
checkpoint | Penetration details have been captured
checkpoint | Gaps between the fire damper and wall no greater than 25mm and is filled with Killargo Intumescent Sealant with no cracking visible
checkpoint | Killargo fire rated mastic has been applied to entire perimeter of fire damper cell on both sides. No evidence of cracking.
checkpoint | Casing perimeter is sealed with Killargo intumescent sealant. No evidence of cracking.
checkpoint | Sheet metal thickness is 0.7mm or greater.
checkpoint | Ductwork is connected to either side of the casing with nylon bolts on the flanges as per the AS1682.2 break away joint method. Bolts do not exceed an 8mm diameter.
checkpoint | Access panel is provided to conveniently access fire damper for visual and/or maintenance inspections.
checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
checkpoint | Pictures attached
checkpoint | Signature (Contract/Subcontractor Assessor)
checkpoint | Signature (Builder Representative)
checkpoint | Pictures/Comments attached below
textbox | Notes/Additional Comments
checklist-flat | Flatpack Installation Checklist [O]
checkpoint | Flatpack duct is installed as per approved mechanical shop drawings
checkpoint | Internal side of flatpack duct and fittings are clear from debris and dust
checkpoint | Is flatpack supported from ceiling using metal hangers or metal support clips at every 2m intervals so that the flatpacks are not sagging?
checkpoint | Wherever the flatpacks are screwed into, ensure properly sealed
checkpoint | Flatpack joints & fittings are properly sealed.
checkpoint | Are correct type of fittings used?
checkpoint | Visual inspection