## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Water Reticuation | itp |  |  |  |  | ITP - Water Reticuation
section | Preconstruction
checkpoint | Precondition Survey
label | SPECIFICATION REFERENCE: Water Specification B.2.11.2.2
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Prior to starting on site.
label | ○ Survey conducted of all surfaces and the exterior of buldings on or adjacent to the boundaries of the site and of other property that might potentially be affected by the works.
label | ACCEPTANCE CRITERIA: Survey documents submitted to Engineer.
checkpoint | Materials Quality
label | SPECIFICATION REFERENCE: FNDC Approved Materials List - Water Services
label | TEST/TASK REQUIRED: Visual check for approved materials, quality and condition.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On arrival to site, prior to using materials.
label | ACCEPTANCE CRITERIA: Materials meet specifications or otherwise approved by Engineer.
label | ○ Delivery dockets.
label | ○ Photos.
checkpoint | Survey Setout
label | SPECIFICATION REFERENCE: Water Specification B.2.11.2.4
label | TEST/TASK REQUIRED: Survey set out.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Prior to commencing each stage of work.
label | ○ Engineer to be notified if any concerns
label | ACCEPTANCE CRITERIA: Survey set out as per IFC drawings.
checkpoint | Service Location
label | SPECIFICATION REFERENCE: Water Specification B.2.11.4.2
label | TEST/TASK REQUIRED: Locate underground services within work area.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Locate, pothole and protect existing services. Pothole information shall be used to confirm fittings required to connect to the existing services.
label | ACCEPTANCE CRITERIA:
section | Installation
checkpoint | Material Properties (Bedding)
label | SPECIFICATION REFERENCE: Water Specification B.5.5.1.13
label | TEST/TASK REQUIRED: GAP20 grading curve to be submitted to Engineer for approval
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Prior to using bedding material on site.
label | ○ PE bedding, pipe surround and haunching shall be GAP20 in accordance with AS/NZS 2566.
label | ACCEPTANCE CRITERIA: Bedding grading curve accepted by Engineer.
checkpoint | Material Properties (Subbase)
label | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
label | TEST/TASK REQUIRED: Subbase material meets FNDC Engineering Standards
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Prior to using subbase material on site.
label | ACCEPTANCE CRITERIA: Subbase material test certificates accepted by Engineer.
checkpoint | Material Properties (Basecourse)
label | SPECIFICATION REFERENCE: FNDC Engineering Standards 3.3.2
label | TEST/TASK REQUIRED: Basecourse material meets FNDC Engineering Standards
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Prior to using basecourse material on site.
label | ACCEPTANCE CRITERIA: Basecourse material test certificates accepted by Engineer.
checkpoint | Pipe
label | SPECIFICATION REFERENCE: Water Specification B.5.8.3
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Visual inspection prior to use (clean and free from defects).
label | ACCEPTANCE CRITERIA: Photographs.
checkpoint | Test Welds (Butt Welding)
label | SPECIFICATION REFERENCE: Water Specification B.5.10.2.2
label | TEST/TASK REQUIRED: Laboratory testing
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Three butt welded joints and one section of virgin pipe shall be tested in accordance with ISO 13953.
label | ○ One test weld for every 10 lengths of pipe laid.
label | ACCEPTANCE CRITERIA: Weld test results submitted to Engineer.
checkpoint | Welded Joints (Butt Welding)
label | SPECIFICATION REFERENCE: Water Specification B.5.10.2.1
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of each butt weld.
label | ○ Weld inspection checklist.
label | ○ Weld data log.
label | ACCEPTANCE CRITERIA: Weld inspection checklist submitted for each butt weld.
label | ○ Weld data log submitted for each weld.
checkpoint | Welded Joints (EF Welding)
label | SPECIFICATION REFERENCE: Water Specification B.5.10.2.1
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of each EF weld.
label | ○ Weld inspection checklist.
label | ACCEPTANCE CRITERIA: Weld inspection checklist submitted for each EF weld.
checkpoint | Pipeline Installation (PE)
label | SPECIFICATION REFERENCE: Water Specification B.6.4.5 and B.6.4.6
label | TEST/TASK REQUIRED: Visual inspection
label | ○ Pipeline installed to correct alignment, grade and level
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of installation of each length of pipe, prior to backfilling.
label | ○ Horizontal alignment tolerance + 100mm.
label | ○ Vertical alignment tolerance + 100mm.
label | ○ Valves on centreline of pipe permissible vertical deviation of +50mm.
label | ACCEPTANCE CRITERIA: As-built drawings.
label | ○ Photographs.
label | ○ Changes to horizontal or vertical alignment to be agreed with Engineer pror
checkpoint | Valve Installation (including Chambers if required)
label | SPECIFICATION REFERENCE: Water Specification B.5.8.4 and B.5.9
label | ○ FNDC Engineering Standards 6.2.8
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Installed as per specifications.
label | ACCEPTANCE CRITERIA: Photographs.
label | ○ As-built drawings.
checkpoint | Valve Boxes and Markings
label | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.8.5, and Sheet 48
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of installation.
label | ○ Valve marker posts and kerb markings as per FNDC standard.
label | ACCEPTANCE CRITERIA: Photographs.
checkpoint | Hydrants
label | SPECIFICATION REFERENCE: Water Specifcation B.5.8.4
label | ○ FNDC Engineering Standards 6.2.9.1
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Installed as per specificationsand IFC drawings.
label | ACCEPTANCE CRITERIA: Photographs.
label | ○ As-built drawings.
checkpoint | Hydrant Boxes and Markings
label | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.9.3, and Sheet 48
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of installation.
label | ○ Hydrant marker posts and kerb markings as per FNDC standard.
label | ACCEPTANCE CRITERIA: Photographs.
checkpoint | Air Release Valves
label | SPECIFICATION REFERENCE: Water Specifcation B.5.5.1.11
label | ○ FNDC Engineering Standards Sheet 51
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of installation.
label | ○ Air valves installed to specification
label | ACCEPTANCE CRITERIA: Photographs.
label | ○ As-built drawings.
checkpoint | Thrust Blocks
label | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.2.3.8, and Sheet 50
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of the thrust block installation, prior to backfilling.
label | ACCEPTANCE CRITERIA: Photographs.
checkpoint | Pipe Bedding
label | SPECIFICATION REFERENCE: Water Specification B.3.4.1
label | ○ FNDC Engineering Standards Sheet 31
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Bedding installed as per specifications.
label | ACCEPTANCE CRITERIA: Photographs.
checkpoint | Pipe Backfill (Outside of Carriageway)
label | SPECIFICATION REFERENCE: Water Specification B.3.3.2
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of backfill.
label | ○ Trench backfilled with original sound material from the trench.
label | ACCEPTANCE CRITERIA: Photographs.
checkpoint | Subbase
label | SPECIFICATION REFERENCE: Water Specification B.3.5.2
label | ○ FNDC Engineering Standards 3.3.3.3 and Sheet 31
label | TEST/TASK REQUIRED: Visual inspection
label | ○ NDM testing
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of subbase layer, prior to installing basecourse.
label | ○ Backfill and compaction completed as per specifications.
label | ACCEPTANCE CRITERIA: Compaction records.
label | ○ Photographs.
checkpoint | Basecourse
label | SPECIFICATION REFERENCE: Water Specification B.3.5.2
label | ○ FNDC Engineering Standards 3.3.3.4 and Sheet 31
label | TEST/TASK REQUIRED: Visual inspection
label | ○ NDM testing
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : NDM testing on completion of basecourse layer, prior to sealing.
label | ○ Basecourse installed as per FNDC Engineering Standards, and NZTA B/02.
label | ACCEPTANCE CRITERIA: Compaction records.
label | ○ Photographs.
holdpoint | HOLD POINT
checkpoint | Detection Tape and Tracer Wire
label | SPECIFICATION REFERENCE: Water Specification B.5.5.1.6
label | ○ FNDC Engineering Standards 6.3.2.4 and Sheet 31
label | TEST/TASK REQUIRED: Visual inspection and electrical continuity testing
label | INSPECTION BY:
label | TASK TIMING OR TASK FREQUENCY : On completion of installation.
label | ○ A blue metallic detection tape labelled 'Water' shall be laid directly above all new non-metallic watermains.
label | ○ Tracer cable (2.5mm²) shall be attached to pipe wall at maximum 3.0m intervals.
label | ACCEPTANCE CRITERIA: Electrical continuity test results provided to Engineer.
checkpoint | Pressure Testing of Pipes
label | SPECIFICATION REFERENCE: Water Specification B.5.10.1
label | ○ FNDC Engineering Standards 6.3.3.2
label | TEST/TASK REQUIRED: Pressure test of PE pipeline
label | INSPECTION BY: UCCL, FNDC,
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : On completion of installation of PE pipeline, after sufficent backfill has been placed to prevent movement.
label | ○ Pressure test as per FNDC Engineering Standard.
label | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
holdpoint | HOLD POINT
checkpoint | Flushing and Disinfection
label | SPECIFICATION REFERENCE: Water Specifcation B.5.12.3
label | ○ FNDC Engineering Standards 6.3.4
label | TEST/TASK REQUIRED: Visual inspection (flushing)
label | ○ Chlorination and testing
label | INSPECTION BY: UCCL, FNDC,
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : On completion of pressure test, prior to connection.
label | ○ Flushing and chlorination/testing completed as per specifications. Results meet FNDC specification.
label | ACCEPTANCE CRITERIA: Test results provided to Engineer for approval prior to connection.
holdpoint | HOLD POINT
checkpoint | Connection to Existing Watermains
label | SPECIFICATION REFERENCE: Water Specification B.5.12.4
label | ○ FNDC Engineering Standards 6.3.5
label | TEST/TASK REQUIRED: Watermain connection
label | INSPECTION BY: UCCL, FNDC,
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Connection to be completed after instruction from Engineer.
label | ○ Note from FNDC Engineering Standard - "Only the FNDC's Reticulation Maintenance Contractor may undertake the connection".
label | ACCEPTANCE CRITERIA: Photographs.
holdpoint | HOLD POINT
checkpoint | Service Connections
label | SPECIFICATION REFERENCE: FNDC Engineering Standards 6.3.2.2 and Sheet 46
label | TEST/TASK REQUIRED: Water connection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Connection to be completed after instruction from Engineer.
label | ACCEPTANCE CRITERIA: Photographs.
label | ○ As-built drawings.
checkpoint | Reinstate Driveways
label | SPECIFICATION REFERENCE: Water Specification B.3.7.6
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
label | ○ Driveways reinstated in the same material and to the same standard as existing prior to works.
label | ACCEPTANCE CRITERIA: Photographs.
checkpoint | Reinstate Footpaths
label | SPECIFICATION REFERENCE: Water Specification B.3.7.6
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of wastewater installation.
label | ○ Footpaths reinstated in the same material and dimensions but constructed to FNDC Footpath Standards.
label | ACCEPTANCE CRITERIA: Concrete dockets.
label | ○ Photographs.
checkpoint | Reinstate Kerb and Channel
label | SPECIFICATION REFERENCE: Water Specification B.3.7.6
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Replacement kerb and channel profiles match line and level of existing kerb and channel.
label | ○ Concrete has minimum 28-day strength of 25MPa.
label | ACCEPTANCE CRITERIA: Photographs.
checkpoint | Concrete Pour (Stuctural - Pipe Bridge Footings, Commercial Driveways)
label | SPECIFICATION REFERENCE: Water Specification B.4.4.2
label | TEST/TASK REQUIRED: Prepour inspection
label | INSPECTION BY: UCCL
label | ○ Haigh Workman
label | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
label | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
label | ○ Concrete dockets.
label | ○ Photographs.
checkpoint | Concrete Pour (Non-Structural - Footpaths, Residential Driveways)
label | SPECIFICATION REFERENCE: FNDC Engineering Standards Sheets 12, 17 and 18
label | TEST/TASK REQUIRED: Visual inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Prior to pouring concrete.
label | ACCEPTANCE CRITERIA: Pre-pour inspection checklist.
label | ○ Concrete dockets.
label | ○ Photographs.
checkpoint | Asphaltic Concrete Layer (DG10)
label | SPECIFICATION REFERENCE: NZTA M10 Specification
label | TEST/TASK REQUIRED: As per NZTA M10 Specification
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : On completion of the pavement surface.
label | ACCEPTANCE CRITERIA: Test results submitted to Engineer.
label | ○ Photographs.
checkpoint | Grout Filling of Redundant Watermains
label | SPECIFICATION REFERENCE: Water Supply Drawings Notes, No. 20.1 and 20.2
label | TEST/TASK REQUIRED: Redundant watermains to be grout filled and remain in place.
label | ○ Remove redundant valve boxes, signs etc.
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Grout filling on completion of new pipelines.
label | ACCEPTANCE CRITERIA: Grouting record.
label | ○ Photographs.
section | Post Construction
checkpoint | As-Built Drawings
label | SPECIFICATION REFERENCE: Water Specifcation B.2.18.1
label | TEST/TASK REQUIRED: As-built drawings meet FNDC specification
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : Draft as-builts shall be complete and accepted by Engineer prior to Practical Completion.
label | ○ Final as-builts issued prior to Final Completion.
label | ACCEPTANCE CRITERIA: As-buiilts submitted to the Engineer for approval.
checkpoint | RAMM Information
label | SPECIFICATION REFERENCE: Water Specification B.2.18.2
label | TEST/TASK REQUIRED: RAMM information
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY : RAMM information submitted to the Engineer on completion of works.
label | ACCEPTANCE CRITERIA: RAMM information submitted to the Engineer.