## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP For Hydrant & Hose Reel #1 | itp |  |  |  |  | ITP For Hydrant & Hose Reel #1
section | Hydrants
checkpoint | Pipework installed as per approved workshop drawing
checkpoint | Correct pipe sizes as per drawing
checkpoint | Pipework supports to AS 2419.1
checkpoint | Fire stair clearance 1000mm maintained
checkpoint | All hydrant valve centrelines installed between 750-1200mm above the floor
checkpoint | All hydrant valve outlets installed horizontal or not more than 35deg below
checkpoint | All hydrant valves achieve 100mm clearance for hand wheel
checkpoint | All hydrant valves achieve 300mm orbital clearance in front of the nozzle
checkpoint | All hydrant valves oriented towards adjacent fire door
checkpoint | All hydrant isolation valves installed within plant rooms or fire stairs
checkpoint | 150mm liquid filled dial gauge at booster valves if pump in installed in series (relay)
checkpoint | Engraved warning label installed if pump is installed in series (relay)
checkpoint | Pressure gauge installed at hydraulically most disadvantaged fire hydrant
checkpoint | Maintenance tags and storz hydrant and caps installed at each hydrant valve
checkpoint | Number tags installed at each hydrant isolation valve and reflected on block plan
checkpoint | Sleeves and fire stop material to penetrations (where specified)
checkpoint | Correct boost pressure and test pressure labels installed at booster location
checkpoint | All hydrant valves tested for operation
section | Hydrostatic Pressure Test For Hydrants
checkpoint | Pressurise to 1700 kPa or 1.5 times highest pressure at that location for minimum of 2 hours
textbox | Start Pressure |  |  | kPa
textbox | Time
textbox | Client Initials
textbox | DA Initials
label
textbox | Finish Pressure |  |  | kPa
textbox | Time
textbox | Client Initials
textbox | DA Initials
section | Hose Reels
checkpoint | Hose Reel isolation valve installed 1 metre above ground
checkpoint | Hose Reels achieve 100mm clearance all around the drum
checkpoint | Maintenance tags and labels installed at each hose reel
checkpoint | All Hose Reel nozzles interlocked
checkpoint | All Hose Reels tested for operation
checkpoint | Block Plan installed
checkpoint | All isolation valves strapped and locked
checkpoint | Isolation valves tags installed for each valve and reflected on the block plan
section | Hydrostatic Pressure Test for Hose Reels
checkpoint | Pressurise to 1400 kPa for a minimum of 2 hours
textbox | Start Pressure |  |  | kPa
textbox | Time
textbox | Client Initials
textbox | DA Initials
label
textbox | Finish Pressure |  |  | kPa
textbox | Time
textbox | Client Initials
textbox | DA Initials