## General
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - SILVERSTREAM | [5 empty] | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561482 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council | [5 empty] | B | Report by Breach | CM | Construction Manager | Stephen Vorgers
Contract Number: | DCC11014-WPS002 | [5 empty] | C | Check | CR | Cust. Representative | Joff Riley / Mark Todd
Area/ Sub-System: | Pipework Installation - Silverstream |  |  | Lot ID Number: | N/A |  | D | Dimension Inspection | IP | Inspection Personnel | Aaron Sutherland
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | 561482-ITP-006.3 |  |  | Version: | Draft |  | H | Hold Point | OP | Operations Manager
ITP Description: | Pipework Installation Pump 3 - Inspection Test Plan | [5 empty] | I | Inspection | PM | Project Manager | Matt Paterson
Discipline: | Stainless Steel Pipework - Installation | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [5 empty] | O | Operation | QE | Quality Engineer
[7 empty] | R | Review | QM | QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Silverstream Pump Station Project Ref: 12581908-GHD-PS-SS-DRG-GN Drawings: G0001, M0001 to M0004 & P0001 | [5 empty] | S | Subcontractor | SP | Supervisor | Bruce Allan
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Matt Paterson |  |  | Date: | 2024-12-10 |  | W | Witness Point | SV | Surveyor
Quality Specified: | None - As per Specification requirements | [7 empty] | WS | Welding Supervisor | Matt York
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Bruce Allan |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Paterson/Stephen Vorgers |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: | Joff Riley / Bruce Buxton |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Stainless Steel Pipe components | Obtain the mill certificates for the materials used - 316L Stainless Steel | Documents from the supplier/Manufacturer | Mill Certificates & Welding certificates | Once | Documentation | C | IP
3.2 | Stainless Steel Pipe components | Take delivery of components from Supplier. Verify all components have been delivered | Quantities as shown on the drawings | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | Once | Visual | C | IP
3.3 | Stainless Steel Pipe components | Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions | Dimensions & orientation as shown on the drawings | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | Once | Visual Dimension Inspection | D | IP
3.4 | Valves & Ancillaries | Check and verify that the Manufacturer & Type is approved for use by the client | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP
3.5 | Dress Sets (gaskets & fasteners) | Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1 | Install gasket, bolts & nuts and tighten. Torque fasteners | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each flange | Record & attach to ITP | Inspection | IP
4.2 | Fasten Dry Well side from spool (cast in wall) Item # 2 | Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Flange | Record & attach to ITP | Inspection | IP
4.3 | Isolation Valve 150mm Item # 3 (suction side) | Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record & attach to ITP | Inspection | IP
4.4 | 150mm Dismantling joint (suction side) Item#4 | Torque fasteners to relevant water standards | Use diametrically opposed touque sequence and manufactruers instructions | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record & attach to ITP | Inspection | IP
4.5 | 150mm Flange Adaptor Spool. Item # 5 | Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record & attach to ITP | Inspection | IP
4.6 | 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6 | Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record & attach to ITP | Inspection | IP
4.7 | 150mm swing check valve. Item # 7 | Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record & attach to ITP | Inspection | IP
4.8 | 150mm Sweeping Spool (discharge). Item # 8 | Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record & attach to ITP | Inspection | IP
4.9 | 150mm Dismantling joint (discharge side) Item#4 | Torque fasteners to relevant water standards | Use diametrically opposed touque sequence and manufactruers instructions | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record & attach to ITP | Inspection | IP
4.10 | Isolation Valve 150mm Item # 3 (discharge side) | Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record & attach to ITP | Inspection | IP
4.11 | Pipework bracketing installed and is secure. | At completion of pipework | Pipework complete and installed. Adjustable brackets | As indicated on the drawings | once | Visual | I | IP

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Final inspection to installed pipework | At completion of pipework | Flanges are straight and bolts tightened all threads sealed and leak free | As per drawings | once | Visual | I | IP
5.2 | Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage | At completion of pipework | Pipework is installed and correct fittings installed to accept the instrumentation | As per drawing schematics | once | Visual | I | IP
5.3 | Pipework bracketing installed and is secure. | At completion of pipework | Pipework complete and installed | As per drawings | once | Visual | I | IP
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: