## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2 | itp |  |  |  |  | 561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 2
label | Inspection Point: Quality Control Activity - Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm
label | Acceptance Criteria - Completion of the assebmly to pump and motor 2 including mounting to the plinth.
label | Verifying Document - Downer 561482-ITP-004.2
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
label | Inspection: Key - QE
label | Inspection: By - D / E
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 2
label | Inspection Point: Quality Control Activity - Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment
label | Acceptance Criteria - Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm
label | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
label | Inspection: Key - QE
label | Inspection: By - D / E
checkpoint | 4.2 - Install drive coupling to Pump 2
label | Inspection Point: Quality Control Activity - Completion of the nstallation of shaft drive coupling - Pump 2
label | Acceptance Criteria - Completion of Item 4.1
label | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - A / I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 2 & Motor assembly
label | Inspection Point: Quality Control Activity - Final inspection & check. Rotate motor/pump assembly by hand to esnure smooth operation
label | Acceptance Criteria - Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed
label | Verifying Document - As per methodology, Shaft lignment verification & Manufacturers Instructions.
label | ○ Detailed report provided from specialist - Wallace Murray Electrical
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3 | itp |  |  |  |  | 561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 3
label | Inspection Point: Quality Control Activity - Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm
label | Acceptance Criteria - Completion of the assebmly to pump and motor 3 including mounting to the plinth.
label | Verifying Document - Downer 561482-ITP-004.3
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
label | Inspection: Key - QE
label | Inspection: By - D / E
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 3
label | Inspection Point: Quality Control Activity - Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment
label | Acceptance Criteria - Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm
label | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
label | Inspection: Key - QE
label | Inspection: By - D / E
checkpoint | 4.2 - Install drive coupling to Pump 3
label | Inspection Point: Quality Control Activity - Completion of the nstallation of shaft drive coupling - Pump 3
label | Acceptance Criteria - Completion of Item 4.1
label | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - A / I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 3 & Motor assembly
label | Inspection Point: Quality Control Activity - Final inspection & check. Rotate motor/pump assembly by hand to esnure smooth operation
label | Acceptance Criteria - Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed
label | Verifying Document - As per methodology, Shaft lignment verification & Manufacturers Instructions.
label | ○ Detailed report provided from specialist - Wallace Murray Electrical
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-006.1 - Pipe & Fitting Installation Pump 1 | itp |  |  |  |  | 561482-ITP-006.1 - Pipe & Fitting Installation Pump 1
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
label | Acceptance Criteria - Documents from the supplier/Manufacturer
label | Verifying Document - Mill Certificates & Welding certificates
label | Frequency - Once
label | Inspection Type (Visual, other) - Documentation
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
label | Acceptance Criteria - Quantities as shown on the drawings
label | Verifying Document - Drawing M0001
label | ○ Drawing M0002
label | ○ Drawing M0003
label | ○ Drawing M0004
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
label | Acceptance Criteria - Dimensions & orientation as shown on the drawings
label | Verifying Document - Drawing M0001
label | ○ Drawing M0002
label | ○ Drawing M0003
label | ○ Drawing M0004
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual Dimension Inspection
label | Inspection: Key - D
label | Inspection: By - IP
checkpoint | 3.4 - Valves & Ancillaries (Blanking Flange)
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
label | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each flange
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Flange
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.3 - Blanking Flange150mm (suction side)
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australian Water Standards Guidelines - 80N.m
label | Frequency - Each Side of Valve
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.3 - Blanking Flange150mm (Discharge side)
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australian Water Standards Guidelines - 80N.m
label | Frequency - Each Side of Valve
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Final inspection to installed pipework
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
label | Verifying Document - As per drawings
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-006.2 - Pipe & Fitting Installation Pump 2 | itp |  |  |  |  | 561482-ITP-006.2 - Pipe & Fitting Installation Pump 2
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
label | Acceptance Criteria - Documents from the supplier/Manufacturer
label | Verifying Document - Mill Certificates & Welding certificates
label | Frequency - Once
label | Inspection Type (Visual, other) - Documentation
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
label | Acceptance Criteria - Quantities as shown on the drawings
label | Verifying Document - Drawing M0001
label | ○ Drawing M0002
label | ○ Drawing M0003
label | ○ Drawing M0004
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
label | Acceptance Criteria - Dimensions & orientation as shown on the drawings
label | Verifying Document - Drawing M0001
label | ○ Drawing M0002
label | ○ Drawing M0003
label | ○ Drawing M0004
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual Dimension Inspection
label | Inspection: Key - D
label | Inspection: By - IP
checkpoint | 3.4 - Valves & Ancillaries
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
label | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each flange
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Flange
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.3 - Isolation Valve 150mm Item # 3 (suction side)
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Side of Valve
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.4 - 150mm Dismantling joint (suction side) Item#4
label | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.5 - 150mm Flange Adaptor Spool. Item # 5
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.6 - 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.7 - 150mm swing check valve. Item # 7
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Side of Valve
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.8 - 150mm Sweeping Spool (discharge). Item # 8
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.9 - 150mm Dismantling joint (discharge side) Item#4
label | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.10 - Isolation Valve 150mm Item # 3 (discharge side)
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Side of Valve
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.11 - Pipework bracketing installed and is secure.
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Pipework complete and installed. Adjustable brackets
label | Verifying Document - As indicated on the drawings
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Final inspection to installed pipework
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
label | Verifying Document - As per drawings
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Pipework is installed and correct fittings installed to accept the instrumentation
label | Verifying Document - As per drawing schematics
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.3 - Pipework bracketing installed and is secure.
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Pipework complete and installed
label | Verifying Document - As per drawings
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-006.3 - Pipe & Fitting Installation Pump 3 | itp |  |  |  |  | 561482-ITP-006.3 - Pipe & Fitting Installation Pump 3
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
label | Acceptance Criteria - Documents from the supplier/Manufacturer
label | Verifying Document - Mill Certificates & Welding certificates
label | Frequency - Once
label | Inspection Type (Visual, other) - Documentation
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
label | Acceptance Criteria - Quantities as shown on the drawings
label | Verifying Document - Drawing M0001
label | ○ Drawing M0002
label | ○ Drawing M0003
label | ○ Drawing M0004
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Stainless Steel Pipe components
label | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
label | Acceptance Criteria - Dimensions & orientation as shown on the drawings
label | Verifying Document - Drawing M0001
label | ○ Drawing M0002
label | ○ Drawing M0003
label | ○ Drawing M0004
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual Dimension Inspection
label | Inspection: Key - D
label | Inspection: By - IP
checkpoint | 3.4 - Valves & Ancillaries
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
label | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each flange
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Flange
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.3 - Isolation Valve 150mm Item # 3 (suction side)
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Side of Valve
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.4 - 150mm Dismantling joint (suction side) Item#4
label | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.5 - 150mm Flange Adaptor Spool. Item # 5
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.6 - 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.7 - 150mm swing check valve. Item # 7
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Side of Valve
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.8 - 150mm Sweeping Spool (discharge). Item # 8
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.9 - 150mm Dismantling joint (discharge side) Item#4
label | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Once
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.10 - Isolation Valve 150mm Item # 3 (discharge side)
label | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
label | Acceptance Criteria - Use diametrically opposed touque sequence
label | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
label | Frequency - Each Side of Valve
label | Inspection Type (Visual, other) - Record & attach to ITP
label | Inspection: Key - Inspection
label | Inspection: By - IP
checkpoint | 4.11 - Pipework bracketing installed and is secure.
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Pipework complete and installed. Adjustable brackets
label | Verifying Document - As indicated on the drawings
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Final inspection to installed pipework
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
label | Verifying Document - As per drawings
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Pipework is installed and correct fittings installed to accept the instrumentation
label | Verifying Document - As per drawing schematics
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.3 - Pipework bracketing installed and is secure.
label | Inspection Point: Quality Control Activity - At completion of pipework
label | Acceptance Criteria - Pipework complete and installed
label | Verifying Document - As per drawings
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection | itp |  |  |  |  | 561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Grout Castings (Penetrations 1 through 3)
label | Inspection Point: Quality Control Activity - Inspection of castings.
label | ○ Inspection for air pockets, cracks, fissures oa any other imperfections
label | Acceptance Criteria - Completion of ITP's
label | ○ 561482-ITP-007.1.
label | ○ 561482-ITP-007.2
label | ○ 561482-ITP-007.3
label | ○ Elapsed time of 7 days post pour
label | Verifying Document - None
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - A
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Removal of Formwork - Penetration 1
label | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
label | Acceptance Criteria - Approval from Engineer
label | Verifying Document - Drawing M0003 and annotations
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Removal of Formwork - Penetration 2
label | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
label | Acceptance Criteria - Approval from Engineer
label | Verifying Document - Drawing M0003 and annotations
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Removal of Formwork - Penetration 3
label | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
label | Acceptance Criteria - Approval from Engineer
label | Verifying Document - Drawing M0003 and annotations
label | Frequency - once
label | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Clean tank of any Downer construction debris
label | Inspection Point: Quality Control Activity - Upon removal of boxing and any remedial activities
label | Acceptance Criteria - Client Representative acceptance
label | Verifying Document - NTC and or other written conformation
label | Frequency - once
label | Inspection Type (Visual, other) - Visual Inspection + Photograph
label | Inspection: Key - H
label | Inspection: By - CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Approval to fill Wet well
label | Inspection Point: Quality Control Activity - All activities and pre-checks required by client
label | Acceptance Criteria - Client Representative acceptance
label | Verifying Document - NTC and or other written conformation
label | Frequency - once
label | Inspection Type (Visual, other) - Visual Inspection + Photograph
label | Inspection: Key - C
label | Inspection: By - CR