## Project Structure
Folder Structure |  |  |  |  | Checklist
Site QA
Penetrations
Installation
ITR 001 Set Out Penetrations
Level 1
Suspended Drainage Services
Installation
Storm Water (suspended)
|  |  |  | Lower Ground | ITR 007 Suspended Storm Drainage
|  |  |  | Level 1 | ITR 007 Suspended Storm Drainage
|  |  |  | Outdoor play area | ITR 007 Suspended Storm Drainage
Sewer (suspended)
|  |  |  | Lower Ground | ITR 006 Suspended Sewer Drainage
|  |  |  | Level 1 | ITR 006 Suspended Sewer Drainage
Trade Waste (suspended)
|  |  |  | Lower Ground | ITR 008 Suspended Greasy Drainage
|  |  |  | Level 1 | ITR 008 Suspended Greasy Drainage
Rough In Water Services
Cold Water
|  |  |  | Staff room | ITR 011 Hot & Cold Rough In
|  |  |  | Kitchen/Pantry | ITR 011 Hot & Cold Rough In
|  |  |  | Laundry | ITR 011 Hot & Cold Rough In
|  |  |  | Childern's Toilet 1 | ITR 011 Hot & Cold Rough In
|  |  |  | Childern's Toilet 2 | ITR 011 Hot & Cold Rough In
|  |  |  | Childern's Toilet 3 | ITR 011 Hot & Cold Rough In
|  |  |  | Childern's Toilet 4 | ITR 011 Hot & Cold Rough In
|  |  |  | Prep Store 1 | ITR 011 Hot & Cold Rough In
|  |  |  | Prep Store 2 | ITR 011 Hot & Cold Rough In
|  |  |  | Staff WC | ITR 011 Hot & Cold Rough In
|  |  |  | Dis. WC | ITR 011 Hot & Cold Rough In
|  |  |  | Craft/Store 1 | ITR 011 Hot & Cold Rough In
|  |  |  | Craft/Store 2 | ITR 011 Hot & Cold Rough In
|  |  |  | Outdoor play area | ITR 011 Hot & Cold Rough In
Hot Water
|  |  |  | Staff room | ITR 011 Hot & Cold Rough In
|  |  |  | Kitchen/Pantry | ITR 011 Hot & Cold Rough In
|  |  |  | Laundry | ITR 011 Hot & Cold Rough In
|  |  |  | Childern's Toilet 1 | ITR 011 Hot & Cold Rough In
|  |  |  | Childern's Toilet 2 | ITR 011 Hot & Cold Rough In
|  |  |  | Childern's Toilet 3 | ITR 011 Hot & Cold Rough In
|  |  |  | Childern's Toilet 4 | ITR 011 Hot & Cold Rough In
|  |  |  | Prep Store 1 | ITR 011 Hot & Cold Rough In
|  |  |  | Prep Store 2 | ITR 011 Hot & Cold Rough In
|  |  |  | Staff WC | ITR 011 Hot & Cold Rough In
|  |  |  | Dis. WC | ITR 011 Hot & Cold Rough In
|  |  |  | Craft/Store 1 | ITR 011 Hot & Cold Rough In
|  |  |  | Craft/Store 2 | ITR 011 Hot & Cold Rough In
|  |  |  | Outdoor play area | ITR 011 Hot & Cold Rough In
Fit Off
Sanitary Fixtures
|  |  |  | Staff room | ITR 014 Sanitary Fit Off
|  |  |  | Kitchen/Pantry | ITR 014 Sanitary Fit Off
|  |  |  | Laundry | ITR 014 Sanitary Fit Off
|  |  |  | Childern's Toilet 1 | ITR 014 Sanitary Fit Off
|  |  |  | Childern's Toilet 2 | ITR 014 Sanitary Fit Off
|  |  |  | Childern's Toilet 3 | ITR 014 Sanitary Fit Off
|  |  |  | Childern's Toilet 4 | ITR 014 Sanitary Fit Off
|  |  |  | Prep Store 1 | ITR 014 Sanitary Fit Off
|  |  |  | Prep Store 2 | ITR 014 Sanitary Fit Off
|  |  |  | Staff WC | ITR 014 Sanitary Fit Off
|  |  |  | Dis. WC | ITR 014 Sanitary Fit Off
|  |  |  | Craft/Store 1 | ITR 014 Sanitary Fit Off
|  |  |  | Craft/Store 2 | ITR 014 Sanitary Fit Off
|  |  |  | Outdoor play area | ITR 014 Sanitary Fit Off
Commissioning
RPZD's
ITR 015 Backflow Test Report
TMV's
|  |  |  | Staff room | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Kitchen/Pantry | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Laundry | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Childern's Toilet 1 | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Childern's Toilet 2 | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Childern's Toilet 3 | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Childern's Toilet 4 | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Prep Store 1 | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Prep Store 2 | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Staff WC | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Dis. WC | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Craft/Store 1 | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Craft/Store 2 | ITR 017 Thermostatic Mixing Valve Test Report
|  |  |  | Staff room | ITR 016 Tempering Valve Test Report
|  |  |  | Kitchen/Pantry | ITR 016 Tempering Valve Test Report
|  |  |  | Laundry | ITR 016 Tempering Valve Test Report
|  |  |  | Childern's Toilet 1 | ITR 016 Tempering Valve Test Report
|  |  |  | Childern's Toilet 2 | ITR 016 Tempering Valve Test Report
|  |  |  | Childern's Toilet 3 | ITR 016 Tempering Valve Test Report
|  |  |  | Childern's Toilet 4 | ITR 016 Tempering Valve Test Report
|  |  |  | Prep Store 1 | ITR 016 Tempering Valve Test Report
|  |  |  | Prep Store 2 | ITR 016 Tempering Valve Test Report
|  |  |  | Staff WC | ITR 016 Tempering Valve Test Report
|  |  |  | Dis. WC | ITR 016 Tempering Valve Test Report
|  |  |  | Craft/Store 1 | ITR 016 Tempering Valve Test Report
|  |  |  | Craft/Store 2 | ITR 016 Tempering Valve Test Report
Water Meters
ITR 013 Water Meter
HWS
|  |  |  | Roof plant | ITR 012 Hot Water Service
Pumps & Equipement
Supplier commissioning reports
Fire Register
| Fire Matrix |  |  |  | Documentation
| Penetrations Drawings |  |  |  | Documentation
Passive Fire / Collars Penetration

## Resources
checklist | Internal Audit Checklist
checkpoint | Drawing Register Current
checkpoint | Drawings as per Register
checkpoint | ITP Records
checkpoint | Material Specification
checkpoint | Sanitary Specification
checkpoint | Calibration records
checkpoint | Sample Register
text | Comments
text | Items of concern
text | Action required
text | Future recommendations
checkpoint | Signed off by Highbury Plumbing Supervisor
checklist | Non Conformance Report
checkpoint | Report completed
text | Short description
text | NCN NO:
text | Level / Area
text | Grid Coord
text | Responsibility
text | Non Conformance Details
checkpoint | Method of disposition
text | Approval required from
checkpoint | Repair / Use as is
text | Customer
checkpoint | Rework / Replace
text | Project Manager
checkpoint | Signed off by Highbury Plumbing Supervisor
checkpoint | Signed off by Scentre Group
checklist | Inspection Test Plan
section | Set Out Penetrations
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Penetrations and Fire Collars to be in accordance with specification as required for each fire compartment rating and for each fire rated element.
checkpoint | Ensure Fire Collars are installed as per manufacturer’s instructions. Tabs on cast in, collars to be exposed. Photos of collar and labelling referencing fire matrix if required
checkpoint | All works completed in accordance to specifications and drawings. All certificates completed and submitted
label | ITR 001
section | In Ground Sewer Drainage
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
checkpoint | All works to be set out as per approved IFC drawings. Works set out to IFC Drawings No.
checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings
checkpoint | Inspection booked with VBA for in ground drainage. HP can sign off if inspector does not attend.
label | ITR 002
section | In Ground Storm Water Drainage
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification and AS 3500
checkpoint | All works to be set out as per approved IFC drawings. Works set out to IFC Drawings No
checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted.
label | ITR 003
section | In Ground Greasy Drainage
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
checkpoint | All works to be set out as per approved IFC drawings. Works set out to IFC Drawings No.
checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
label | ITR 004
section | Fire Services
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification
checkpoint | All pipe work to be as per specifications and AS 2419 & AS 2441 or alternatively approved by CFA/MFB
checkpoint | All pipe work to be tested to 1700 kPA in accordance to specifications and requirements as per AS 2419 Hydrants & AS 2441 Hose Reels
checkpoint | Prior to handover system must be inspected & certified in accordance to drawings, code, specification, dispensation & 129 report and FER.
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted.
label | ITR 005
section | Suspended Sewer Drainage
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | Ensure acoustic lagging is installed if required to specification and acoustic engineers report
checkpoint | As per AS 3500 all traps have been tested for leaks by discharging water into drains
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
label | ITR 006
section | Suspended Stormwater
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework to be checked for correct invert levels, gradients & clearance levels/head height in accordance with specifications and requirements
checkpoint | Ensure acoustic lagging is installed if required to specification and acoustic engineers report
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
label | ITR 007
section | Domestic Cold Water In
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.2.2015
checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework to be tested to 1500 kPA for 30 minutes as per AS 3500:1 clause 18.3.1 in accordance with specifications and requirements
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
label | ITR 008
section | Gas Service
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500
checkpoint | All pipe work to be as per specifications and AS 3500 or alternatively approved including road sizes, clipping configurations and methods
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
checkpoint | Prior to gas being turned on ESV must be notified, inspection arrange and approval issued (if required). HP Management must be notified at the completion of works.
label | ITR 009
section | Hot & Cold Water Rough In
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of material to be used. Ensure all materials are in accordance to specification AS 3500.1.2015 & AS 3500.4.2015 or alternatively approved.
checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings
checkpoint | All pipework to be tested in accordance with specifications and requirements namely 1500 kPA for 30 minutes as per AS 3500:1 clause 18.1.3.
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted.
label | ITR 010
section | Hot Water Service
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples HWS.. Ensure all materials are in accordance to specification AS 3500.1.2015 & AS 3500.4.2015 or alternatively approved
checkpoint | All pipe work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All works completed in accordance to specifications & drawings. All certificates completed and submitted
label | ITR 011
section | Water Meter
checkpoint | Submit shop drawings for approval in accordance with specifications and requirements. All drawings MUST be approved prior to commencement of works
checkpoint | Submit all samples of materials. Ensure all materials are in accordance to specification AS 3500.1.2015 & AS 3500.4.2015 or alternatively approved
checkpoint | All works to be set up as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings
checkpoint | All meter work to be as per specifications and AS 3500.2.2015 or alternatively approved and appropriately sized
checkpoint | Tested and Commissioning completed by passing an amount of known volume (bucket) and confirm the volume of water and meter reading are the same or within the required tolerances
label | ITR 012
section | Sanitary Fit Off
checkpoint | Submit all sanitary fixtures and tapware. Ensure all material is in accordance with specification AS 3500 and watermarked.
label | ITR 013
section | Backflow Test Report
checkpoint | Submit Backflow Test Report
label | ITR 014
section | Tempering Valve Test Report
checkpoint | Submit Tempering Valve Test Report
label | ITR 015
section | Thermostatic Mixing Valve Test Report
checkpoint | Submit Thermostatic Mixing Valve Test Report
label | ITR 016
section | Third Party Commissioning
checkpoint | Submit any Third Party Commissioning Reports which one are applicable:
label | Ie Pumps, Tanks, HWS, Fire Hydrants
label | Report from Third Party
checklist | ITR 001 Set Out Penetrations
checkpoint | All works to be set our as per approved IFC drawings. Works set out to IFC Drawing No.
checkpoint | All penetrations and fire collars to be as per specifications or alternatively approved
checkpoint | All penetrations set out using total station or surveyed grid points by the builder
checkpoint | Ensure fire collars are installed as per manufacturer’s instructions.
checkpoint | Tabs on cast in collar to be exposed.
checkpoint | Photos of collar end labelling referencing fire matrix if required
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist | ITR 002 Sewer Drainage
checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint | Notify HP Management for inspection of drainage prior to backfill.
checkpoint | Book inspection with VBA for in-ground drainage. HP can sign off if inspector does not attend.
checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist | ITR 003 Stormwater Drainage In Ground
checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint | All pits to be checked for correct invert levels & finished floor levels in accordance to specifications & requirements & IFC drawings.
checkpoint | Ensure correct locations of pits.
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications & requirements
checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist | ITR 004 Greasy Drainage In Ground
checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint | Ensure all backfill is in accordance to specifications & compaction requirements.
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist | ITR 005 Fire Service
checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint | All pipe work to be as per specifications & Standards or alternatively approved by CFA/MFB.
checkpoint | All pipework to be tested TO 1700 kPA in accordance to specifications &
checkpoint | requirements as per AS 2419 Hydrants & AS 2441 Hose Reels
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checkpoint | Prior to handover system must be inspected & certified in accordance to drawings, code, specification, dispensation, 129 report and FER
checklist | ITR 006 Suspended Sewer Drainage
checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist | ITR 007 Suspended Storm Drainage
checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist | ITR 008 Suspended Greasy Drainage
checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint | Ensure acoustic lagging is installed if required to specification & acoustic engineers report.
checkpoint | As per AS 3500 test traps for leaks by discharging water into drains
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist | ITR 009 Domestic Cold Water In Ground
checkpoint | All works to be set out as per approved IFC Drawings No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be tested to 1500 kPA for 30 minutes as per AS 3500:1 clause 18.3.1 & in accordance with specifications and requirements . Ensure isolation from authority main, fixtures, tapware and appliances while undertaking testing.
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
checklist | ITR 010 Gas Service
checkpoint | All works to be set out as per approved IFC Drawings No.
checkpoint | All pipe work to be as per specifications & AS5601.1 or alternatively approved including rod sizes and clipping configurations and methods
checkpoint | All pipework to be tested in accordance with specifications and requirements & AS5601.1
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checkpoint | Prior to gas being turned on ESV must inspect and approved installation if required, including all builders work requirements IE signage, access panels, ventilation, riser shafts etc..
checkpoint | Must notify HP management on completion of works.
checklist | ITR 011 Hot & Cold Rough In
checkpoint | All works to be set our as per approved IFC drawings and penetrations to be installed to - IFC Drawing No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework, material and fittings to be installed as per approved IFC Drawing No:
checkpoint | All pipework to be checked for correct invert levels & gradients in accordance to specifications, requirements & approved IFC drawings.
checkpoint | All pipework to be tested to 1500 kPA for 30 minutes as per AS 3500:1 clause 18.3.1 & in accordance with specifications and requirements . Ensure isolation from authority main, fixtures, tapware and appliances while undertaking testing
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy.
checklist | ITR 012 Hot Water Service
checkpoint | All works to be set out as per approved IFC drawings. Works set out to Drawing No.
checkpoint | All pipe work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | All pipework to be tested in accordance to specifications and requirements namely 1500 kPA for 30 minutes
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
checklist | ITR 013 Water Meter
checkpoint | All works to be set out as per approved IFC Drawing No:
checkpoint | All meter work to be as per specifications & AS3500.2.2015 or alternatively approved and appropriately sized
checkpoint | Ensure that all pipework to meters has been sealed and jointed, all capping adequately installed for testing.
checkpoint | Ensure all meters are sufficient supported and installed in correct location
checkpoint | Pass an amount of water in a container of known volume (bucket) and confirm the volume of water and meter reading are the same or within the required tolerances
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
checklist | ITR 014 Sanitary Fit Off
checkpoint | All works to be set our as per approved Architectural Drawing No.
checkpoint | Inspect for product defects.
checkpoint | Install as per manufacturer's recommendations and requirements
checkpoint | All sanitary items to be tested in accordance to specifications and manufacturers requirements
checkpoint | Check for leaks
checkpoint | Ensure all excess material is removed from work area & leave clean & tidy
checklist | ITR 015 Backflow Test Report
checkpoint | Backflow Test Report Completed
text | Date of test
text | Location of test
text | Licence No.
text | Test Kit Serial No.
text | Date test kit last certified
text | Place of certification
text | Make of device
text | Size (mm)
text | Model
text | Serial No.
label | Initial Test Before Maintenance
checkpoint | Permission to shut of water
bool | Reduced Pressure Zone Device
bool | Double Check Valve (Columns 1 & 2)
bool | Pressure Type
checkpoint | Check Valve No 1
bool | Closed Tight
bool | Leaked
text | kPa
checkpoint | Check Valve No 2
bool | Closed Tight
bool | Leaked
text | kPa
checkpoint | Relief Valve
bool | Opened At
bool | Not Opened
text | kPa
checkpoint | Check Valve
bool | Closed Tight
bool | Leaked
text | kPa
checkpoint | Air Inlet
bool | Opened At
bool | Not Opened
text | kPa
checkpoint | Downstream Isolation Valve
bool | Closed Tight
bool | Leaked
text | kPa
checkpoint | Comment / Take photos of any reasons for failure (NA if not required)
label | Re-Test After
checkpoint | Permission to shut of water
bool | Reduced Pressure Zone Device
bool | Double Check Valve (Columns 1 & 2)
bool | Pressure Type
checkpoint | Check Valve No 1
bool | Closed Tight
bool | Leaked
text | kPa
checkpoint | Check Valve No 2
bool | Closed Tight
bool | Leaked
text | kPa
checkpoint | Relief Valve
bool | Opened At
bool | Not Opened
text | kPa
checkpoint | Check Valve
bool | Closed Tight
bool | Leaked
text | kPa
checkpoint | Air Inlet
bool | Opened At
bool | Not Opened
text | kPa
checkpoint | Downstream Isolation Valve
bool | Closed Tight
bool | Leaked
text | kPa
checkpoint | Described Maintenance - Add comments / photos
text | Parts & Materials Used
text | Water Meter Number
checkpoint | Testing signed off
checklist | ITR 016 Tempering Valve Test Report
checkpoint | Tempering Valve Test
text | Licence No.
text | Test kit serial No.
text | Date test kit last certified:
text | Place of certification
text | Make
text | Model
text | Location of valve
checkpoint | Flush / Clean filters
checkpoint | One outlet in use
text | kPa
checkpoint | Temp of warm water
text | Fixture
text | Pre Set Temp
checkpoint | Described Maintenance - Add comments / photos
text | Parts & Materials Used
checkpoint | Testing signed off
checklist | ITR 017 Thermostatic Mixing Valve Test Report
checkpoint | Thermostatic Mixing Valve Test
text | Licence No.
text | Test kit serial No.
text | Date test kit last certified:
text | Place of certification
text | Make
text | Model
text | Location of valve
checkpoint | Shut down test
checkpoint | Flush / Clean filters
checkpoint | Static Test
bool | One outlet in use
text | kPa
checkpoint | Temp of warm water
text | Fixture
text | Pre Set Temp
checkpoint | Described Maintenance - Add comments / photos
text | Parts & Materials Used
checkpoint | Testing signed off
checklist | Passive Fire / Collars Penetration
checkpoint | Please take detail photos of penetration & noteling
dropdown | Material | PVC, HDPE, CU, PEX, GAL
dropdown | Pipe size | 20, 25, 32, 40, 50, 56, 63, 65, 75, 80, 90, 100, 110, 125, 150, 160, 200, 225, 250, 300, 315, 375, 450
dropdown | Fire Matrix Ref Number | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, 26, 27, 28, 29, 30, 31, 32, 33, 34, 35, 36, 37, 38, 39, 40, 41, 42, 43, 44,45,46,47,48,49,50,51,52,53,54,55,56,57,58