## Sheet1
561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2 | [16 empty] | 3.1 - Grout Castings (Penetrations 1 through 3)
3.1 | Align pump and motor shafts and install coupling - Pump CHAR(AMP) Motor Assembly 2 | Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm | Completion of the assebmly to pump and motor 2 including mounting to the plinth. | Downer 561482-ITP-004.2 | once | Visual + Photograph + document provided by specialist | QE | D / E | [8 empty] | Inspection Point: Quality Control Activity - Inspection of castings. Inspection for air pockets, cracks, fissures oa any other imperfections
4.1 | Align pump and motor shafts and install coupling - Pump CHAR(AMP) Motor Assembly 2 | Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment | Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm | Report provided by Engineering Specialist - Wallace Murray Electrical | once | Visual + Photograph + document provided by specialist | QE | D / E | [8 empty] | Acceptance Criteria - Completion of ITP's 561482-ITP-007.1. 561482-ITP-007.2 561482-ITP-007.3 Elapsed time of 7 days post pour
4.2 | Install drive coupling to Pump 2 | Completion of the nstallation of shaft drive coupling - Pump 2 | Completion of Item 4.1 | Report provided by Engineering Specialist - Wallace Murray Electrical | Once | Visual + Photograph | A / I | IP | [8 empty] | Verifying Document - None
5.1 | Pump 2 CHAR(AMP) Motor assembly | Final inspection CHAR(AMP) check. Rotate motor/pump assembly by hand to esnure smooth operation | Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed | As per methodology, Shaft lignment verification CHAR(AMP) Manufacturers Instructions. Detailed report provided from specialist - Wallace Murray Electrical | once | Visual + Document | I | IP | [8 empty] | Frequency - Once
Inspection Type (Visual, other) - Visual + Photographs
Inspection: Key - A
561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3 | [16 empty] | Inspection: By - IP
3.1 | Align pump and motor shafts and install coupling - Pump CHAR(AMP) Motor Assembly 3 | Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm | Completion of the assebmly to pump and motor 3 including mounting to the plinth. | Downer 561482-ITP-004.3 | once | Visual + Photograph + document provided by specialist | QE | D / E | [8 empty] | 4.1 - Removal of Formwork - Penetration 1
4.1 | Align pump and motor shafts and install coupling - Pump CHAR(AMP) Motor Assembly 3 | Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment | Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm | Report provided by Engineering Specialist - Wallace Murray Electrical | once | Visual + Photograph + document provided by specialist | QE | D / E | [8 empty] | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
4.2 | Install drive coupling to Pump 3 | Completion of the nstallation of shaft drive coupling - Pump 3 | Completion of Item 4.1 | Report provided by Engineering Specialist - Wallace Murray Electrical | Once | Visual + Photograph | A / I | IP | [8 empty] | Acceptance Criteria - Approval from Engineer
5.1 | Pump 3 CHAR(AMP) Motor assembly | Final inspection CHAR(AMP) check. Rotate motor/pump assembly by hand to esnure smooth operation | Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed | As per methodology, Shaft lignment verification CHAR(AMP) Manufacturers Instructions. Detailed report provided from specialist - Wallace Murray Electrical | once | Visual + Document | I | IP | [8 empty] | Verifying Document - Drawing M0003 and annotations
Frequency - once
Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
561482-ITP-006.1 - Pipe CHAR(AMP) Fitting Installation Pump 1 | [16 empty] | Inspection: Key - H
3.1 | Stainless Steel Pipe components | Obtain the mill certificates for the materials used - 316L Stainless Steel | Documents from the supplier/Manufacturer | Mill Certificates CHAR(AMP) Welding certificates | Once | Documentation | C | IP | [8 empty] | Inspection: By - CR
3.2 | Stainless Steel Pipe components | Take delivery of components from Supplier. Verify all components have been delivered | Quantities as shown on the drawings | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | Once | Visual | C | IP | [8 empty] | 4.2 - Removal of Formwork - Penetration 2
3.3 | Stainless Steel Pipe components | Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions | Dimensions CHAR(AMP) orientation as shown on the drawings | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | Once | Visual Dimension Inspection | D | IP | [8 empty] | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
3.4 | Valves CHAR(AMP) Ancillaries (Blanking Flange) | Check and verify that the Manufacturer CHAR(AMP) Type is approved for use by the client | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP | [8 empty] | Acceptance Criteria - Approval from Engineer
3.5 | Dress Sets (gaskets CHAR(AMP) fasteners) | Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP | [8 empty] | Verifying Document - Drawing M0003 and annotations
4.1 | Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each flange | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Frequency - once
4.2 | Fasten Dry Well side from spool (cast in wall) Item # 2 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Flange | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
4.3 | Blanking Flange150mm (suction side) | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australian Water Standards Guidelines - 80N.m | Each Side of Valve | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Inspection: Key - H
4.3 | Blanking Flange150mm (Discharge side) | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australian Water Standards Guidelines - 80N.m | Each Side of Valve | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Inspection: By - CR
5.1 | Final inspection to installed pipework | At completion of pipework | Flanges are straight and bolts tightened all threads sealed and leak free | As per drawings | once | Visual | I | IP | [8 empty] | 4.3 - Removal of Formwork - Penetration 3
Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
Acceptance Criteria - Approval from Engineer
561482-ITP-006.2 - Pipe CHAR(AMP) Fitting Installation Pump 2 | [16 empty] | Verifying Document - Drawing M0003 and annotations
3.1 | Stainless Steel Pipe components | Obtain the mill certificates for the materials used - 316L Stainless Steel | Documents from the supplier/Manufacturer | Mill Certificates CHAR(AMP) Welding certificates | Once | Documentation | C | IP | [8 empty] | Frequency - once
3.2 | Stainless Steel Pipe components | Take delivery of components from Supplier. Verify all components have been delivered | Quantities as shown on the drawings | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | Once | Visual | C | IP | [8 empty] | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
3.3 | Stainless Steel Pipe components | Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions | Dimensions CHAR(AMP) orientation as shown on the drawings | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | Once | Visual Dimension Inspection | D | IP | [8 empty] | Inspection: Key - H
3.4 | Valves CHAR(AMP) Ancillaries | Check and verify that the Manufacturer CHAR(AMP) Type is approved for use by the client | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP | [8 empty] | Inspection: By - CR
3.5 | Dress Sets (gaskets CHAR(AMP) fasteners) | Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP | [8 empty] | 5.1 - Clean tank of any Downer construction debris
4.1 | Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each flange | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Inspection Point: Quality Control Activity - Upon removal of boxing and any remedial activities
4.2 | Fasten Dry Well side from spool (cast in wall) Item # 2 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Flange | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Acceptance Criteria - Client Representative acceptance
4.3 | Isolation Valve 150mm Item # 3 (suction side) | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Verifying Document - NTC and or other written conformation
4.4 | 150mm Dismantling joint (suction side) Item#4 | Torque fasteners to relevant water standards | Use diametrically opposed touque sequence and manufactruers instructions | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Frequency - once
4.5 | 150mm Flange Adaptor Spool. Item # 5 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Inspection Type (Visual, other) - Visual Inspection + Photograph
4.6 | 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Inspection: Key - H
4.7 | 150mm swing check valve. Item # 7 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Inspection: By - CR
4.8 | 150mm Sweeping Spool (discharge). Item # 8 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | 5.2 - Approval to fill Wet well
4.9 | 150mm Dismantling joint (discharge side) Item#4 | Torque fasteners to relevant water standards | Use diametrically opposed touque sequence and manufactruers instructions | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Inspection Point: Quality Control Activity - All activities and pre-checks required by client
4.1 | Isolation Valve 150mm Item # 3 (discharge side) | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record CHAR(AMP) attach to ITP | Inspection | IP | [8 empty] | Acceptance Criteria - Client Representative acceptance
4.11 | Pipework bracketing installed and is secure. | At completion of pipework | Pipework complete and installed. Adjustable brackets | As indicated on the drawings | once | Visual | I | IP | [8 empty] | Verifying Document - NTC and or other written conformation
5.1 | Final inspection to installed pipework | At completion of pipework | Flanges are straight and bolts tightened all threads sealed and leak free | As per drawings | once | Visual | I | IP | [8 empty] | Frequency - once
5.2 | Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage | At completion of pipework | Pipework is installed and correct fittings installed to accept the instrumentation | As per drawing schematics | once | Visual | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual Inspection + Photograph
5.3 | Pipework bracketing installed and is secure. | At completion of pipework | Pipework complete and installed | As per drawings | once | Visual | I | IP | [8 empty] | Inspection: Key - C
Inspection: By - CR
561482-ITP-006.3 - Pipe CHAR(AMP) Fitting Installation Pump 3
3.1 | Stainless Steel Pipe components | Obtain the mill certificates for the materials used - 316L Stainless Steel | Documents from the supplier/Manufacturer | Mill Certificates CHAR(AMP) Welding certificates | Once | Documentation | C | IP
3.2 | Stainless Steel Pipe components | Take delivery of components from Supplier. Verify all components have been delivered | Quantities as shown on the drawings | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | Once | Visual | C | IP
3.3 | Stainless Steel Pipe components | Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions | Dimensions CHAR(AMP) orientation as shown on the drawings | Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004 | Once | Visual Dimension Inspection | D | IP
3.4 | Valves CHAR(AMP) Ancillaries | Check and verify that the Manufacturer CHAR(AMP) Type is approved for use by the client | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP
3.5 | Dress Sets (gaskets CHAR(AMP) fasteners) | Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP
4.1 | Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each flange | Record CHAR(AMP) attach to ITP | Inspection | IP
4.2 | Fasten Dry Well side from spool (cast in wall) Item # 2 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Flange | Record CHAR(AMP) attach to ITP | Inspection | IP
4.3 | Isolation Valve 150mm Item # 3 (suction side) | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record CHAR(AMP) attach to ITP | Inspection | IP
4.4 | 150mm Dismantling joint (suction side) Item#4 | Torque fasteners to relevant water standards | Use diametrically opposed touque sequence and manufactruers instructions | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP
4.5 | 150mm Flange Adaptor Spool. Item # 5 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP
4.6 | 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP
4.7 | 150mm swing check valve. Item # 7 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record CHAR(AMP) attach to ITP | Inspection | IP
4.8 | 150mm Sweeping Spool (discharge). Item # 8 | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP
4.9 | 150mm Dismantling joint (discharge side) Item#4 | Torque fasteners to relevant water standards | Use diametrically opposed touque sequence and manufactruers instructions | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Once | Record CHAR(AMP) attach to ITP | Inspection | IP
4.1 | Isolation Valve 150mm Item # 3 (discharge side) | Install gasket, bolts CHAR(AMP) nuts and tighten. Torque fasteners to relevant water standards | Use diametrically opposed touque sequence | As per WSA-109 Australiann Water Standards Guidelines - 80N.m | Each Side of Valve | Record CHAR(AMP) attach to ITP | Inspection | IP
4.11 | Pipework bracketing installed and is secure. | At completion of pipework | Pipework complete and installed. Adjustable brackets | As indicated on the drawings | once | Visual | I | IP
5.1 | Final inspection to installed pipework | At completion of pipework | Flanges are straight and bolts tightened all threads sealed and leak free | As per drawings | once | Visual | I | IP
5.2 | Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage | At completion of pipework | Pipework is installed and correct fittings installed to accept the instrumentation | As per drawing schematics | once | Visual | I | IP
5.3 | Pipework bracketing installed and is secure. | At completion of pipework | Pipework complete and installed | As per drawings | once | Visual | I | IP
561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection
3.1 | Grout Castings (Penetrations 1 through 3) | Inspection of castings. Inspection for air pockets, cracks, fissures oa any other imperfections | Completion of ITP's 561482-ITP-007.1. 561482-ITP-007.2 561482-ITP-007.3 Elapsed time of 7 days post pour | None | Once | Visual + Photographs | A | IP | 3.1 - Grout Castings (Penetrations 1 through 3) | Inspection Point: Quality Control Activity - Inspection of castings. Inspection for air pockets, cracks, fissures oa any other imperfections | Acceptance Criteria - Completion of ITP's 561482-ITP-007.1. 561482-ITP-007.2 561482-ITP-007.3 Elapsed time of 7 days post pour | Verifying Document - None | Frequency - Once | Inspection Type (Visual, other) - Visual + Photographs | Inspection: Key - A | Inspection: By - IP
4.1 | Removal of Formwork - Penetration 1 | Check and verify quality of casting both wet well side and Dry side | Approval from Engineer | Drawing M0003 and annotations | once | Document + Visual + Photograph + Engineer site Inspection | H | CR | 4.1 - Removal of Formwork - Penetration 1 | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side | Acceptance Criteria - Approval from Engineer | Verifying Document - Drawing M0003 and annotations | Frequency - once | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection | Inspection: Key - H | Inspection: By - CR
4.2 | Removal of Formwork - Penetration 2 | Check and verify quality of casting both wet well side and Dry side | Approval from Engineer | Drawing M0003 and annotations | once | Document + Visual + Photograph + Engineer site Inspection | H | CR | 4.2 - Removal of Formwork - Penetration 2 | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side | Acceptance Criteria - Approval from Engineer | Verifying Document - Drawing M0003 and annotations | Frequency - once | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection | Inspection: Key - H | Inspection: By - CR
4.3 | Removal of Formwork - Penetration 3 | Check and verify quality of casting both wet well side and Dry side | Approval from Engineer | Drawing M0003 and annotations | once | Document + Visual + Photograph + Engineer site Inspection | H | CR | 4.3 - Removal of Formwork - Penetration 3 | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side | Acceptance Criteria - Approval from Engineer | Verifying Document - Drawing M0003 and annotations | Frequency - once | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection | Inspection: Key - H | Inspection: By - CR
5.1 | Clean tank of any Downer construction debris | Upon removal of boxing and any remedial activities | Client Representative acceptance | NTC and or other written conformation | once | Visual Inspection + Photograph | H | CR | 5.1 - Clean tank of any Downer construction debris | Inspection Point: Quality Control Activity - Upon removal of boxing and any remedial activities | Acceptance Criteria - Client Representative acceptance | Verifying Document - NTC and or other written conformation | Frequency - once | Inspection Type (Visual, other) - Visual Inspection + Photograph | Inspection: Key - H | Inspection: By - CR
5.2 | Approval to fill Wet well | All activities and pre-checks required by client | Client Representative acceptance | NTC and or other written conformation | once | Visual Inspection + Photograph | C | CR | 5.2 - Approval to fill Wet well | Inspection Point: Quality Control Activity - All activities and pre-checks required by client | Acceptance Criteria - Client Representative acceptance | Verifying Document - NTC and or other written conformation | Frequency - once | Inspection Type (Visual, other) - Visual Inspection + Photograph | Inspection: Key - C | Inspection: By - CR